## Table 1
Client: AIAL | [8 empty] | Subcontractor: TBC | [8 empty] | Work Area: SCH, HOSR
Project Name: Domestic Jet Terminal | [8 empty] | Job No: HA0423 | [8 empty] | Subcontractor Representative: TBC
1. ITP Element: Utility Services Ducting – High Voltage, Low Voltage and Communication systems
2. Revision Records
Rev No. |  |  | Revision Description | [11 empty] | Name of Author |  |  |  |  | Authorized by: |  |  | Date
A |  |  | For Approval | [11 empty] | Rohit Sen |  |  |  |  | Matt Cheyne
B
C
0
1
3. Relevant Documents
Doc No. |  |  |  | Specification/ Drwgs/ Standards |  |  |  | Additional Info |  |  |  | Document No. |  | Specification/ Drwgs/ Standards | [8 empty] | Additional Info
1 |  |  |  | DP001-MMD-SPC-CV-Z-Z-0001 |  |  |  | Rev 02 |  |  |  | 6
2 |  |  |  | DP001-MMD-DRW-UT-B-Z-3031 - 3055 |  |  |  | Rev 01, 02 & 03 |  |  |  | 7
3 |  |  |  | DP001-MMD-DRW-UT-B-Z-3071 - 3091 |  |  |  | Rev 01, 02 & 03 |  |  |  | 8
4 |  |  |  | DP001-MMD-DRW-UT-B-Z-3137 - 3139 |  |  |  | Rev 01 |  |  |  | 9
5 |  |  |  | DP001-MMD-DRW-UT-B-Z-3010-3018 |  |  |  | Rev 02 & 03 |  |  |  | 10
4. Process
No. |  | Description Inspection / test |  |  |  | Frequency | Spec/standard |  |  | Acceptance Criteria |  |  | Measuring Devices |  |  | Reporting Format | Inspected by* |  |  |  |  | Hold Points Sign off |  | Remarks
[17 empty] | HCL |  | SC |  | Consult
1 |  | Material Compliance
1.1 |  | Fill Materials
1.1.1 |  | Bedding material PAP 7 for PE pipes AP40 for Chambers |  |  |  | Per Batch | CIV Spec - S12.3.4 |  |  | Accept/ Reject |  |  | N/A |  |  | Dockets / Material Data Sheets | R |  | SUB |  | R | Hold Point
1.1.1 |  | Backfill Material GAP65 or TNZ M/4 AP40 |  |  |  | Per Batch | CIV Spec - S12.3.5 CIV Spec - S4.4.5 |  |  | Accept / Reject |  |  | N/A |  |  | Dockets / Material Data Sheets | R |  | SUB |  | R | Hold Point
1.2 |  | Pipes
1.2.1 |  | Pipes: 110 OD PE SDR 17 160 OD PE SDR 17 |  |  |  | Each Pipe | CIV Spec - S12.3.3 |  |  | Accept/Reject |  |  | N/A |  |  | Dockets / Technical Data Sheets | R |  | SUB |  | R | Hold Point |  | All the PE pipe colors must comply with the respective service as mentioned in S12.3.3
1.2.2 |  | Bends: Pre-Fabricated HDPE bends |  |  |  | Each Bend | CIV Spec - S12.4.5 |  |  | Accept/Reject |  |  | N/A |  |  | Dockets / Technical Data Sheets | R |  | SUB |  | R | Hold Point
1.2.3 |  | Electrofusion Couplers |  |  |  | Each coupler | CIV Spec – S12.4.6 |  |  | Accept/Reject |  |  | N/A |  |  | Dockets / Technical Data Sheets | R |  | SUB |  | R | Hold Point
2 |  | Construction
2.1 |  | Pre-Condition Assessments
2.1.1 |  | Existing ducts/chambers to be removed |  |  |  | Each pipe | CIV Spec - S12.4.1 |  |  | Removed and disposed |  |  | N/A |  |  | Photos / Asbuilts | I |  | SUB |  | R |  |  | Once removed, all trenches to be backfilled to Subgrade level
2.1.2 |  | Survey Setout Pipe alignments, Position, Heights |  |  |  | Each Pipes/trench | CAD Models |  |  | Survey Setout Pipe alignments, Position, Manholes Position and Heights |  |  | GPS, Total Station |  |  | Setout CSV file, Photos/Visual | [7 empty] | Setout model and CSV provided by HCL
2.2 |  | Ducting
2.2.1 |  | Excavation Extents |  |  |  | Each element installed | CIV Spec - S12.4.2 CIV Spec - S4.5.9 (earthworks section) |  |  | N/A |  |  | Rotating level and GPS |  |  | N/A | M |  |  |  |  | Witness Point
2.2.2 |  | HDPE Ground Mat |  |  |  | Each Unit | Note 10 – DP0001- MMD-DRW-UT-F-Z- 3137 - 3139 |  |  | Accept/Reject |  |  | Photos, Dockets |  |  | N/A | I |  | SUB |  | R |  |  | HDPE ground protection Mat will be installed only in areas shown in the drawings.
2.2.2 |  | Bedding, surround |  |  |  | Per installation | As per drwgs min/ max fill |  |  | N/A |  |  | Rotating level / tape / staff |  |  | Photos, QVC | M |  | SUB |  | R |  |  | PAP7 for PE
2.2.3 |  | Pipe installation, Connection and jointing Electrofusion weld |  |  |  | Each pipe | CIV Spec - S12.4.5 CIV Spec - S12.4.6 |  |  | N/A |  |  | Observation |  |  | QVC, As-Builts | I |  | SUB |  | R | Witness Point |  | Caps to be used if lines not complete, All Welding to be performed under controlled Environmental conditions.
2.2.4 |  | Weld Testing |  |  |  | All welding Joints | CIV Spec - S12.5.2 |  |  | N/A |  |  | Visual Checks for each Weld and Peel Decohesion Testing for one in every 20 welds or Min 2 welds per line |  |  | QVC, Photos, Test Results | R |  | SUB |  | R | Witness Point
2.2.5 |  | Tracer Wires |  |  |  | Comms duct | CIV Spec - S12.4.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | Tracer Wire to 4mm2 multi-Strand Accept/Reject |  |  | Continuity Test (electronically generated tone and detector probe) |  |  | Photos, Test results, QC | I |  | SUB |  | R
2.2.6 |  | Inspection for Duct size, color, spacing, |  |  |  | All ducts | CIV Spec - S12.4.5 DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | N/A |  |  | N/A |  |  | Photos, QVC | M |  | SUB |  | I | Witness Point |  | Engineer to inspect before backfilling
2.2.7 |  | Warning Tapes/ marker tapes |  |  |  | Each Pipe | CIV Spec - S12.3.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | Warning Tapes must refer to respective Services. Installation heights must follow the typical trench details. |  |  | N/A |  |  | Photos | I |  | SUB |  | R
2.2.8 |  | Mag Slabs/Polymeric Slabs |  |  |  | HV and LV ducts | CIV Spec - S12.3.10 DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | Installation heights must follow the typical trench details. |  |  | N/A |  |  | Photos | I |  | SUB |  | R
2.2.9 |  | Draw Cord |  |  |  | Each pipe | CIV Spec - S12.3.8 S12.4.8 DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | Continuous draw cord and excess to be left at the ends of each duct |  |  | N/A |  |  | Photos | I |  | SUB |  | R
2010-02-02 |  | Pipe Cover and Backfilling |  |  |  | Each Pipe | CIV Spec - S4.4.5 Table 4.3 (Earthworks Section) DP001-MMD-DRW- UT-F-Z-3137 - 3139 |  |  | Backfilling CIV > 25 Bedding CIV to be confirmed |  |  | Clegg Hammer |  |  | Photos, QVC, Clegg Sheets | M |  | SUB |  | I
2011-02-02 |  | 3m Marker Balls |  |  |  | Each Item | CIV Spec – S12.4.5 |  |  | Installed above the HV ducts at each side of the point of crossing |  |  | Physical Product confirmation |  |  | Photos | I |  | SUB |  | R |  |  | Programmed 3m marker balls to be supplied by principal/client.
3 |  | Post Construction
3.1 |  | As-Builts
3.1.1 |  | As built Works |  |  |  | Each pipe | N/A |  |  | N/A |  |  | Surveyor Equipment, Total Station |  |  | Certified As- built PDF and DWG file | R |  | Sub |  | R
3.2 |  | Duct Condition
3.2.1 |  | Duct Cleaning and Proving |  |  |  | Each Duct | N/A |  |  | N/A |  |  | Brush and Mandrill |  |  | Photos/Videos | M |  | SUB |  | R | Witness Point
5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
6. Distribution Records
| Name |  |  |  | Position | [5 empty] | Company | [13 empty] | Date
| TBA | [9 empty] | Mott McDonalds
| TBA HAWKINS Inspection and Test Plan ¦ | [9 empty] | BECA | [13 empty] | Page 5 of 5
| TBA | [9 empty] | AIAL
 Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document
Note: The Engineer shall be provided a minimum of two (2) working days’ notice ahead of a requested inspection
HAWKINS Inspection and Test Plan ¦ Page 6 of 5