## Table 1
Client: AIAL | [8 empty] | Subcontractor: TBC | [7 empty] | Work Area: Civils – HOSR and SCH
Project Name: Domestic Jet Terminal | [8 empty] | Job No: HA0423 | [7 empty] | Subcontractor Representative: TBC
1. ITP Element: Stormwater
2. Revision Records
Rev No. |  |  | Revision Description | [11 empty] | Name of Author |  |  |  | Authorised by: |  |  |  | Date
1 |  |  | For Review | [11 empty] | Matt Cheyne |  |  |  | Matt Cheyne
3. Relevant Documents
Doc No. |  |  |  | Specification/ Drwgs/ Standards |  |  |  | Additional Info |  |  |  | Document No. |  | Specification/ Drwgs/ Standards | [8 empty] | Additional Info
1 |  |  |  | DP001-MMD-SPC-CV-Z-Z-0001 |  |  |  | Rev 02 |  |  |  | 6 |  | DP001-MMD-DRW-SW-F-Z-3270 - 3273 | [8 empty] | Rev 02
2 |  |  |  | Watercare Civil Construction Standard | [7 empty] | 7 |  | DP001-MMD-DRW-SW-G-Z-3200 - 3202 | [8 empty] | Rev 01
3 |  |  |  | DP001-MMD-DRW-SW-B-Z-3051 - 3064 |  |  |  | Rev 02 |  |  |  | 8 |  | DP001-MMD-DRW-SW-F-Z-3210 - 3212 | [8 empty] | Rev 01
4 |  |  |  | DP001-MMD-DRW-SW-D-Z-3100 - 3110 |  |  |  | Rev 02 |  |  |  | 9
5 |  |  |  | DP001-MMD-DRW-SW-F-Z-3240 - 3242 |  |  |  | Rev 01 |  |  |  | 10
4. Process
No. |  | Description Inspection / test |  |  |  | Frequency | Spec/standard |  |  |  | Acceptance Criteria |  | Measuring Devices |  |  | Reporting Format |  | Inspected by* |  |  |  | Hold Points Sign off |  | Remarks
[18 empty] | HCL |  | SC | Consult
1 |  | Material Compliance
1.1 |  | Fill Materials
1.1.1 |  | Bedding material GAP 20 for Concrete Pipes PAP 7 for PE pipes |  |  |  | Per Batch | CIV Spec - S9.3.11 AS/NZS 3725 |  |  |  | Accept/ Reject |  | N/A |  |  | Dockets / Material Data Sheets |  | R |  | SUB | R | Hold Point
1.1.1 |  | Backfill Material GAP65 or GAP40 or AP40 |  |  |  | Per Batch | CIV Spec - S9.3.12 CIV Spec - S4.4.5 |  |  |  | Accept / Reject |  | N/A |  |  | Dockets / Material Data Sheets |  | R |  | SUB | R | Hold Point
1.2 |  | Manholes + Pipes
1.2.1 |  | Pre-Cast Manholes |  |  |  | Each Unit | CIV Spec - S9.3.7 |  |  |  | Dockets/ Visual Checks |  | N/A |  |  | Dockets / Material Data |  | R |  | SUB | R | Hold Point
1.2.2 |  | Concrete Pipes: 375Ø RCRRJ Class 4 300Ø RCRRJ Class 4 225Ø RCRRJ Class 4 |  |  |  | Each Pipe | CIV Spec - S9.3.1 DP001-MMD-DRW-SW-D- Z-3100 to 3110 |  |  |  | Dockets/ Visual Checks |  | N/A |  |  | Dockets / Technical Data Sheets |  | R |  | SUB | R | Hold Point
1.2.3 |  | PE Pipes 280Ø ODPE 100 PN16 |  |  |  | Each Pipe | CIV Spec - 10.3.2 DP001-MMD-DRW-SW-B- Z-3051 to 3052 |  |  |  | Dockets/ Visual Checks |  | N/A |  |  | Dockets / Technical Data Sheets |  | R |  | SUB | R | Hold Point |  | Pipe colour tbc
1.2.4 |  | Access covers and frames Landside: 240 kN Class D Airside: 900 kN Class G |  |  |  | Each unit | CIV Spec - S9.3.8 |  |  |  | Shop drawings, Dockets/ Visual Checks |  | N/A |  |  | Dockets / Technical Data Sheets |  | R |  | SUB | R | Hold Point
1.3 |  | Concrete
1.3.1 |  | Insitu Concrete Mix Design |  |  |  | Each structure | CIV Spec - S13.3.1.2 |  |  |  | Accept / Reject |  | N/A |  |  | Design Mix |  | R |  | SUB | R | Hold point
1.4 |  | Reinforcement
1.4.1 |  | In-situ Reinforcement |  |  |  | Each Structure | CIV Spec - S14.3.1 |  |  |  | Accept/Reject |  | N/A |  |  | Dockets/ Technical Data Sheets |  | R |  | SUB | R
1.5 |  | Waterproofing
1.5.1 |  | Pipe & Pit Waterproofing – Hydrotite CJ 0725 or Similar |  |  |  | Each Pipe and Structure | DP001-MMD-DRW-SW-F-Z- 3211 Rev 1 |  |  |  | Accept/Reject |  | N/A |  |  | Dockets/ Technical Data Sheets
2 |  | Construction
2.1 |  | Pre-Condition Assessments
2.1.1 |  | Existing pipes / manholes to be removed or retained |  |  |  | Each pipe | CIV Spec - S9.4.1 |  |  |  | Removed and disposed OR sealed and capped off |  | N/A |  |  | Photos / Asbuilts |  | I |  | SUB | R | RFI if any found that are not expected |  | Survey on site/ asbuilts review capped off any found
2.1.2 |  | Survey Setout Pipe alignments, Position, Manholes Position and Heights |  |  |  | Each Manhole | N/A |  |  |  | Survey Setout records and Setout pegs |  | GPS, Total Station |  |  | Setout CSV file, Photos/Visual
2.2 |  | Pipeline Construction
2.2.1 |  | Excavation Extents |  |  |  | Each element installed | CIV Spec - S9.4.2 CIV Spec - S4.5.9 (earthworks section) |  |  |  | -20mm to +0mm o |  | Rotating level and GPS |  |  | N/A |  | M | [5 empty] | Watercare Civil Construction Standard C2 referenced
2.2.2 |  | Drainage manholes/ pits subgrade testing |  |  |  | Drainage manholes and pits: 2 tests at the base of excavation | CIV Spec - S4.6.2.2 (earthworks section) |  |  |  | Bearing Capacity 100kpa Shear Vane tests at 0.5m below the base and 1.0m below the base or Scala Penetrometer tests to 1.0m below the base |  | Shear Vane Test or Scala Test |  |  | Photos, Excel & pdf |  | M |  | SUB | W |  |  | If ground failing, Undercut 400mm and fill with 5Mpa flowable fill
2.2.3 |  | Pipe Trench subgrade testing |  |  |  | Each trench at every 5m | CIV Spec – S9.5.2.1 |  |  |  | Minimum CBR 3% |  | Scala Test |  |  | Excel & pdf |  | M |  | SUB | R | Witness point |  | If failing Undercutting required. Engineer to confirm the Undercut details
2.2.4 |  | Bedding, surround |  |  |  | Per installation | As per drwgs min/ max fill CIV Spec - S9.4.3 DP001-MMD-DRW-SW-F-Z- 3270 Rev 2 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1 |  |  |  | 0mm / +3mm |  | Rotating level / tape / staff |  |  | Photos, QVC |  | M |  | * |  |  |  | PAP7 for PE & PVC GAP 20 For Concrete Pipes
2.2.5 |  | Pipe installation, Connection and jointing |  |  |  | Each pipe | CIV Spec - S9.4.4 CIV Spec - S9.4.9 Watercare General Construction Standards Section 9-C3 DP001-MMD-DRW-SW-F-Z- 3270 Rev 2 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1 |  |  |  | Position tolerance +/- 10mm Level Tolerance +/-5mm Pipe grade as per design |  | Observation |  |  | QVC, Long section Check sheets, As-Builts |  | I |  |  |  | Witness Point |  | Caps to be used if lines not complete, Chases dug out for belled socket joints Rubber seals
2.2.6 |  | Backfilling |  |  |  | Each Pipe | CIV Spec - S4.4.4 Table 4.3 (Earthworks Section) DP001-MMD-DRW-SW-F-Z- 3270 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1 |  |  |  | CIV > 25 Clegg Test corelated to an NDM |  | Clegg Hammer |  |  | Photos, QVC, Clegg Sheets |  | M |  | SUB |  | Witness Point |  | Engineer to inspect before backfilling
2.3 |  | Manholes and structures installation
2.3.1 |  | Pre- Cast Manholes |  |  |  | Each Unit | CIV Spec - S9.4.6 Watercare General Civil Construction Standard 9C.4 |  |  |  | Position tolerances +/- 10mm Level Tolerance -0mm to + 3mm. Manufacturers installation guidelines |  | As-Builts |  |  | Photos
2.3.2 |  | Mass Concrete Stormwater Manholes (Thickening) |  |  |  | Each Unit | CIV Spec - S13.4.3.2 DP001-MMD-DRW-SW-F-Z- 3211 |  |  |  | 20MPa concrete |  | As-Builts |  |  | Photos | [7 empty] | Refer to Table 2 for dimensions in DP001- MMD-DRW-SW-F-Z- 321 Rev 3
2.3.3 |  | Insitu Manholes |  |  |  | Each Unit | CIV Spec - S13.3.1.2 Watercare Standard Section C4. Concrete |  |  |  | Position tolerances +/- 10mm Level Tolerance -0mm to + 3mm |  | As-Builts |  |  | Photos, QA check sheets
2.3.4 |  | Trench Excavation |  |  |  | Each Unit | CIV Spec - S13.4.1 |  |  |  | Scala test Min 3% CBR or Min Bearing capacity 100kPa |  | Shear Vane/Scala test |  |  | Photos, test Results PDF |  | R |  | SUB | R | Witness point
2.3.5 |  | Formwork |  |  |  | Each unit | CIV Spec - S13.4.2 |  |  |  | Shop drawings, |  | N/A |  |  | Photos, QC check Sheet, Engineer Inspection |  | M |  | SUB | I | Witness point
2.3.6 |  | Reinforcing Steel |  |  |  | Each Unit | CIV Spec - S14.4.2 CIV Spec - S14.4.8 CIV Spec - S14.4.11 CIV Spec - S13.5.1 DP001-MMD-DRW-SW-F-Z- 3210 |  |  |  | Plans and Shop drawings |  | N/A |  |  | Photos, QC check Sheet, Engineer Inspection | [5 empty] | Hold Point |  | Engineer to inspect before concreting
2.3.7 |  | Pipe Connection to Manholes |  |  |  | Each Unit | CIV Spec - S10.4.5 DP001-MMD-DRW-WW-F- Z-3203 Rev 2 DP001-MMD-DRW-SW-F-Z- 5034 Watercare Standards WW11 |  |  |  | Plans and Shop drawings |  | N/A |  |  | Photos, QVC | [7 empty] | For HDPE pipe connection refer to WW11 drawing
2.3.8 |  | Backfilling |  |  |  | Each Unit | CIV Spec - S13.4.4 Table 4.3 (Earthworks Section) |  |  |  | CIV > 25 Clegg Test corelated to an NDM |  | Clegg Hammer |  |  | Photos, QVC, Clegg Sheets |  | M |  | M |  | Witness Point |  | Engineer to inspect before backfilling
2.3.9 |  | Benching |  |  |  | Each Unit | DP001-MMD-DRW-F-Z- 3200 |  |  |  | Material Dockets |  | N/A |  |  | Drainage QVC. Photos | [7 empty] | Benching Rendered to Min 1 in 12 grade
2010-02-03 |  | Manhole Throat, Lid |  |  |  | Each Unit | WaterCare Standard WW6 and WW 7 DP001-MMD-DRW-SW-F-Z- 3210 DP001-MMD-DRW-SW-F-Z- 3211 |  |  |  | Materials Dockets, Shop Drawings |  | N/A |  |  | QVC, Photos | [7 empty] | Reference to Watercare General Construction drawings
3 |  | Post Construction
3.1 |  | As-Builts
3.1.1 |  | As built Works |  |  |  | Each pipe | CIV Spec - S9.4.10 |  |  |  | Position tolerance +/- 10mm Level Tolerance +/- 5m |  | Surveyor Equipment, Total Station |  |  | Certified As-built PDF and DWG file |  | R |  | Sub | R
3.2 |  | Pipeline Condition
3.2.1 |  | CCTV Survey |  |  |  | Each new pipe and Manholes | CIV Spec - S9.5.2.4 |  |  |  | Accept / Reject |  | CCTV |  |  | Video and Report |  | R |  | Sub | R | Hold point |  | Shall be carried out prior to final pavement surfacing for new and remaining pipes
5 Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
Results of Compactions | [12 empty] | EPD Certificate if applicable
Material Certificates
QC records
As Built
CCTV
6. Distribution Records
| Name |  |  |  | Position |  |  |  |  | Company | [14 empty] | Date
| TBA | [8 empty] | MMD
| TBA | [8 empty] | BECA
| TBA | [8 empty] | AIAL
 Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document
EFC- Eastern Forecourt HOSR- Head of Stand Road SCH – Super Cargo Highway