## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-CIV-007-A - Utility Services Ducting – High Voltage, Low Voltage and Communication systems | itp |  |  |  |  | ITP-CIV-007-A - Utility Services Ducting – High Voltage, Low Voltage and Communication systems
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding material PAP 7 for PE pipes - AP40 for Chambers
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.4
label | Acceptance Criteria - Accept/ Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.1.1 - Backfill Material - GAP65 or TNZ M/4 AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S12.3.5 CIV Spec - S4.4.5
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Pipes)
checkpoint | 1.2.1 - Pipes: 110 OD PE SDR 17, 160 OD PE SDR 17
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.3
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - All the PE pipe colors must comply with the respective service as mentioned in S12.3.3
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Bends: Pre-Fabricated HDPE bends
label | Frequency - Each Bend
label | Spec/standard - CIV Spec - S12.4.5
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.3 - Electrofusion Couplers
label | Frequency - Each coupler
label | Spec/standard - CIV Spec – S12.4.6
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Existing ducts/chambers to be removed
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.1
label | Acceptance Criteria - Removed and disposed
label | Measuring Devices - N/A
label | Reporting Format - Photos / Asbuilts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - Once removed, all trenches to be backfilled to Subgrade level
checkpoint | 2.1.2 - Survey Setout Pipe alignments, Position, Heights
label | Frequency - Each Pipes/trench
label | Spec/standard - CAD Models
label | Acceptance Criteria - Survey Setout Pipe alignments, Position, Manholes Position and Heights
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, Photos/Visual
label | Remarks - Setout model and CSV provided by HCL
section | 2 - Construction (2.2 - Ducting)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S12.4.2 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
label | Hold Points Sign off - Witness Point
checkpoint | 2.2.2 - HDPE Ground Mat
label | Frequency - Each Unit
label | Spec/standard - Note 10 – DP0001- MMD-DRW-UT-F-Z- 3137 - 3139
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - Photos, Dockets
label | Reporting Format - N/A
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - HDPE ground protection Mat will be installed only in areas shown in the drawings.
checkpoint | 2.2.2 - Bedding, surround
label | Frequency - Per installation
label | Spec/standard - As per drwgs min/ max fill
label | Acceptance Criteria - N/A
label | Measuring Devices - Rotating level / tape / staff
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - R
label | Remarks - PAP7 for PE
checkpoint | 2.2.3 - Pipe installation, Connection and jointing Electrofusion weld
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.4.5 CIV Spec - S12.4.6
label | Acceptance Criteria - N/A
label | Measuring Devices - Observation
label | Reporting Format - QVC, As-Builts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
label | Remarks - Caps to be used if lines not complete, All Welding to be performed under controlled Environmental conditions.
checkpoint | 2.2.4 - Weld Testing
label | Frequency - All welding Joints
label | Spec/standard - CIV Spec - S12.5.2
label | Acceptance Criteria - N/A
label | Measuring Devices - Visual Checks for each Weld and Peel Decohesion Testing for one in every 20 welds or Min 2 welds per line
label | Reporting Format - QVC, Photos, Test Results
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
checkpoint | 2.2.5 - Tracer Wires
label | Frequency - Comms duct
label | Spec/standard - CIV Spec - S12.4.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Tracer Wire to 4mm2 multi-Strand Accept/Reject
label | Measuring Devices - Continuity Test (electronically generated tone and detector probe)
label | Reporting Format - Photos, Test results, QC
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.6 - Inspection for Duct size, color, spacing,
label | Frequency - All ducts
label | Spec/standard - CIV Spec - S12.4.5 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - N/A
label | Measuring Devices - N/A
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.2.7 - Warning Tapes/ marker tapes
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S12.3.9 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Warning Tapes must refer to respective Services. Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.8 - Mag Slabs/Polymeric Slabs
label | Frequency - HV and LV ducts
label | Spec/standard - CIV Spec - S12.3.10 DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Installation heights must follow the typical trench details.
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.9 - Draw Cord
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S12.3.8 S12.4.8, DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Continuous draw cord and excess to be left at the ends of each duct
label | Measuring Devices - N/A
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
checkpoint | 2.2.10 - Pipe Cover and Backfilling
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S4.4.5 Table 4.3 (Earthworks Section), DP001-MMD-DRW- UT-F-Z-3137 - 3139
label | Acceptance Criteria - Backfilling CIV > 25 Bedding CIV to be confirmed
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Consult - I
checkpoint | 2.2.11 - 3m Marker Balls
label | Frequency - Each Item
label | Spec/standard - CIV Spec – S12.4.5
label | Acceptance Criteria - Installed above the HV ducts at each side of the point of crossing
label | Measuring Devices - Physical Product confirmation
label | Reporting Format - Photos
label | HCL - I
label | SC - SUB
label | Consult - R
label | Remarks - Programmed 3m marker balls to be supplied by principal/client.
section | 3 - Post Construction (3.1 - As-Builts)
checkpoint | 3.1.1 - As built Works
label | Frequency - Each pipe
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As- built PDF and DWG file
label | HCL - R
label | SC - Sub
label | Consult - R
section | 3 - Post Construction (3.2 - Duct Condition)
checkpoint | 3.2.1 - Duct Cleaning and Proving
label | Frequency - Each Duct
label | Spec/standard - N/A
label | Acceptance Criteria - N/A
label | Measuring Devices - Brush and Mandrill
label | Reporting Format - Photos/Videos
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness Point
checkpoint-no-status | Document Deliverables
textbox | (The documents listed below shall be completed and compiled during the course of the construction)
checkpoint | Distribution Records
signoff | Signoff
checklist | ITP-CIV-0005-01 - Stormwater | itp |  |  |  |  | ITP-CIV-0005-01 - Stormwater
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding material GAP 20 for Concrete Pipes - PAP 7 for PE pipes
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S9.3.11 AS/NZS 3725
label | Acceptance Criteria - Accept/ Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.1.1 - Backfill Material - GAP65 or TNZ M/4 AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S9.3.12 CIV Spec - S4.4.5
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Manholes + Pipes)
checkpoint | 1.2.1 - Pre-Cast Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S9.3.7
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Concrete Pipes: 375Ø RCRRJ Class 4, 300Ø RCRRJ Class 4, 225Ø RCRRJ Class 4
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S9.3.1, DP001-MMD-DRW-SW-D- Z-3100 to 3110
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.3 - PE Pipes: 280Ø ODPE 100 PN16
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - 10.3.2, DP001-MMD-DRW-SW-B- Z-3051 to 3052
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - Pipe colour tbc
holdpoint | HOLD POINT
checkpoint | 1.2.4 - Access covers and frames Landside: 240 kN Class D Airside: 900 kN Class G
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S9.3.8
label | Acceptance Criteria - Shop drawings, Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.3 - Concrete)
checkpoint | 1.3.1 - Insitu Concrete Mix Design
label | Frequency - Each structure
label | Spec/standard - CIV Spec - S13.3.1.2
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Design Mix
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.4 - Reinforcement)
checkpoint | 1.4.1 - In-situ Reinforcement
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.3.1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets/ Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
section | 1 - Material Compliance (1.5 - Waterproofing)
checkpoint | 1.5.1 - Pipe & Pit Waterproofing – Hydrotite CJ 0725 or Similar
label | Frequency - Each Pipe and Structure
label | Spec/standard - DP001-MMD-DRW-SW-F-Z- 3211 Rev 1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets/ Technical Data Sheets
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Existing pipes / manholes to be removed or retained
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.1
label | Acceptance Criteria - Removed and disposed OR sealed and capped off
label | Measuring Devices - N/A
label | Reporting Format - Photos / Asbuilts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - RFI if any found that are not expected
label | Remarks - Survey on site/ asbuilts review capped off any found
checkpoint | 2.1.2 - Survey Setout - Pipe alignments, Position, Manholes Position and Heights
label | Frequency - Each Manhole
label | Spec/standard - N/A
label | Acceptance Criteria - Survey Setout records and Setout pegs
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, Photos/Visual
section | 2 - Construction (2.2 - Pipeline Construction)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S9.4.2 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - -20mm to +0mm o
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
label | Remarks - Watercare Civil Construction Standard C2 referenced
checkpoint | 2.2.2 - Drainage manholes/ pits subgrade testing
label | Frequency - Drainage manholes and pits: 2 tests at the base of excavation
label | Spec/standard - CIV Spec - S4.6.2.2 (earthworks section)
label | Acceptance Criteria - Bearing Capacity 100kpa
label | ○ Shear Vane tests at 0.5m below the base and 1.0m below the base or Scala Penetrometer tests to 1.0m below the base
label | Measuring Devices - Shear Vane Test or Scala Test
label | Reporting Format - Photos, Excel & pdf
label | HCL - M
label | SC - SUB
label | Consult - W
label | Remarks - If ground failing, Undercut 400mm and fill with 5Mpa flowable fill
checkpoint | 2.2.3 - Pipe Trench subgrade testing
label | Frequency - Each trench at every 5m
label | Spec/standard - TBC (Email from Dana – MM)
label | Acceptance Criteria - Minimum CBR 3%
label | Measuring Devices - Scala Test
label | Reporting Format - Excel & pdf
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness point
label | Remarks - If failing Undercutting required. Engineer to confirm the Undercut details
checkpoint | 2.2.4 - Bedding, surround
label | Frequency - Per installation
label | Spec/standard - As per drwgs min/ max fill CIV Spec - S9.4.3
label | ○ DP001-MMD-DRW-SW-F-Z- 3270 Rev 2
label | ○ DP001-MMD-DRW-SW-F-Z- 5031 Rev 1
label | Acceptance Criteria - 0mm / +3mm
label | Measuring Devices - Rotating level / tape / staff
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - *
label | Remarks - PAP7 for PE & PVC GAP 20 For Concrete Pipes
checkpoint | 2.2.5 - Pipe installation, Connection and jointing
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.4 CIV Spec - S9.4.9
label | ○ Watercare General Construction Standards Section 9-C3
label | ○ DP001-MMD-DRW-SW-F-Z- 3270 Rev 2
label | ○ DP001-MMD-DRW-SW-F-Z-
label | ○ 5031 Rev 1
label | Acceptance Criteria - Position tolerance +/- 10mm
label | ○ Level Tolerance +/-5mm
label | ○ Pipe grade as per design
label | Measuring Devices - Observation
label | Reporting Format - QVC, Long section Check sheets, As-Builts
label | HCL - I
label | Hold Points Sign off - Witness Point
label | Remarks - Caps to be used if lines not complete, Chases dug out for belled socket joints Rubber seals
checkpoint | 2.2.6 - Pipe Cover and Backfilling
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S4.4.4 Table 4.3 (Earthworks Section)
label | ○ DP001-MMD-DRW-SW-F-Z- 3270
label | ○ DP001-MMD-DRW-SW-F-Z- 5031 Rev 1
label | Acceptance Criteria - CIV > 24
label | ○ Clegg Test corelated to an NDM
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.2.7 - Pipe Testing - Joint Testing for PE Pressure and Leakage test
label | Frequency - From MH to MH
label | Spec/standard - CIV Spec - 10.5.3 Watercare General construction Standard 10.3 and 10.5
label | Acceptance Criteria - Low Pressure Air Test or Hydrostatic Test
label | Measuring Devices - Air test system
label | Reporting Format - Photos, Videos
label | Hold Points Sign off - Witness Point
label | Remarks - *Final detail to be confirmed with updated spec*
section | 2 - Construction (2.3 - Manholes and structures installation)
checkpoint | 2.3.1 - Pre- Cast Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S9.4.6 Watercare General Civil Construction Standard 9C.4
label | Acceptance Criteria - Position tolerances +/- 10mm
label | ○ Level Tolerance -0mm to + 3mm.
label | ○ Manufacturers installation guidelines
label | Measuring Devices - As-Builts
label | Reporting Format - Photos
checkpoint | 2.3.2 - Mass Concrete Stormwater Manholes (Thickening)
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.3.2, DP001-MMD-DRW-SW-F-Z- 3211
label | Acceptance Criteria - 20MPa concrete
label | Measuring Devices - As-Builts
label | Reporting Format - Photos
label | Remarks - Refer for Table 2 for dimensions
checkpoint | 2.3.3 - Insitu Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.3.1.2 Watercare Standard Section C4. Concrete
label | Acceptance Criteria - Position tolerances +/- 10mm
label | ○ Level Tolerance -0mm to + 3mm
label | Measuring Devices - As-Builts
label | Reporting Format - Photos, QA check sheets
checkpoint | 2.3.4 - Trench Excavation
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.1
label | Acceptance Criteria - Scala test Min 3% CBR or Min Bearing capacity 100kPa
label | Measuring Devices - Shear Vane/Scala test
label | Reporting Format - Photos, test Results PDF
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness point
checkpoint | 2.3.5 - Formwork
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S13.4.2
label | Acceptance Criteria - Shop drawings,
label | Measuring Devices - N/A
label | Reporting Format - Photos, QC check Sheet, Engineer Inspection
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Witness point
checkpoint | 2.3.6 - Reinforcing Steel
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S14.4.2
label | ○ CIV Spec - S14.4.8
label | ○ CIV Spec - S14.4.11
label | ○ CIV Spec - S13.5.1
label | ○ DP001-MMD-DRW-SW-F-Z- 3210
label | Acceptance Criteria - Plans and Shop drwaings
label | Measuring Devices - N/A
label | Reporting Format - Photos, QC check Sheet, Engineer Inspection
label | Hold Points Sign off - Hold Point
label | Remarks - Engineer to inspect before concreting
holdpoint | HOLD POINT
checkpoint | 2.3.7 - Pipe Connection to Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S10.4.5
label | ○ DP001-MMD-DRW-WW-F- Z-3203 Rev 2
label | ○ DP001-MMD-DRW-SW-F-Z- 5034
label | ○ Watercare Standards WW11
label | Acceptance Criteria - Plans and Shop drawings
label | Measuring Devices - N/A
label | Reporting Format - Photos, QVC
label | Remarks - For HDPE pipe connection refer to WW11 drawing
checkpoint | 2.3.8 - Backfilling
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.4, Table 4.3 (Earthworks Section)
label | Acceptance Criteria - CIV > 24
label | ○ Clegg Test corelated to an NDM
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - M
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.3.9 - Benching
label | Frequency - Each Unit
label | Spec/standard - DP001-MMD-DRW-F-Z- 3200
label | Acceptance Criteria - Material Dockets
label | Measuring Devices - N/A
label | Reporting Format - Drainage QVC. Photos
label | Remarks - Benching Rendered to Min 1 in 12 grade
checkpoint | 2.3.10 - Manhole Throat, Lid
label | Frequency - Each Unit
label | Spec/standard - WaterCare Standard WW6 and WW 7
label | ○ DP001-MMD-DRW-SW-F-Z- 3210
label | ○ DP001-MMD-DRW-SW-F-Z- 3211
label | Acceptance Criteria - Materials Dockets, Shop Drawings
label | Measuring Devices - N/A
label | Reporting Format - QVC, Photos
label | Remarks - Reference to Watercare General Construction drawings
section | 3 - Post Construction (3.1 - As-Builts)
checkpoint | 3.1.1 - As built Works
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.10
label | Acceptance Criteria - Position tolerance +/- 10mm
label | ○ Level Tolerance +/- 5m
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As-built PDF and DWG file
label | HCL - R
label | SC - Sub
label | Consult - R
section | 3 - Post Construction (3.2 - Pipeline Condition)
checkpoint | 3.2.1 - CCTV Survey
label | Frequency - Each new pipe and Manholes
label | Spec/standard - CIV Spec - S9.5.2.4
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - CCTV
label | Reporting Format - Video and Report
label | HCL - R
label | SC - Sub
label | Consult - R
label | Hold Points Sign off - Hold point
label | Remarks - Shall be carried out prior to final pavement surfacing for new and remaining pipes
holdpoint | HOLD POINT
checkpoint-no-status | Document Deliverables
label | (The documents listed below shall be completed and compiled during the course of the construction)
label | ○ Results of Compactions
label | ○ Material Certificates
label | ○ QC records
label | ○ As Built
label | ○ CCTV
label | ○ EPD Certificate if applicable
checkpoint | Distribution Records
signoff | Signoff
checklist | ITP-CIV-0005-A - Stormwater | itp |  |  |  |  | ITP-CIV-0005-A - Stormwater
section | 1 - Material Compliance (1.1 - Fill Materials)
checkpoint | 1.1.1 - Bedding material GAP 20 for Concrete Pipes - PAP 7 for PE pipes
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S9.3.11 AS/NZS 3725
label | Acceptance Criteria - Accept/ Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.1.1 - Backfill Material - GAP65 or GAP40 or AP40
label | Frequency - Per Batch
label | Spec/standard - CIV Spec - S9.3.12 CIV Spec - S4.4.5
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.2 - Manholes + Pipes)
checkpoint | 1.2.1 - Pre-Cast Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S9.3.7
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Material Data
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.2 - Concrete Pipes: 375Ø RCRRJ Class 4, 300Ø RCRRJ Class 4, 225Ø RCRRJ Class 4
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S9.3.1 DP001-MMD-DRW-SW-D- Z-3100 to 3110
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
checkpoint | 1.2.3 - PE Pipes: 280Ø ODPE 100 PN16
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - 10.3.2 DP001-MMD-DRW-SW-B- Z-3051 to 3052
label | Acceptance Criteria - Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - Pipe colour tbc
holdpoint | HOLD POINT
checkpoint | 1.2.4 - Access covers and frames Landside: 240 kN Class D Airside: 900 kN Class G
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S9.3.8
label | Acceptance Criteria - Shop drawings, Dockets/ Visual Checks
label | Measuring Devices - N/A
label | Reporting Format - Dockets / Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold Point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.3 - Concrete)
checkpoint | 1.3.1 - Insitu Concrete Mix Design
label | Frequency - Each structure
label | Spec/standard - CIV Spec - S13.3.1.2
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - N/A
label | Reporting Format - Design Mix
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Hold point
holdpoint | HOLD POINT
section | 1 - Material Compliance (1.4 - Reinforcement)
checkpoint | 1.4.1 - In-situ Reinforcement
label | Frequency - Each Structure
label | Spec/standard - CIV Spec - S14.3.1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets/ Technical Data Sheets
label | HCL - R
label | SC - SUB
label | Consult - R
section | 1 - Material Compliance (1.5 - Waterproofing)
checkpoint | 1.5.1 - Pipe & Pit Waterproofing – Hydrotite CJ 0725 or Similar
label | Frequency - Each Pipe and Structure
label | Spec/standard - DP001-MMD-DRW-SW-F-Z- 3211 Rev 1
label | Acceptance Criteria - Accept/Reject
label | Measuring Devices - N/A
label | Reporting Format - Dockets/ Technical Data Sheets
section | 2 - Construction (2.1 - Pre-Condition Assessments)
checkpoint | 2.1.1 - Existing pipes / manholes to be removed or retained
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.1
label | Acceptance Criteria - Removed and disposed OR sealed and capped off
label | Measuring Devices - N/A
label | Reporting Format - Photos / Asbuilts
label | HCL - I
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - RFI if any found that are not expected
label | Remarks - Survey on site/ asbuilts review capped off any found
checkpoint | 2.1.2 - Survey Setout - Pipe alignments, Position, Manholes Position and Heights
label | Frequency - Each Manhole
label | Spec/standard - N/A
label | Acceptance Criteria - Survey Setout records and Setout pegs
label | Measuring Devices - GPS, Total Station
label | Reporting Format - Setout CSV file, Photos/Visual
section | 2 - Construction (2.2 - Pipeline Construction)
checkpoint | 2.2.1 - Excavation Extents
label | Frequency - Each element installed
label | Spec/standard - CIV Spec - S9.4.2 CIV Spec - S4.5.9 (earthworks section)
label | Acceptance Criteria - -20mm to +0mm o
label | Measuring Devices - Rotating level and GPS
label | Reporting Format - N/A
label | HCL - M
label | Remarks - Watercare Civil Construction Standard C2 referenced
checkpoint | 2.2.2 - Drainage manholes/pits subgrade testing
label | Frequency - Drainage manholes and pits: 2 tests at the base of excavation
label | Spec/standard - CIV Spec - S4.6.2.2 (earthworks section)
label | Acceptance Criteria - Bearing Capacity 100kpa Shear Vane tests at 0.5m below the base and 1.0m below the base or Scala Penetrometer tests to 1.0m below the base
label | Measuring Devices - Shear Vane Test or Scala Test
label | Reporting Format - Photos, Excel & pdf
label | HCL - M
label | SC - SUB
label | Consult - W
label | Remarks - If ground failing, Undercut 400mm and fill with 5Mpa flowable fill
checkpoint | 2.2.3 - Pipe Trench subgrade testing
label | Frequency - Each trench at every 5m
label | Spec/standard - CIV Spec – S9.5.2.1
label | Acceptance Criteria - Minimum CBR 3%
label | Measuring Devices - Scala Test
label | Reporting Format - Excel & pdf
label | HCL - M
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness point
label | Remarks - If failing Undercutting required. Engineer to confirm the Undercut details
checkpoint | 2.2.4 - Bedding, surround
label | Frequency - Per installation
label | Spec/standard - As per drwgs min/ max fill CIV Spec - S9.4.3 DP001-MMD-DRW-SW-F-Z- 3270 Rev 2 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1
label | Acceptance Criteria - 0mm / +3mm
label | Measuring Devices - Rotating level / tape / staff
label | Reporting Format - Photos, QVC
label | HCL - M
label | SC - *
label | Remarks - PAP7 for PE & PVC GAP 20 For Concrete Pipes
checkpoint | 2.2.5 - Pipe installation, Connection and jointing
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.4 CIV Spec - S9.4.9 Watercare General Construction Standards Section 9-C3 DP001-MMD-DRW-SW-F-Z- 3270 Rev 2 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1
label | Acceptance Criteria - Position tolerance +/- 10mm Level Tolerance +/-5mm Pipe grade as per design
label | Measuring Devices - Observation
label | Reporting Format - QVC, Long section Check sheets, As-Builts
label | HCL - I
label | Hold Points Sign off - Witness Point
label | Remarks - Caps to be used if lines not complete, Chases dug out for belled socket joints Rubber seals
checkpoint | 2.2.6 - Backfilling
label | Frequency - Each Pipe
label | Spec/standard - CIV Spec - S4.4.4 Table 4.3 (Earthworks Section) DP001-MMD-DRW-SW-F-Z- 3270 DP001-MMD-DRW-SW-F-Z- 5031 Rev 1
label | Acceptance Criteria - CIV > 25 Clegg Test corelated to an NDM
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - SUB
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
section | 2 - Construction (2.3 - Manholes and structures installation)
checkpoint | 2.3.1 - Pre-Cast Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S9.4.6 Watercare General Civil Construction Standard 9C.4
label | Acceptance Criteria - Position tolerances +/- 10mm Level Tolerance -0mm to + 3mm. Manufacturers installation guidelines
label | Measuring Devices - As-Builts
label | Reporting Format - Photos
checkpoint | 2.3.2 - Mass Concrete Stormwater Manholes (Thickening)
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.3.2 DP001-MMD-DRW-SW-F-Z- 3211
label | Acceptance Criteria - 20MPa concrete
label | Measuring Devices - As-Builts
label | Reporting Format - Photos
label | Remarks - Refer to Table 2 for dimensions in DP001- MMD-DRW-SW-F-Z- 321 Rev 3
checkpoint | 2.3.3 - Insitu Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.3.1.2 Watercare Standard Section C4. Concrete
label | Acceptance Criteria - Position tolerances +/- 10mm Level Tolerance -0mm to + 3mm
label | Measuring Devices - As-Builts
label | Reporting Format - Photos, QA check sheets
checkpoint | 2.3.4 - Trench Excavation
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.1
label | Acceptance Criteria - Scala test Min 3% CBR or Min Bearing capacity 100kPa
label | Measuring Devices - Shear Vane/Scala test
label | Reporting Format - Photos, test Results PDF
label | HCL - R
label | SC - SUB
label | Consult - R
label | Hold Points Sign off - Witness point
checkpoint | 2.3.5 - Formwork
label | Frequency - Each unit
label | Spec/standard - CIV Spec - S13.4.2
label | Acceptance Criteria - Shop drawings,
label | Measuring Devices - N/A
label | Reporting Format - Photos, QC check Sheet, Engineer Inspection
label | HCL - M
label | SC - SUB
label | Consult - I
label | Hold Points Sign off - Witness point
checkpoint | 2.3.6 - Reinforcing Steel
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S14.4.2 CIV Spec - S14.4.8 CIV Spec - S14.4.11 CIV Spec - S13.5.1 DP001-MMD-DRW-SW-F-Z- 3210
label | Acceptance Criteria - Plans and Shop drawings
label | Measuring Devices - N/A
label | Reporting Format - Photos, QC check Sheet, Engineer Inspection
label | Hold Points Sign off - Hold Point
label | Remarks - Engineer to inspect before concreting
holdpoint | HOLD POINT
checkpoint | 2.3.7 - Pipe Connection to Manholes
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S10.4.5 DP001-MMD-DRW-WW-F- Z-3203 Rev 2 DP001-MMD-DRW-SW-F-Z- 5034 Watercare Standards WW11
label | Acceptance Criteria - Plans and Shop drawings
label | Measuring Devices - N/A
label | Reporting Format - Photos, QVC
label | Remarks - For HDPE pipe connection refer to WW11 drawing
checkpoint | 2.3.8 - Backfilling
label | Frequency - Each Unit
label | Spec/standard - CIV Spec - S13.4.4 Table 4.3 (Earthworks Section)
label | Acceptance Criteria - CIV > 25 Clegg Test corelated to an NDM
label | Measuring Devices - Clegg Hammer
label | Reporting Format - Photos, QVC, Clegg Sheets
label | HCL - M
label | SC - M
label | Hold Points Sign off - Witness Point
label | Remarks - Engineer to inspect before backfilling
checkpoint | 2.3.9 - Benching
label | Frequency - Each Unit
label | Spec/standard - DP001-MMD-DRW-F-Z- 3200
label | Acceptance Criteria - Material Dockets
label | Measuring Devices - N/A
label | Reporting Format - Drainage QVC. Photos
label | Remarks - Benching Rendered to Min 1 in 12 grade
checkpoint | 2.3.10 - Manhole Throat, Lid
label | Frequency - Each Unit
label | Spec/standard - WaterCare Standard WW6 and WW 7 DP001-MMD-DRW-SW-F-Z- 3210 DP001-MMD-DRW-SW-F-Z- 3211
label | Acceptance Criteria - Materials Dockets, Shop Drawings
label | Measuring Devices - N/A
label | Reporting Format - QVC, Photos
label | Remarks - Reference to Watercare General Construction drawings
section | 3 - Post Construction (3.1 - As-Builts)
checkpoint | 3.1.1 - As built Works
label | Frequency - Each pipe
label | Spec/standard - CIV Spec - S9.4.10
label | Acceptance Criteria - Position tolerance +/- 10mm Level Tolerance +/- 5m
label | Measuring Devices - Surveyor Equipment, Total Station
label | Reporting Format - Certified As-built PDF and DWG file
label | HCL - R
label | SC - Sub
label | Consult - R
section | 3 - Post Construction (3.2 - Pipeline Condition)
checkpoint | 3.2.1 - CCTV Survey
label | Frequency - Each new pipe and Manholes
label | Spec/standard - CIV Spec - S9.5.2.4
label | Acceptance Criteria - Accept / Reject
label | Measuring Devices - CCTV
label | Reporting Format - Video and Report
label | HCL - R
label | SC - Sub
label | Consult - R
label | Hold Points Sign off - Hold point
label | Remarks - Shall be carried out prior to final pavement surfacing for new and remaining pipes
holdpoint | HOLD POINT
checkpoint-no-status | Document Deliverables
label | (The documents listed below shall be completed and compiled during the course of the construction)
label | ○ Results of Compactions
label | ○ Material Certificates
label | ○ QC records
label | ○ As Built
label | ○ CCTV
label | ○ EPD Certificate if applicable
checkpoint | Distribution Records
signoff | Signoff