## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - CCTV Bases | itp
section | CCTV Bases
checkpoint | Design
label | TEST REQUIRED - PS1 design for CCTV bases
label | INSPECTION BY - UCCL/MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to construction
label | ACCEPTANCE CRITERIA - PS1 design approval by Meridian
label | UCCL - S
label | CLIENT - R
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill/site concrete
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Formwork
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
label | UCCL - H
label | CLIENT - W
checkpoint | Steel Reinforcing
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
label | UCCL - H
label | CLIENT - W
checkpoint | Post Pour Inspection
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed. Concrete Docket, Photos.
label | UCCL - W
label | CLIENT - W
checklist | ITP - Lightning Tower Bases | itp
section | Tank Slab
checkpoint | Design
label | TEST REQUIRED - PS1 design for lightning bases
label | INSPECTION BY - UCCL/MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to construction
label | ACCEPTANCE CRITERIA - PS1 design approval by Meridian
label | UCCL - S
label | CLIENT - R
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill/site concrete
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Formwork
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL/RSV Consulting
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
label | UCCL - H
label | CLIENT - W
checkpoint | Steel Reinforcing
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL/RSV Consulting
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
label | UCCL - H
label | CLIENT - W
checkpoint | Post Pour Inspection
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed. Concrete Docket, Photos
label | UCCL - W
label | CLIENT - W
checklist | ITP - Transformer Foundations and HV Ducts | itp
section | Transformer Foundations (Installation)
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Hardfill Layer
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of hardfill layer
label | ACCEPTANCE CRITERIA - Hardfill levels to line and level and within tolerances
label | UCCL - W
label | CLIENT - W
checkpoint | Installation
label | TEST REQUIRED - Visual inspection, As-Built Positions
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Foundations installed to correct line and level and within tolerances. As-built drawings.
label | UCCL - S
label | CLIENT - R
section | High Voltage Ducts
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing thermal bedding
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Hardfill Layer
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of hardfill layer
label | ACCEPTANCE CRITERIA - Hardfill levels to line and level and within tolerances
label | UCCL - W
label | CLIENT - W
checkpoint | Ducting QA
label | TEST REQUIRED - Duct Inspection Record
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Per trench
label | ACCEPTANCE CRITERIA - Duct Inspection Checklist completed per trench
label | UCCL - S
label | CLIENT - W
checkpoint | Thermal Backfill
label | SPECIFICATION REFERENCE - Plateau test accepted in place of MDD
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following installation of ducts, where specified
label | ACCEPTANCE CRITERIA - 10 pasess with plate compactor, per MELNZ-RFI-000310
label | UCCL - W
label | CLIENT - W
checkpoint | Sand Backfill
label | SPECIFICATION REFERENCE - Plateau test accepted in place of MDD
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following installation of ducts, where specified
label | ACCEPTANCE CRITERIA - Self compaction of sand, as per MELNZ-RFI-000310
label | UCCL - W
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R
checklist | ITP - Fire Water Tank | itp
section | Tank Slab
checkpoint | Design
label | TEST REQUIRED - PS1 design for tank slab
label | INSPECTION BY - UCCL/MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to construction
label | ACCEPTANCE CRITERIA - PS1 design approval by Meridian
label | UCCL - S
label | CLIENT - R
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill/site concrete
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Hardfill Layer
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of hardfill layer
label | ACCEPTANCE CRITERIA - Hardfill levels to line and level and within tolerances
label | UCCL - W
label | CLIENT - W
checkpoint | Concrete Mix Design
label | TEST REQUIRED - Mix design to be approved prio to use
label | INSPECTION BY - UCCL/RSV Consulting
label | TASK TIMING OR TASK FREQUENCY - Prior to use on site
label | ACCEPTANCE CRITERIA - Mix design as per PS1 design and approved by RSV Consulting
label | UCCL - S
label | CLIENT - A
checkpoint | Formwork
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL/RSV Consulting
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
label | UCCL - H
label | CLIENT - W
checkpoint | Steel Reinforcing
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL/RSV Consulting
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
label | UCCL - H
label | CLIENT - W
checkpoint | Foundation Earth
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Earth bars and cables installed as per instruction by MEL.
label | UCCL - H
label | CLIENT - H
checkpoint | Post Pour Inspection
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet ot be completed. PS4 sign off.
label | UCCL - W
label | CLIENT - W
section | Pump Slab
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill/site concrete
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Hardfill Layer
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of hardfill layer
label | ACCEPTANCE CRITERIA - Hardfill levels to line and level and within tolerances
label | UCCL - W
label | CLIENT - W
checkpoint | Formwork
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Dimensional check completed and within tolerances. Formwork installed inspected as being suitable for pouring concrete.
label | UCCL - H
label | CLIENT - W
checkpoint | Steel Reinforcing
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Steel installed as per IFC drawings. Grade of steel as specified. Number, size and spacing of bars as per IFC drawings.
label | UCCL - H
label | CLIENT - W
checkpoint | Foundation Earth
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - Earth bars and cables installed as per instruction by MEL.
label | UCCL - H
label | CLIENT - H
checkpoint | Post Pour Inspection
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet ot be completed.
label | UCCL - W
label | CLIENT - W
section | Fire Water Tank
checkpoint | Design
label | TEST REQUIRED - PS1 design for tank
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to construction
label | ACCEPTANCE CRITERIA - PS1 design approval by Meridian
label | UCCL - S
label | CLIENT - R
checkpoint | Tank Installation
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of tank installation
label | ACCEPTANCE CRITERIA - Record of installation. QA report by Tasman Tanks installer.
label | UCCL - W
label | CLIENT - W
checkpoint | Tank Completion
label | TEST REQUIRED - PS4 for tank installation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of tank installation
label | ACCEPTANCE CRITERIA - Signed PS4
label | UCCL - W
label | CLIENT - R
checklist | ITP - Stormwater (incl. Fire Water Pond) | itp
section | Stormwater
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Backfill
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of backfill layers
label | ACCEPTANCE CRITERIA - Backfill compacted and to line and level within tolerances
label | UCCL - W
label | CLIENT - W
checkpoint | Hush Pit Installation
label | TEST REQUIRED - Visual inspection, As-Built Positions
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Installed to correct line and level and within tolerances.
label | UCCL - W
label | CLIENT - W
checkpoint | Manhole Installation
label | TEST REQUIRED - Visual inspection, As-Built Positions
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Installed to correct line and level and within tolerances.
label | UCCL - W
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R
section | Firewater Pond
checkpoint | Pond Liner
label | TEST REQUIRED - Supplier/Installer Documentation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Supplier/installer documentation provided to Meridian on Completion
label | UCCL - W
label | CLIENT - W
checkpoint | Backfill on Liner
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Material specifications, Photos
label | UCCL - W
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R
checklist | ITP - Streetlights | itp
section | Streetlights
checkpoint | Design
label | TEST REQUIRED - PS1 design for streetlight installation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to construction
label | ACCEPTANCE CRITERIA - PS1 design approval by Meridian
label | UCCL - S
label | CLIENT - R
checkpoint | Subgrade
label | TEST REQUIRED - Scala test of subgrade
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - After excavation, prior to placing hardfill/site concrete
label | ACCEPTANCE CRITERIA - Scala achieves minimum 3 blows per 100mm
label | UCCL - W
label | CLIENT - W
checkpoint | Backfill
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On installation of street light bases
label | ACCEPTANCE CRITERIA - Backfill material meets specifications
label | UCCL - W
label | CLIENT - W
checkpoint | Electrical Installation
label | TEST REQUIRED - Installer documentation (COC)
label | INSPECTION BY - UCCL/NorthPower
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Installer documentation (COC) provided to Meridian
label | UCCL - W
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R
checklist | ITP - Watermain | itp
section | Watermain
checkpoint | Material Supply
label | TEST REQUIRED - Material dockets
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On receiving materials
label | ACCEPTANCE CRITERIA - Materials meet specification
label | UCCL - S
label | CLIENT - W
checkpoint | Butt Welding
label | TEST REQUIRED - Weld Records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Test weld tensile report. Welds meet specification.
label | UCCL - W
label | CLIENT - W
checkpoint | EF Welding
label | TEST REQUIRED - Weld Records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Welds meet specification.
label | UCCL - W
label | CLIENT - W
checkpoint | Pressure Testing
label | TEST REQUIRED - Pressure test records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation, prior to charging the system
label | ACCEPTANCE CRITERIA - Pressure test passes
label | UCCL - H
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R
checklist | ITP - Wastewater | itp
section | Wastewater
checkpoint | Material Supply
label | TEST REQUIRED - Material dockets
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On receiving materials
label | ACCEPTANCE CRITERIA - Materials meet specification
label | UCCL - S
label | CLIENT - W
checkpoint | Mini-Manholes
label | TEST REQUIRED - Installation
checkpoint | EF Welding
label | TEST REQUIRED - Weld Records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - Welds meet specification.
label | UCCL - W
label | CLIENT - W
checkpoint | Connection
label | TEST REQUIRED - Council Inspection/Approval
label | INSPECTION BY - WDC
label | TASK TIMING OR TASK FREQUENCY - On completion of installation, prior to backfilling
label | ACCEPTANCE CRITERIA - Council approval
label | UCCL - H
label | CLIENT - H
checkpoint | Backfill and Reinstatement
label | TEST REQUIRED - Backfill records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of reinstatement
label | ACCEPTANCE CRITERIA - Backfill and resintatement meets specification
label | UCCL - W
label | CLIENT - W
checkpoint | As-Built Survey Drawings
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - On completion of installation
label | ACCEPTANCE CRITERIA - As-built drawings provided to Meridian
label | UCCL - S
label | CLIENT - R