## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Rough In (BUILDING-B)
| Scope |  |  | Rough In | BUILDING-B
Rows
|  | Level-2 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-2 | Apartment Wall Closure
|  | Level-2 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-2 | Apartment Ceiling Closure
|  | Level-3 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-3 | Apartment Wall Closure
|  | Level-3 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-3 | Apartment Ceiling Closure
|  | Level-4 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-4 | Apartment Wall Closure
|  | Level-4 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-4 | Apartment Ceiling Closure
|  | Level-5 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-5 | Apartment Wall Closure
|  | Level-5 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-5 | Apartment Ceiling Closure
|  | Level-6 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-6 | Apartment Wall Closure
|  | Level-6 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-6 | Apartment Ceiling Closure
|  | Level-7 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-7 | Apartment Wall Closure
|  | Level-7 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-7 | Apartment Ceiling Closure
|  | Level-8 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-8 | Apartment Wall Closure
|  | Level-8 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-8 | Apartment Ceiling Closure
|  | Level-9 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-9 | Apartment Wall Closure
|  | Level-9 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-9 | Apartment Ceiling Closure
|  | Level-10 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-10 | Apartment Wall Closure
|  | Level-10 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-10 | Apartment Ceiling Closure
|  | Level-11 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-11 | Apartment Wall Closure
|  | Level-11 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-11 | Apartment Ceiling Closure
|  | Level-12 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-12 | Apartment Wall Closure
|  | Level-12 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-12 | Apartment Ceiling Closure
|  | Level-13 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-13 | Apartment Wall Closure
|  | Level-13 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-13 | Apartment Ceiling Closure
|  | Level-14 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-14 | Apartment Wall Closure
|  | Level-14 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-14 | Apartment Ceiling Closure
|  | Level-15 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-15 | Apartment Wall Closure
|  | Level-15 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-15 | Apartment Ceiling Closure
|  | Level-16 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-16 | Apartment Wall Closure
|  | Level-16 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-16 | Apartment Ceiling Closure
|  | Level-17 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-17 | Apartment Wall Closure
|  | Level-17 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-17 | Apartment Ceiling Closure
|  | Level-18 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-B | Level-18 | Apartment Wall Closure
|  | Level-18 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-B | Level-18 | Apartment Ceiling Closure
Columns
|  | FCU installed in right location as per mechanical layout & the model number is in accordance with latest AC schedule? |  | fcu installed in right location as per mechanical layout and the model number is in accordance with latest ac schedule? | apartment wall closure
|  | FCU installed at right height to ensure grille is centred into the bulkhead & 5% slope towards drain point? |  | fcu installed at right height to ensure grille is centred into the bulkhead & 5% slope towards drain point? | apartment wall closure
|  | Thermostat control cabling has been installed? |  | apartment wall closure | thermostat control cabling has been installed?
|  | Thermostat location is correct as per RCP? |  | thermostat location is correct as per rcp? | apartment wall closure
|  | Drains have been run to Tundish & does not protrude wall framing? |  | drains have been run to tundish and does not protrude wall framing? | apartment wall closure
|  | Drains tested & witnessed by Boad Air? |  | drains tested and witnessed by boad air? | apartment wall closure
|  | All wiring including interconnection wiring & power from isolator to the condensers are roughed without defect? |  | all wiring including interconnection wiring and power from isolator to the condensers are roughed without defect? | apartment wall closure
|  | Refrigeration pipes have been installed & all refnets are sealed & hard to soffit & don’t impede on ceiling height? |  | refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height? | apartment wall closure
|  | Refrigeration insulation is not damaged? |  | apartment wall closure | refrigeration insulation is not damaged?
|  | Refrigeration pipes run through cavity without being kinked or damaged? |  | apartment wall closure | refrigeration pipes run through cavity without being kinked or damaged?
|  | Pipe projecting the wall cavities in balconies have been sealed? |  | pipe projecting the wall cavities in balconies have been sealed? | apartment wall closure
|  | Exhaust Vent & Make up Air boxes are installed as per drawings & sealed? |  | exhaust vent & make up air boxes are installed as per drawings and sealed? | apartment wall closure
|  | Air Conditioning |  | air conditioning | apartment ceiling closure | air conditioning:
|  | Air Conditioning - Inspection Date: | Inspection Date: | air conditioning | apartment ceiling closure | air conditioning:
|  | Air Conditioning - FCUs are installed & other services are not impeding access to fan coil? |  | apartment ceiling closure | air conditioning: | fcus are installed and other services are not impeding access to fan coil?
|  | Air Conditioning - FCU filter track & filters are installed & nearby service is not impede filter access? |  | apartment ceiling closure | air conditioning: | fcu filter track and filters are installed and nearby service is not impede filter access?
|  | Air Conditioning - Wiring connected to indoor unit electrical box? |  | apartment ceiling closure | air conditioning: | wiring connected to indoor unit electrical box?
|  | Air Conditioning - Condensate line has 2% fail towards the tundish & has support every 1m-1.5m? |  | apartment ceiling closure | condensate line has 2% fail towards the tundish and has support every 1m-1.5m? | air conditioning:
|  | Air Conditioning - Refrigeration lines supported by pipe clamps to avoid damage the insulation? |  | apartment ceiling closure | air conditioning: | refrigeration lines supported by pipe clamps to avoid damage the insulation?
|  | Air Conditioning - All FCU flexible ducts connections to air terminals & spigots have been air tight by using duct tape? |  | apartment ceiling closure | air conditioning: | all fcu flexible ducts connections to air terminals and spigots have been air tight by using duct tape?
|  | Air Conditioning - All FCU flexible ducts installed & supported by intact load spreader? |  | all fcu flexible ducts installed and supported by intact load spreader? | apartment ceiling closure | air conditioning:
|  | Air Conditioning - All FCU flexible ducts connections to air terminals & spigots have been secured by using fixing ties/cables ties |  | apartment ceiling closure | air conditioning: | all fcu flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties
|  | Air Conditioning - Supply boxes are installed & supported at correct location in the middle of bulkhead height? |  | apartment ceiling closure | supply boxes are installed and supported at correct location in the middle of bulkhead height? | air conditioning:
|  | Ventilation |  | apartment ceiling closure | ventilation: | ventilation
|  | Ventilation - Inspection Date: | Inspection Date: | apartment ceiling closure | ventilation: | ventilation
|  | Ventilation - Vent fans are installed with rubber isolation in the correct location as per drawing? |  | vent fans are installed with rubber isolation in the correct location as per drawing? | apartment ceiling closure | ventilation:
|  | Ventilation - All flex are installed & supported by intact load spreaders? |  | apartment ceiling closure | ventilation: | all flex are installed and supported by intact load spreaders?
|  | Ventilation - All flexible ducts inner core & outer core have been mechanically secured & taped to spigots & air terminals by using duct tape & fixing/cable ties? |  | apartment ceiling closure | ventilation: | all flexible ducts inner core and outer core have been mechanically secured & taped to spigots and air terminals by using duct tape & fixing/cable ties?
|  | Ventilation - Flexible ducts run on the right location & not jammed? |  | flexible ducts run on the right location and not jammed? | apartment ceiling closure | ventilation:
|  | Ventilation - Butterfly dampers are installed & they are in a fully opened position & air tight sealed? |  | butterfly dampers are installed and they are in a fully opened position and air tight sealed? | apartment ceiling closure | ventilation:
|  | Ventilation - PVC ducts have been hung at correct height & supported by hanging straps? |  | apartment ceiling closure | ventilation: | pvc ducts have been hung at correct height and supported by hanging straps?
|  | Access Panel |  | apartment ceiling closure | access panel | access panel:
|  | Access Panel - Inspection Date: | Inspection Date: | apartment ceiling closure | access panel | access panel:
|  | Access Panel - Access Panel location has been marked on floor as per RCP & has been checked |  | access panel location has been marked on floor as per rcp and has been checked | apartment ceiling closure | access panel:
|  | Access Panel - All other services do not impede access |  | apartment ceiling closure | all other services do not impede access | access panel:
Rough In (BUILDING-B / Common Area)
| Scope |  |  | Rough In | BUILDING-B | Common Area
Rows
|  | Level-2 | dynamic | Rough In | BUILDING-B | Level-2 | Common Area
|  | Level-3 | dynamic | Rough In | BUILDING-B | Level-3 | Common Area
|  | Level-4 | dynamic | Rough In | BUILDING-B | Level-4 | Common Area
|  | Level-5 | dynamic | Rough In | BUILDING-B | Level-5 | Common Area
|  | Level-6 | dynamic | Rough In | BUILDING-B | Level-6 | Common Area
|  | Level-7 | dynamic | Rough In | BUILDING-B | Level-7 | Common Area
|  | Level-8 | dynamic | Rough In | BUILDING-B | Level-8 | Common Area
|  | Level-9 | dynamic | Rough In | BUILDING-B | Level-9 | Common Area
|  | Level-10 | dynamic | Rough In | BUILDING-B | Level-10 | Common Area
|  | Level-11 | dynamic | Rough In | BUILDING-B | Level-11 | Common Area
|  | Level-12 | dynamic | Rough In | BUILDING-B | Level-12 | Common Area
|  | Level-13 | dynamic | Rough In | BUILDING-B | Level-13 | Common Area
|  | Level-14 | dynamic | Rough In | BUILDING-B | Level-14 | Common Area
|  | Level-15 | dynamic | Rough In | BUILDING-B | Level-15 | Common Area
|  | Level-16 | dynamic | Rough In | BUILDING-B | Level-16 | Common Area
|  | Level-17 | dynamic | Rough In | BUILDING-B | Level-17 | Common Area
|  | Level-18 | dynamic | Rough In | BUILDING-B | Level-18 | Common Area
Columns
|  | Duct Installation - Are drawings on site the latest issue |  | duct installation checklist | are drawings on site the latest issue
|  | Duct Installation - Are plant & equipment location correct |  | are plant and equipment location correct | duct installation checklist
|  | Duct Installation - Fan in the duct run has been installed |  | duct installation checklist | fan in the duct run has been installed
|  | Duct Installation - Model of the fan is correct as per latest Fan Schedule |  | duct installation checklist | model of the fan is correct as per latest fan schedule
|  | Duct Installation - Duct size & location correct |  | duct installation checklist | duct size and location correct
|  | Duct Installation - Material & gauge correct |  | duct installation checklist | material and gauge correct
|  | Duct Installation - Is correct support method being used - Risers are supported at each level. |  | duct installation checklist | is correct support method being used - risers are supported at each level.
|  | Duct Installation - Is correct jointing method being used |  | is correct jointing method being used | duct installation checklist
|  | Duct Installation - Are joints completed & cleated installed on flanges |  | are joints completed and cleated installed on flanges | duct installation checklist
|  | Duct Installation - Is correct joint sealant being used |  | duct installation checklist | is correct joint sealant being used
|  | Duct Installation - Has the spacer been placed between the fan & the silencer, & the splitter orientation rotated by 90°? |  | duct installation checklist | has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
|  | Duct Installation - Is 1 diameter of straight duct between pod attenuator & fan inlet been allowed to ensure impeller obtains even flow? |  | duct installation checklist | is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
|  | Duct Installation - Is adequate distance between attenuator & fans been maintained? |  | is adequate distance between attenuator and fans been maintained? | duct installation checklist
|  | Duct Installation - Are the attenuator splitters in the plane of the bend ? |  | duct installation checklist | are the attenuator splitters in the plane of the bend ?
|  | Duct Installation - Are transitions close to attenuators gradual? |  | duct installation checklist | are transitions close to attenuators gradual?
|  | Duct Installation - Is a settling duct between volume control dampers & attenuators allowed? |  | duct installation checklist | is a settling duct between volume control dampers and attenuators allowed?
|  | Duct Installation - Are fire dampers installed & break away joint complete |  | are fire dampers installed and break away joint complete | duct installation checklist
|  | Duct Installation - Are flexible ducts installed, supported & connected to spigot by approved method using duct tape on internal core & cable tie on outer core |  | duct installation checklist | are flexible ducts installed, supported and connected to spigot by approved method using duct tape on internal core and cable tie on outer core
|  | Duct Installation - Are flexible connections to equipment sealed & aligned |  | duct installation checklist | are flexible connections to equipment sealed and aligned
|  | Duct Installation - Is ductwork insulation as per drawings |  | is ductwork insulation as per drawings | duct installation checklist
|  | Duct Installation - Is ductwork fire rating complete |  | duct installation checklist | is ductwork fire rating complete
|  | Duct Installation - Are all spigots installed & dampers fully open |  | duct installation checklist | are all spigots installed and dampers fully open
|  | Duct Installation - Are all access panels for fire damper access installed & closed |  | duct installation checklist | are all access panels for fire damper access installed and closed
|  | Duct Installation - Is ductwork installation complete |  | duct installation checklist | is ductwork installation complete
|  | Lobby Area - Lobby Area: |  | lobby area: | lobby area
|  | Lobby Area - Inspection Date: | Inspection Date: | lobby area: | lobby area
|  | Lobby Area - Other services installed are not impeding access to fan coil |  | other services installed are not impeding access to fan coil | lobby area
|  | Lobby Area - All Ductwork passing block walls are flushed & sealed |  | all ductwork passing block walls are flushed and sealed | lobby area
|  | Lobby Area - Transfer duct installed at Accessible toilet wall & penetration flushed & sealed |  | transfer duct installed at accessible toilet wall and penetration flushed and sealed | lobby area
|  | Lobby Area - Where passing the block wall flexible ducts has been equipped with Sleeve & penetration sealed |  | where passing the block wall flexible ducts has been equipped with sleeve and penetration sealed | lobby area
|  | Lobby Area - Refrigerant pipes passing through fire rarted walls are sealed at wall penetration by using approved material |  | refrigerant pipes passing through fire rarted walls are sealed at wall penetration by using approved material | lobby area
|  | Ducting - Riser |  | riser | ducting-common area
|  | Ducting - Are drawings on site the latest issue |  | are drawings on site the latest issue | ducting-common area
|  | Ducting - Are plant & equipment location correct |  | are plant and equipment location correct | ducting-common area
|  | Ducting - Duct size & location correct |  | duct size and location correct | ducting-common area
|  | Ducting - Material & gauge correct |  | material and gauge correct | ducting-common area
|  | Ducting - Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method |  | is correct support method being used - maximum vertical support to be 3600mm using as 4254 approved method | ducting-common area
|  | Ducting - Is correct Joining method being used |  | is correct joining method being used | ducting-common area
|  | Ducting - Are joints completed & cleated installed on flanges |  | are joints completed and cleated installed on flanges | ducting-common area
|  | Ducting - Is correct joint sealant being used |  | is correct joint sealant being used | ducting-common area
|  | Ducting - Is ductwork installation complete |  | is ductwork installation complete | ducting-common area