## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
345ddc44-7a22-497f-a506-97aca9cf6583 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000003 - Main Switchboards | itp | DB #
9d313561-34b4-4119-b267-f6509277311a | section | ITC
dd164818-b340-4632-8de1-5ab0eb7ffe25 | checkpoint | Confirm All Pre-requesite Work Has Been Completed
b71e0a5e-7c8e-4b20-b743-50ca422783d6 | checkpoint | Completion of "Visual Inspection of Distribution Board" Check list prior to testing
27803e77-22cb-5c9c-9a84-7ec313164d8d | button | No damage | YES,NO
99971487-4c3b-5423-87da-5bed22364fee | button | Sufficient supports | YES,NO
8243979f-2474-526a-a89d-d198d8cb1b3f | button | Correct labelling | YES,NO
2fd4fe67-dafb-4e38-9b93-c63fe1dea1b9 | checkpoint | INSULATION RESISTANCE
1898892e-2967-5b99-8f33-ccf8937c33a6 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
334f2cbd-fa2c-55e4-b897-e3709fb4690d | note | The insulation resistance shall be not less than 1 MΩ.
44475211-7687-5950-b0d2-367f29ebf6f4 | textbox | R-W
1092c507-33e4-5d7e-91c8-9eeefbff7741 | textbox | R-B
89579447-63f3-573d-a92b-29b3c1fbc487 | textbox | W-B
00dd62c4-285c-52d8-ab4b-7603da2d45d9 | textbox | R-N
ec3c2f6c-c545-5eed-ba5f-27acc7a85db4 | textbox | W-N
7aee3b70-dc26-5d41-988c-085fa95e1fdc | textbox | B-N
d65ca42e-5364-58ba-b459-f0257a729188 | textbox | R-E
8a88b10b-084a-585d-ac94-957e2a013ade | textbox | W-E
2a7bd662-8c4c-53d4-a664-60bca4a4c817 | textbox | B-E
a0f09bad-3e3c-469f-8bdd-d4f8a970754b | checkpoint | CIRCUIT BREAKER OPERATION - OPEN POSITION
b132c51a-4085-5c42-9731-cc411aa25ad9 | note | Continuity Test – With breaker in open position
91411342-a92d-4ca5-bf03-1a88ea42932e | checkpoint | CIRCUIT BREAKER OPERATION - CLOSED POSITION
68eb7ed9-e801-52e4-8f46-ce3584deae49 | note | Continuity Test – With breaker in closed position
ccdf98f5-dddf-4f4c-b9bc-bdb73c2f3e23 | checkpoint | CIRCUIT BREAKER SETTING CHECKS
79bb6ee5-701b-599b-94cb-e36c914ab22a | note | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
05a43503-a7c0-4552-83c8-1f1fc7b8d429 | checkpoint | CURRENT TRANSFORMER POLARITY CHECKS
65c6baad-9916-50b0-921d-49984d5431e7 | note | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
3b8e8313-da56-4400-bb5e-c7a7cba34450 | checkpoint | CURRENT TRANSFORMER RATIO CHECK
7ccfe567-678c-51af-993c-058e63877043 | note | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
fc811301-2fe6-5136-a7b1-48f05527d20b | textbox | CT Ratio
3bab56a8-941d-4c3e-b125-d1724074521a | checkpoint | Multimeter reading (V=Volts & A=Amps)
d44ddd49-a37b-5f8d-9995-b39328a42c9b | textbox | Red Phase
0770c1bf-ec22-5dff-8f08-cfeb278eaa0a | textbox | White Phase
eb7413fe-097c-5798-a78b-5a649135a3bc | textbox | Blue Phase
0eaaa295-1d37-4d38-8306-de74711ea0d1 | checkpoint | DB Meter reading (V=Volts & A=Amps)
0ffdbceb-bc79-5eb1-bd7e-9e4975947c46 | textbox | Red Phase
42389db0-d93c-575c-bdf8-2c3c753b0cdb | textbox | White Phase
6b6f239f-2ec3-5d55-9789-8e7345c323b1 | textbox | Blue Phase
67ce3c3a-7b69-4ff1-9027-19f21a04764e | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000004 - Distribution Boards | itp | DB #
aa337912-9bee-4158-b23a-f238c065921f | section | ITC
1d39949f-d87b-40f6-80b9-460816529273 | checkpoint | Confirm All Pre-requesite Work Has Been Completed
09ba8235-7874-4d19-ba46-d9cfaf26212d | checkpoint | Completion of "Visual Inspection of Distribution Board" Check list prior to testing
d72d7ff2-92ae-5a18-81b7-c73f1698ba42 | button | No damage | YES,NO
fc2139a6-d5f6-5c0a-a25e-9e5882439b78 | button | Sufficient supports | YES,NO
f167286f-864e-5521-b71b-5aef67f2aa98 | button | Correct labelling | YES,NO
aabe24e7-355b-4eeb-a249-1e8d99d0b42f | checkpoint | INSULATION RESISTANCE
6a53ddbd-54fa-5bb6-b9c9-0f4c5be53284 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
687914a3-4a04-57ea-abfb-a8333de206e2 | note | The insulation resistance shall be not less than 1 MΩ.
fdfa1606-98ce-5b5a-962f-9222cb05ff75 | textbox | R-W
949ad97f-dd16-5397-bda8-c8d2f58e0e20 | textbox | R-B
cd0ad0d6-272d-53e1-a4c1-6144e59f07c2 | textbox | W-B
eb52c14f-b3ac-5707-89a2-2f6842b6030e | textbox | R-N
535d6c27-870c-5468-a64d-b8204eec6f64 | textbox | W-N
77ede247-4a32-5251-a6f3-d1611cdce46d | textbox | B-N
1c0b95bd-24dc-515a-a6b0-e7dfe7b66c53 | textbox | R-E
1eade390-e031-5bcc-9e9a-5b13929ce81a | textbox | W-E
e6bd1f8b-92f7-546e-9d97-5a117c8f5a62 | textbox | B-E
e6324c78-bfcd-4f84-b5f4-ad6a78322c7d | checkpoint | CIRCUIT BREAKER OPERATION - OPEN POSITION
0b3ff35b-e2f2-5488-8535-d3ad17e1c387 | note | Continuity Test – With breaker in open position
07bb891d-976b-4d3e-9281-32297705a555 | checkpoint | CIRCUIT BREAKER OPERATION - CLOSED POSITION
6c168106-5358-5032-81e6-cde29ae7113c | note | Continuity Test – With breaker in closed position
d55fc22c-2631-4a99-a0a5-17b5ef8a78c3 | checkpoint | CIRCUIT BREAKER SETTING CHECKS
6121d4f9-5172-5609-bea5-8a4017e62bea | note | Verify Breaker Settings are as per Distribution Board Shop drawings, Associated schematics & DB Schedules (Board Drawings to be attached to ITC)
0eb8a6ea-23ea-4ab1-86d6-508e32f53485 | checkpoint | CURRENT TRANSFORMER POLARITY CHECKS
9675f9eb-c04e-545b-9136-8f5415765520 | note | Visual Inspection – Confirm CT Marking Indicators are as per manufacturer Install. Guidelines. Visual Inspection of all other wiring
3161e808-a364-40b6-9292-917dab07fe15 | checkpoint | CURRENT TRANSFORMER RATIO CHECK
f3371668-67c8-56fa-9c64-518beafa50cc | note | Visual Inspection of CT Ratio. Record CT ratio and confirm it is as per the switchboard shop drawing
fb6164e2-4075-5e9d-8830-8a8c301995af | textbox | CT Ratio
3b843aa4-a46e-416b-8069-7f30b585737e | checkpoint | Multimeter reading (V=Volts & A=Amps)
998e3e51-d519-54de-8a72-83d5de6adbb2 | textbox | Red Phase
e5b954d9-376e-5daf-b9c5-f9531426eb9b | textbox | White Phase
2a56f45f-8af1-5383-b232-805dbe74b1a8 | textbox | Blue Phase
0aad88fb-a746-48d2-bb38-2133d36ce494 | checkpoint | DB Meter reading (V=Volts & A=Amps)
c1b254cd-a2bc-5a1c-855f-e1b613b2e9d5 | textbox | Red Phase
b2ce33fb-422d-5e8b-be78-591a8f3e3949 | textbox | White Phase
31811330-7735-5e51-9e68-172f5dfa7ab4 | textbox | Blue Phase
cd179520-3b6f-4722-941e-ae679f0f17b5 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000005 - Conduits | itp | LEVEL / AREA
52231bf5-6a17-4d52-98bb-e48f57783084 | section | CONDUITS
c62bf191-3e8b-486a-ace7-ab0aa71edd54 | checkpoint | CORRECT LOCATION TO DRAWING
90e14198-5809-58af-977b-bfaafe7476d1 | note | As per HD SHD
1cf2f7c7-417c-4b7d-98b4-85c9ebc7726d | checkpoint | CORRECT SIZE AND TYPE
45cbedc0-2b44-5475-8084-8076d0adfa35 | note | As per HD SHD
6fc63625-8eb8-409d-8d56-934d5e38bab2 | checkpoint | CORRECT SPACING IN SLAB
8ca1a473-c1c1-4454-a13d-abd10412fcaa | checkpoint | CORRECT DEPTH IN SLAB
04a711df-97e3-43c4-b4fa-56b0486c3597 | checkpoint | CLEAR TO OTHER SERVICES
00a31cef-529f-4a69-8583-616671e004c6 | checkpoint | ACCEPTABLE INSTALLATION STANDARD
ea2df58d-9593-4dc4-bb1e-fe24e982b620 | checkpoint | NO DAMAGE TO CONDUITS & CONDUITS ARE SECURELY FIXED
8cd5f8da-432b-41c5-bb49-a01d1bc5b7ff | checkpoint | MEASUREMENTS ARE TAKEN FOR ANY DEVIATION & PHOTOS RECORDED
283371c6-42d5-4900-922f-ead291f3bba4 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000006 - Cable Tray | itp | LEVEL / AREA
7afe42d9-e161-4e9d-aa3b-51898d092f31 | section | CABLE TRAY
7c49685a-6130-4d88-8dee-a0f5033b0252 | checkpoint | AREA/LOCATION
4e66d5f4-d664-52bf-acc5-188a0e770420 | note | As per HD SHD
737df3f3-3ffe-4a4c-acb2-271dc623c393 | checkpoint | CORRECT SIZE
b6437529-e622-5dcc-8a24-cb3ea1924468 | note | As per HD SHD
ee716195-8eb6-4592-b0d6-fe42125b4c29 | checkpoint | CORRECT TYPE
5f7559a9-e3cc-5732-a413-f1c1a595ecc7 | note | Tray/Ladder/Basket
ffdc51a8-b89e-4d94-9e8c-5ffea568bfd3 | checkpoint | CORRECT RATING
b1422768-3415-58c0-a435-4ada8f0f467e | note | Fire Rated/Standard
1d20d748-02ae-424e-bee5-213d89397f3a | checkpoint | CORRECT MATERIAL
f41cc95a-2956-5f0f-96c0-805bcd21a412 | note | Zinc/Gal/HD/SS
13f00746-392e-4672-8201-bed0bbeacb52 | checkpoint | CORRECT SUPPORT
1ecc24e2-c72e-55da-8823-d7cfec7477c8 | note | As Per Manufacturer's guidelines
2691bba2-6a94-4b99-a70c-61a51925b2ba | checkpoint | CORRECT ALIGNMENT
4ce9a6f6-6d05-5cd2-93f1-3e9378df6edf | note | Visual Inspection
424e1099-0061-45ca-a5f4-a55b0471d912 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000008 - Low Voltage Submain Cables | itp | CABLE ID: FROM - TO
a6348e44-9218-4792-b90b-1e7b97323e0b | section | LOW VOLTAGE SUBMAIN CABLES
26b6bba8-6d5a-48dd-b590-a6e2b2f5d9af | checkpoint | PRE-REQUISITE WORKS
41f3b621-232a-5152-a3c7-c61146923ee3 | button | Compliance | FIRE RATED,NON-FIRE RATED
82ca6906-1591-5e9a-b5cf-806d7728166d | button | Type | XLPE90,XHF110
77d816d4-c0ff-5482-ba77-5d03939cbd81 | textbox | Size |  |  | RECORD DIAMETER
1f2dea6b-3bd8-5413-bb05-e3880f69e600 | textbox | Cores |  |  | RECORD CORES
8e03f3b8-1c0d-4ddc-9f07-0c1f63c5d09e | checkpoint | INSTALLATION CHECKS
c8aabdb4-7b03-5a61-bd11-526054e163e3 | note | VISUAL INSPECTION TO CONFIRM NO DAMAGE TO INSULATION
53bfe223-5400-481d-aa18-07a3fed76738 | checkpoint | CONTINUITY TEST
ae13ac14-d453-54e3-96ad-7c0c2e53646d | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
82d4aaed-1734-59f0-8cb7-add907d71b0a | note | RESISTANCE OF EARTH SHALL NOT BE MORE THAN 0.5Ω
10851fdc-cd24-579f-ba46-5d3989cc5e77 | textbox | TARGET RESISTANCE (OHM)
44dc2c0e-7b9b-5983-b310-7387d3a14096 | textbox | RESULT
4949a773-1033-4565-92a7-9f3affb86dc6 | checkpoint | INSULATION RESISTANCE
4f56823f-1996-5ae5-a07c-bf18b8209fe7 | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
d42963b0-aa85-5988-825e-5dc4fce3cb36 | note | The insulation resistance shall be not less than 1 MΩ.
377c069b-1005-5a30-9bf0-8fe5cc4b796d | textbox | R-W
aa158db5-0148-55de-98f2-1f1041422096 | textbox | R-B
f62bfb67-ee4c-581b-816e-250e8a8cd207 | textbox | W-B
ef91e273-1a36-5c0d-939c-0af6160a0870 | textbox | R-N
3dff313b-56f4-565b-965f-3e954d41c36a | textbox | W-N
4178e483-3868-5c31-9105-fda795380f2a | textbox | B-N
a5d9d79b-9466-52be-9e65-f8ab5555ac6b | textbox | R-E
22a6e75e-1ace-5a9b-9251-4600d3c6a189 | textbox | W-E
b8cc9733-ad74-5316-8139-575cb96033f0 | textbox | B-E
1ae96cc2-2ecd-4197-b06a-d17fb19ba42d | checkpoint | PHASE ROTATION
e63ae067-e3cd-59ef-877d-3f73a4b0a44c | note | AS/NZS 3017:2007 3.5 Phase Sequence - Phase sequence testing is necessary to ensure that multi-phase equipment such as multi-phase motors and semiconductor controlled equipment operates in a predictable manner.
4e7f18c7-4172-59cf-8a9f-897dfa631b38 | note | Record result
931fca62-b4be-52d7-91be-54bb7265c25e | textbox | ROTATION:
d7ac1b18-874e-4b29-97f0-62c08ebb28e6 | checkpoint | VOLTAGE CHECK
7f92def7-856e-56bf-9521-049ec929af8e | note | Test Line Voltages and ensure the voltages are within acceptable range
b3435aec-b56a-512e-8c5a-32845271795e | note | Aus Grid NS238 6.1.1.1 Low Voltage Supply
44079409-a545-5334-930f-2f5f4707957f | note | 230V +10% / -6% = Range 216V to 253V
fbdccb10-eac1-5e57-ae62-603f221e587d | note | 400V +10% / -6% = Range 376V to 440V
36975791-4100-5a70-9c54-5b04a9972ab3 | textbox | RED PHASE:
3a0f0a90-d8e1-58a6-b88b-60d093ceb4b9 | textbox | WHITE PHASE:
5dbafd45-d2f6-5e76-856c-de1b23143d02 | textbox | BLUE PHASE:
0886281b-5e69-4615-b010-0dae486de53b | checkpoint | IMPEDANCE (OHM)
39b51c17-12d4-561a-958a-53045519f764 | note | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
7f910a58-e126-5c2b-a96d-cab1f6c8d439 | note | 20A TYPE C PROTECTION 1.53 Ω.
34c83741-b482-57ad-ac14-a9f5d0500722 | note | 32A TYPE C PROTECTION 0.96 Ω.
e36a38f7-bb84-5ffe-a955-6326b7be36ab | textbox | IMPEDANCE (OHM):
24617ed5-af78-5db3-9a32-523c7278c24b | textbox | TARGET IMPEDANCE (OHM):
8545a83e-6855-4432-9bef-baf8373d3794 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000009 - Main Earthing System | itp | CABLE ID: FROM - TO
d4e3eab0-eba8-4743-9883-c857fb86fc1f | section | MAIN EARTHING SYSTEM
4c163f6a-5490-44f1-a30a-63be3195e179 | checkpoint | PRE-REQUISITE WORKS
29c25bfa-f424-5647-9d8d-a589832b66d2 | note | Confirm All Work Has Been Completed
2e8db8b2-9fb1-4442-bafb-09a12ccc5132 | checkpoint | VISUAL CHECK
37c7e6f4-2843-58d0-9037-79513c515df4 | note | Visual Inspection – No damage, outlet installed correctly
de113cf1-8776-42d1-98cd-3a93a901fce3 | checkpoint | CONTINUITY TEST
f155e85f-b83f-56da-a969-3fda33c034de | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
f823bfac-c029-526b-a19c-ac5f689ba319 | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
3883e193-b448-4731-a9b6-753ca849d80a | checkpoint | ELECTRICAL RESISTANCE TEST
8879ed39-1487-5844-9bea-5d94939c5071 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
f1c64d5f-6c5f-573d-96a6-b873cf39e318 | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
fce3d2ac-7c78-5e77-bfdc-9cf1c9cde1dd | textbox | RESISTANCE: |  |  | Ω
fc7151fe-eb12-57d7-abc0-860e65cd6ee9 | textbox | TARGET RESISTANCE (OHM) |  |  | Ω
16b8c94e-c7a6-42e4-b0ad-a88afc098ea7 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000010 - Lightning Protection - RWV | itp | LOCATION
5046a263-77aa-41b3-95af-b6835d207b50 | section | EARTHING
33402065-798b-4be3-a3e9-161e58603ff6 | checkpoint | Rods, clamps, conductors
15a102e8-d322-5759-9bd6-db7bd2ef1a46 | textbox | Location
b5d6fe4f-f137-5485-a533-839969e27c87 | textbox | Correct size
1c40f31a-5766-5141-acf7-044dc26faa5a | textbox | Correct number
fa3c1616-223c-5eef-b69d-6639b8b59dc1 | textbox | Straight and secure
4395fa5b-0c91-4ff1-a954-676aa293f848 | checkpoint | Test points
08e8b995-3e4f-5114-be49-5c3f81d20512 | textbox | Location
51c08209-af0d-579f-8dae-88138075d498 | textbox | Correct number
a0b21fdf-eeee-5f2a-b44d-563968819a8a | textbox | Straight and secure
a39912e9-a5fe-4a6e-9641-7296f0455226 | section | DOWN CONDUCTORS
03f732cc-ee2e-468c-a6ca-53a8654f2ef5 | checkpoint | Structure used
8353c3fc-59b2-5382-ba8d-e0844284f6f7 | textbox | Location
86b6afe8-6f3a-5b2c-b283-07f8e763798d | textbox | Correct number
11043cc5-b532-5934-a45e-121a3366b5b6 | textbox | Continuity testing
d3fcb88e-9f14-4d3f-9a9a-945e984b0438 | checkpoint | Separate
68ebfd3f-3fe6-57d0-88ab-f53cded33167 | textbox | Location
9b73a752-ba46-5091-aec8-4a15b3f35561 | textbox | Correct size
806abbb4-acef-57cc-be05-87cfd8717f74 | textbox | Correct number
daf63fe0-57d8-5350-8225-93612bf13e74 | textbox | Straight and secure
550a41b1-4094-4b84-a997-354bbba1977c | section | Aerial termination;
cb4a0789-e758-4ba0-b98e-41890fc5b838 | checkpoint | Terminals
fbde6469-a331-58ec-a97c-66d85378ec52 | textbox | Location
072db263-d2c8-59c9-8c14-926d4d5c406f | textbox | Correct size
dce60eee-651f-55b1-b26f-aa67590cf1ae | textbox | Correct number
087a2ede-e8a4-5aa9-94b0-2cbd6d69949b | textbox | Straight and secure
da9ab3d0-1802-49d3-abf9-48750dd49dd5 | checkpoint | Strapping
3a0ee2f6-860b-5008-867a-9d3bc80e4d3d | textbox | Location
d2f46476-d7ee-5e4f-9d26-dccc01b5158d | textbox | Correct size
e7d5cbe3-2dd9-5ece-8446-36197648bb9b | textbox | Correct number
7d41eb2b-0c89-5494-9d30-45832b223136 | textbox | Straight and secure
9eeff5e4-b142-4c6b-9133-2fc3249034af | checkpoint | Bonding
18bfe5ed-c4ca-5e56-a0d4-e6887a49b88a | textbox | Location
cb38d289-6260-5ef4-9eee-4b4b5c0aea66 | textbox | Correct size
562be44d-c76e-5f1c-9512-a9259c569761 | textbox | Correct number
189faac7-ba89-53de-8274-49dd8ba5be4e | textbox | Straight and secure
e737a957-d9f0-4e58-b2bd-66c0cce1c330 | section | TESTING
ef229f05-280c-493c-973a-a1acee26f0f0 | checkpoint | Earth resistance test
59d3a4b0-1549-50e1-90ee-bf4e4de328f9 | textbox | Report number
7dcbeb8b-4e9a-422b-b555-49340506771f | checkpoint | Column continuity test
c8c40951-aa39-5ad8-8c38-17aeac6cbfc1 | textbox | Report number
381d4822-5330-4361-8bc8-998600120eda | checkpoint | Full system test
efa2ea11-cddd-5b20-a818-86e7a680d1b5 | textbox | Report number
c9641695-f00c-498c-b235-931aac600682 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000011 - Lighting Circuits | itp | CABLE ID: FROM - TO
ef39ed41-3325-407a-880b-079923adaf84 | section | LIGHTING CIRCUITS
afa769ee-983b-4676-b140-84986b8da5cb | checkpoint | PRE-REQUISITE WORKS
7be6400a-c4a3-5ddb-afac-304e785345c1 | button | DB COMPLETE | YES,NO
36988923-f8bb-5552-a5f7-2fadcd346696 | button | DB ENERGIZED | YES,NO
4d558d6f-a191-5e20-b69c-97f28d8c4c0a | button | DB COMMISSIONED | YES,NO
7254402c-5920-4208-9368-160270b98910 | checkpoint | INSTALLATION CHECKS
1409e039-c545-52a7-835b-8a5127533da0 | note | Visual Inspection to confirm no damage to insulation, Plug bases installed correctly
4b0a66de-fae4-4523-942e-504a2de8d544 | checkpoint | CONTINUITY TEST
0f2eb3f1-dff1-5021-8005-474af5c46fd2 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device
63591842-3932-5033-8524-b83c7c46dad6 | note | EXAMPLE 2.5MM 2C+E 20A Type C – ˂ 0.50 Ω
cdcd4ba7-b69f-5558-aefe-2d01eba24856 | textbox | TARGET RESISTANCE:
8d40ab7a-0c30-4607-99af-b9e6a1445b8e | checkpoint | INSULATION RESISTANCE
60468d4d-0b2c-52ab-85c0-75c50013066d | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
6d334083-ab7e-558e-8d57-c11fecadea54 | note | The insulation resistance shall be not less than 1 MΩ.
ad7e1bf1-9206-5ee3-8539-7552e62b5777 | textbox | R-W
92f37878-371e-57c0-9f0a-e34ed6c897a7 | textbox | R-B
3e171d0f-e6ec-57c9-9ed7-50706ed413fe | textbox | W-B
b19c4578-2a9a-54c3-af4c-6e0b5ee6edbc | textbox | R-N
ba2aa75c-2221-5c75-a13e-2cd7cae1a4eb | textbox | W-N
5cfe203c-ac79-5cbd-a303-401873fa48a9 | textbox | B-N
e3797533-5f3e-5537-975b-15e1208b245e | textbox | R-E
78c96853-f591-5676-ac8f-b125455a9757 | textbox | W-E
7b2dad4a-f694-530f-817f-4ade06b7af4c | textbox | B-E
a4f47b15-4def-44ce-a1ad-d935b66b8dd6 | checkpoint | VOLTAGE CHECK
471bfd45-92bb-53a1-aba7-c24067425a5b | note | Test Line Voltages and ensure the voltages are within acceptable range
1f822e99-c476-5e92-a04b-af440f34f659 | note | Aus Grid NS238 6.1.1.1 Low Voltage Supply
cb32cd91-853e-5e6e-9dec-e5b02d6ef129 | note | 230V +10% / -6% = Range 216V to 253V
bf86a6a2-a892-5ec3-9cb7-4f87c5a19654 | textbox | RED PHASE (RECORD VOLTAGE):
a91c0ce5-0625-4271-a5fa-77f7a3b3e220 | checkpoint | POLARITY CHECK
e4b8071e-abc1-5d2f-ae57-67f44b9b6b13 | note | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
88786f93-888a-5f56-b8f4-f33fca98628d | note | Verification through continuity testing of each conductor
ad967396-a36c-5afd-adf9-1f78e3cdae59 | textbox | NO TRANSPOSITION
833b55cb-43cd-56c7-9a8f-c120f67f11ef | textbox | SWITCH IN ACTIVE
482f767f-ba48-4cf9-9e97-f3fcbbefad36 | checkpoint | RCD TRIPPING TEST
daee56df-db22-5e2c-a4b6-ce3678aa4aaf | note | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
1507085d-09e5-5ec1-8d65-5f607e2ac9ba | note | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
46dac0be-2c3b-54c4-a4b6-64a46568730c | note | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
5f6f7d17-97ca-5adf-a91d-bdd853d04c79 | note | Result < 300ms
5c019eba-8f5d-5e66-83df-e32dc455d341 | textbox | TRIP CURRENT
6ffb84d8-8cc0-5ace-b1a0-154fd13a8452 | textbox | TRIPPING TIME
86548d7e-34c4-43f4-91cb-61a380c62050 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000012 - Lighting Control - Automated | itp | LEVEL / NETWORK
fbc74ca2-35df-4faf-be5e-229aa1bee19f | section | INSPECTION AND PROGRAMMING
aaca9df6-41ec-4fa5-9819-3e411fe5b34e | checkpoint | Dynalite equipment Load schedules completed with circuitry information for each output equipment by flash testing individual outputs
cc9bdc39-bd66-4227-97f9-3c7b864281f0 | checkpoint | Testing of output unit for each DALI universe operation by flash testing individual outputs
7f1a0ab1-94a4-4bd8-b31f-3d7915ea19ae | checkpoint | Field input lighting control equipment (Switches, occupancy Sensors, light Level Sensors) installed and terminated as per specification
c6f04d20-af8a-4705-9b11-f467d94f6469 | checkpoint | Input commissioning sheets complete with field device information
66c01aea-bbb3-4bbb-8ae0-682e13ec776a | checkpoint | Programming of DALI control units as per zone mark up
408fbf2b-403e-43a6-ac8c-1ce796367a56 | checkpoint | Programming of lighting control input units (Switches, occupancy Sensors, Light Level Sensors)
8795585c-487f-4f63-be3e-2ad63f5ab755 | checkpoint | Touch screen operation tested
dd28c2ac-8d75-45c8-9e37-dd92d4ca5518 | section | COMMISSIONING
f63db462-d90b-4c44-a469-d2847676272f | checkpoint | Tested power failure recovery system isolate power to control system
6565c4cb-25b4-40be-91f8-e17822b07816 | checkpoint | Addressing of Network Bridges and gateways ping test via ICN network
7d8f0990-b836-4998-b07a-920af6fa2bb9 | checkpoint | Allocated devices responding to allocated addresses via Ping test
65fa610b-10e6-4f4f-903f-4f8b47239a95 | checkpoint | Tested Head End operation and control functions
aabe3469-de2b-4817-bcc6-3281f7ccbbe7 | checkpoint | Mapping of Graphical data points (read/white), Manual controls buttons
5c4a55ab-7569-4dc7-a53d-cd7db5beec8d | checkpoint | Witness testing verifies correct control
af6196fd-657f-4094-8911-363e9f2b3097 | checkpoint | Device functionality confirmed
909b9c66-a6ee-4cd9-9335-0235e72e1d84 | checkpoint | Realtime reporting demonstrated
f60575ed-b4ec-407a-b43d-f76cd02b4e08 | section | TESTS
4e7b553f-fa27-401a-88ad-7a244b5907d0 | checkpoint | Test Required: Functional
387ba2df-8113-5610-9ed3-546937c0642e | textbox | Functional sections
7edbb32f-1fe0-4acb-87a9-b0f9721dcdac | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000013 - Emergency Lighting | itp | FITTING ID
d6355a41-5ceb-4d72-90a1-78a6458a265e | section | EMERGENCY LIGHTING
0cfc25bd-d871-4467-970c-7426c4c976d2 | checkpoint | PRE-REQUISITE WORKS
2beffc04-95d9-43e5-8e3e-3656eed8f2bd | checkpoint | CORRECT LOCATION
e5c840eb-15fe-4acd-8b80-a2e23cdb32af | checkpoint | CONSTRUCTION AND FINISH
c646c714-2c7b-401e-8f1c-a9dfb0cef50d | checkpoint | LEVEL AND ALIGNMENT
9a6d2e52-837d-4ba0-9ccb-85ef6a0da94b | checkpoint | ACCESS PROVISIONS
e7e7e8b9-986f-45fc-923b-4d05f73adf84 | checkpoint | EARTH CONNECTION
7a1ac2d4-e8bf-48cf-a143-12e653a66bf8 | checkpoint | LABELLING
5c5346d6-f8f4-428f-af98-6c910c7d25f6 | checkpoint | DISCHARGE AUTONOMY TEST
7bcea4cb-b2b7-4b92-ba1e-15729bdf5d64 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000014 - Power Outlets | itp | OUTLET #
164d7539-4448-46ec-b0d0-564e958b821d | section | POWER OUTLETS
f1dd7777-d442-4ec2-9853-3de77618408d | checkpoint | PRE-REQUISITE WORKS
f7f2a192-1ff2-5241-916c-722d2ad193f0 | note | Confirm All Work Has Been Completed
d7cc74f8-68f8-4851-9202-52091460f9e2 | checkpoint | INSTALLATION CHECKS
d37a0003-24d4-5487-ab5d-4a51e0dc52a2 | note | Visual Inspection – No damage, outlet installed correctly
726392e6-c04c-4e4b-8eea-dd509da32e11 | checkpoint | CONTINUITY TEST
78986652-edbd-5a53-a09f-1a3b3aba1aa8 | note | AS/NSW 3017:2007 - 3.1.2 The resistance of protective earthing conductors shall be low enough to permit the passage of current necessary to operate the circuit protective device (AS/NZS 3017:2007 Table 3.2 Max. Values of Resistance)
d9b0f317-c9f4-5188-ad0c-a7b88af3b52a | note | 2.5MM 2C+E 20A Type C – < 0.50 Ω
0835b456-5f0a-5f37-90e9-0e5b9fdfe6b9 | textbox | RESISTANCE: |  |  | Ω
a70c7c61-0ecb-5d8b-9e03-51d987ee5654 | textbox | TARGET RESISTANCE: |  |  | Ω
254f5921-27e2-410c-8b8f-61a28a13aba9 | checkpoint | INSULATION RESISTANCE
df079988-f42c-577c-a7b2-c274d8726fee | note | AS/NZS 3017:2007 Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation.
e1ae0454-a5fc-5bec-bd39-5131ea28862c | note | The insulation resistance shall be not less than 1 MΩ.
4a6e013c-c3e8-51c1-991c-9bcd2bbedbb8 | textbox | R-W
3943ee30-60c8-5b57-9384-b24c06d09718 | textbox | R-B
4498a69f-85f4-53f3-8a4d-64b9169d1cd3 | textbox | W-B
e90271b5-5ae1-5db9-8265-5f480deeb1a6 | textbox | R-N
2201d0e2-269a-5db7-ac6d-25ea6f090ae2 | textbox | W-N
ecc1037b-262d-56b8-b108-1d1d6a854077 | textbox | B-N
55d8b46e-6538-5a90-a487-eb699c09e84e | textbox | R-E
f859b5e5-db7c-5173-9cdb-335241f50658 | textbox | W-E
86f52bdc-7e46-58e7-91e0-b9c58b1b8844 | textbox | B-E
6c566825-6013-4ab1-84e3-4b6c6920329b | checkpoint | POLARITY CHECK
8c7e524e-e3a5-5e23-ba3c-96c9db9435fa | note | AS/NZS 3017:2007 Polarity – Ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors
4234bf11-6e1b-5d05-aaa4-03feb9cf925d | note | Verification through continuity testing of each conductor
167e44ff-1ccc-53bf-9315-29f0aaad053c | textbox | NO TRANSPOSITION
e25d0a89-551c-5579-8df1-b59981dd57c5 | textbox | SWITCH IN ACTIVE
a5cd86ce-cbb4-410a-9e97-e024e1918d9a | checkpoint | EARTH FAULT LOOP IMPEDANCE TEST
f9633e08-e777-544e-851c-9b59b9aec624 | note | AS:NZS 3017:2007 The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault loop to cause a protective device to operate within a specified disconnection time.
1094249c-f9a5-59c3-8115-766e73150b5b | note | 20A TYPE C PROTECTION 1.53 Ω.
4c883a34-c8fd-57a3-b11a-b30afe15f730 | note | 32A TYPE C PROTECTION 0.96 Ω.
2cbbb186-70a2-5ecc-a399-e3e2b7520d62 | textbox | IMPEDANCE: |  |  | Ω
64d83729-4d7c-585d-b8cc-20eb615b4c4d | textbox | TARGET IMPEDANCE: |  |  | Ω
edd5a9f7-4856-4594-a56a-240d38c2cfb4 | checkpoint | RCD TRIPPING TEST
b7d5a498-7b39-5824-9507-4e6bd265342e | note | AS/NZS 3017:2007 Ensure the RCD operates and disconnects the designated circuit.
50d5947e-dae6-58f4-b266-d0902f689c79 | note | Testing must be completed using an integral test device, the device must apply the rated tripping current and measure the tripping time.
b4089d1a-d2a8-5835-89f1-91694e812bc1 | note | Type of RCD: General Tripping Current; 30Ma Max. Max. Tripping Time: 300ms
94cf0e56-882e-5bf4-b7d4-062c90394000 | note | Result < 300ms
886dcb34-7df1-5b61-8949-4f4444ed5dec | textbox | TRIP CURRENT
0b655ad7-963f-5660-9596-a201f7afda05 | textbox | TRIPPING TIME
338ad1e3-e7e5-4dd4-ba01-b45c8058be3f | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000016 - PFC Equipment | itp | INSTRUMENT S/N #
12505f2f-bceb-43f9-8fd1-711b8956c83b | section | INSTALLATION INSPECTION (WARNING: SYSTEM MUST BE DE-ENERGISED)
c08157e3-060b-443c-bf21-bbd9483db32b | checkpoint | SIGNS OF EXTERNAL DAMAGE
b1fd51bd-3ea4-4836-8fbd-7930c445bf9a | checkpoint | SIGNS OF INTERNAL DAMAGE
2d245191-d703-4fba-a034-6da419018fa0 | checkpoint | ENCLOSURE SECURELY MOUNTED
a454e432-427a-429d-8c65-5206d1521533 | checkpoint | ENCLOSURE VENTILATION
e3c48ea8-307b-4325-b922-9a893f936e26 | checkpoint | SIZE OF POWER CABLE
96c1c61d-99a5-46ce-ba9b-ee85cf9aa8e5 | checkpoint | SIZE OF NEUTRAL CABLE
43dd2729-87eb-423c-85b5-a428daa5d69d | checkpoint | SIZE OF PE CABLE
36a32f36-5746-4eb7-ac00-21eb8e574888 | checkpoint | CABLE CONNECTIONS
ef56fa73-f424-4d6c-b3b4-473ff17b52ac | checkpoint | PHASE SEQUENCE
4a196620-8ff5-40f7-8e34-12954a9bd6c7 | checkpoint | POSITION OF CT'S
9e8bbf0e-5e23-47ad-9040-540b90c7ae80 | checkpoint | POWER FUSES
11dc3931-dd12-481d-8d94-48a72c48ba4b | checkpoint | CONTROL FUSES
0837c976-5de3-42ba-b1af-acc1507db2d8 | checkpoint | CT LINKS
9d428c2a-db3e-4c5d-8c1a-4bb8ec2cb165 | checkpoint | INSULATION RESISTANCE (WARNING: SYSTEM MUST BE DE-ENERGISED)
a1e42362-3d50-5405-8d3e-8e6c8d406273 | note | MEGGER VALUE: >200MΩ
90ececc3-86e2-54f0-b025-e28f4377e2a3 | tickbox | L1 - L2
49be9021-117a-5f32-90a2-65af655e296e | tickbox | L1 - L3
877bf748-3a39-58c8-9cba-6e968118a4f7 | tickbox | L2 - L3
0ede3efc-db07-5bb9-97ff-86bdc854e5b3 | tickbox | L1 - N
4bae0799-22c4-54f5-a3c7-d0dc7572ed12 | tickbox | L2 - N
65a5ab3e-1fe0-5b37-8cb5-e75cf5226c29 | tickbox | L3 - N
7cc6454c-afc7-5b49-bff4-e3e569e43e94 | tickbox | L1 - PE
13af1c60-21af-5e49-8bcf-6bb408b5b92c | tickbox | L2 - PE
eed6918d-e296-549a-a789-7982177057dd | tickbox | L3 - PE
95859d12-3798-544e-bbb0-003bb9f36111 | tickbox | N - PE
ade70c73-49a1-533a-9ee1-9aa42fb73159 | textbox | other value (specify)
a5790f70-5c24-4f75-9273-aa42edc4e08f | checkpoint | RESISTANCE OF EARTHING SYSTEM (WARNING: SYSTEM MUST BE DE-ENERGISED)
7dc0223a-4baf-5a84-b36f-055bf3590f31 | note | MEGGER VALUE: <0.5Ω
e92cad0a-3a04-5868-ab17-d58194f8ce9f | tickbox | GLAND PLATE
2e1e05ad-e1c6-59cc-b782-c3c97469f94b | tickbox | ENCLOSURE
c2fb0622-9668-5a0e-b489-0709d2180008 | tickbox | DOORS
306c480d-de25-5a8c-97de-1951a2994fc2 | textbox | other value (specify)
76258d7f-6733-4c81-bc24-66124a58cf5f | checkpoint | CIRCUIT BREAKER SETTINGS (WARNING: SYSTEM MUST BE DE-ENERGISED)
b21deeaf-578a-5c9d-b862-cb29f8bf5ce7 | tickbox | CIRCUIT BREAKER INSTALLED in switchboard
2d7bca78-271a-5bdc-892d-fd0b7090a5a1 | tickbox | CIRCUIT BREAKER INSTALLED in HAPFC system
649156f7-ea24-5fd3-b314-26afb2c75188 | note | PROTECTION FUNCTION - Long Delay Overload
2b117fe8-dc6a-5495-becc-8b1de3c09c6b | note | RECOMMENDED SETTING: 1.25 to 1.5 times In
9b429bb2-12de-56f8-9343-0595996dc24d | textbox | SETTING AT COMMISSIONING:
b6a7f65f-1972-5b17-a5d4-a0cf2512f66c | note | PROTECTION FUNCTION - Instant Short Circuit
936bf0ec-9817-5641-9384-e6d0efffadec | note | RECOMMENDED SETTING: 5 times In
7cbc05f5-f271-5ebb-b00f-74a840b762d9 | textbox | SETTING AT COMMISSIONING:
67ef96c8-958a-5a3b-81d9-fe8d19f073c3 | note | To determine In, use the following formula:
41ff1ee6-b481-51ae-973e-c4409a0fa335 | note | In (A) = ((Q kVAr/50kVAr) x 70A + IAHF)) x 1.3
a676ccbd-78c5-55e3-a78e-efe2411aac94 | note | Where:
23985855-9047-5b71-8c86-78e727db65c6 | note | In – Total Nominal Current of HAPFC unit (expressed in Amps)
40978723-a02a-5d49-856d-9f9620a2c6a8 | note | Q – Total Nominal Reactive Power of Capacitor bank (expressed in kVAr)
417f69bd-89ec-531e-a40c-e686390bd288 | note | IAHF – Total Rated Current of HPQ modules (expressed in Amps)
c72bb4b6-fd7a-559e-9fa9-2ec5e66eb4f6 | note | NOTE: IT IS ESSENTIAL TO CHECK AND MAKE ALL NECESSARY ADJUSTMENTS TO THE HAPFC CIRCUIT BREAKER(S) TO ENSURE DISCRIMINATION IS CO-ORDINATED WITH THE UPSTREAM PROTECTION.
067f7066-8e15-4eb2-9148-7a0faeba4d02 | checkpoint | THERMO CONTROLLER (WARNING: SYSTEM MUST BE DE-ENERGISED)
1d9f750b-ef36-5118-89bf-c6c9a39e4e14 | textbox | STAGE #1 Set to:
87f45838-0987-5c2c-839a-ccf5e75c86f6 | textbox | STAGE #2 Set to:
b9b27839-c16c-4199-96ce-a79a5aab8ea4 | checkpoint-no-value | CONTROLLER
3b8f0b3e-de31-5df0-9e06-930fb8680632 | textbox | Model
7a283bb5-78a0-5c63-9bfc-e4d15ff2dbd4 | textbox | Serial Number
77b5cb68-e796-5b7e-9715-bc38dfedebdb | textbox | HMI Version
76dc1ac3-a1d1-50fa-974b-234546491406 | textbox | HMI Data Version
385c40ca-bcef-4293-9aad-5a3dbc79255a | checkpoint-no-value | HPQ MODULE - MASTER
aa090661-115f-5845-9523-9ebc8e316643 | textbox | Model
9f4faa46-45dd-5250-92ac-c9e0b49770a8 | textbox | Serial Number
6664d315-e3a5-5d16-ba4f-853f642cda2d | textbox | Manufacturer
d4750e84-550f-5052-ac60-74242dbc8db3 | textbox | MCC Version
aace0179-4ac9-471a-aa99-56001a0e8c2c | checkpoint-no-value | HPQ MODULE - SLAVE
66dcc161-089a-542a-be82-43bf917495a3 | textbox | Model
c29a0f56-4366-5679-92bc-a412b4ddcb08 | textbox | Serial Number
881c950a-38af-5f94-80ea-6b9580022538 | textbox | Manufacturer
962affe8-df6c-523b-81af-67354d4bcfcf | textbox | MCC Version
539fd41d-2758-4684-8a77-05dacbfec528 | section | CAPACITOR BANK (UNIT MUST BE DE-ENERGISED)
7993dfe7-8ec8-40ca-b5bf-6f63c311c7d4 | checkpoint | CAPACITOR BANK
fb00200e-a631-5fe9-94db-2f4e71b69a00 | textbox | Stage:
2445e267-2e3e-5f51-851f-c4ade0a293ca | textbox | Size, kVAr:
8bd9ce03-d30f-5c9d-8437-497a2ff593e1 | note | Capacitance, uF
c176e530-d14a-5b36-a7b4-5400c786b7d6 | textbox | L1-L2:
f5dcbba0-7aa4-593f-ad08-73c26cdf1a35 | textbox | L1-L3:
cfa46072-ae26-53b6-ba2f-7cdfa84ef8f0 | textbox | L2-L3:
e194bdca-431d-4447-a012-35ca263208cc | section | VOLTAGE WHEN SYSTEM DE-ENERGISED
c5fd3802-7e21-4c89-a90d-b0173581c4d8 | checkpoint | LINE VOLTAGE
57452a92-40c3-55a1-85d4-21e3bea91f1b | textbox | L1-L2
3b7d4c93-5764-54e7-aa9e-2fff7d64fb03 | textbox | L1-L3
974a91a6-da70-5e69-8844-5c4626a00027 | textbox | L2-L3
bef254ec-ecb7-45e6-a3e7-4b9181095359 | section | CAPACITOR BANK - CURRENT
46da5502-315a-4866-b3c8-e845c88f25cf | checkpoint | CAPACITOR BANK - CURRENT
e911737e-b65e-5091-8f85-173521c5a583 | textbox | Stage:
c9bc4bbc-7095-5065-8d1a-bb30a04c38da | textbox | Size, kVAr:
e191ae64-d1eb-5e2e-aa8d-0fe690d562e0 | note | Current, A
502242d6-c56f-505f-8cb3-c594a0a5b876 | textbox | L1
969ed21e-86eb-5383-9b18-49cb7e9ebb71 | textbox | L2
0c3e66a2-ea70-5bd5-b46a-6d43f731ed4d | textbox | L3
61abab20-be94-423c-bb5d-0ddbe2e47034 | section | CONNECTION SETTINGS
b43ed669-1ee0-4c4b-9d9b-09e86f6f7b95 | checkpoint | Controller
2b715224-6d09-56ca-b1bd-f64f1979ab0d | textbox | Name
a100df63-b1f5-549d-8ad9-1b200b3764e4 | textbox | IP-address
7cc1ef39-57ba-5c2a-ae89-abb01d5c2ea7 | textbox | Port
56105f35-bc06-4340-97f1-4591d1a354fd | checkpoint | HPQ Master
20e5a269-ebce-5004-80a7-12b1c820ef80 | textbox | Name
a199e33c-a9aa-5025-b971-68c6e285702c | textbox | IP-address
582bbd21-eca7-5dd2-8deb-167ffb1ef81c | textbox | Port
6382016d-1905-432c-827c-58c95ffe65cb | checkpoint | HPQ Slave
30c9308b-252d-5cff-bd71-38a8a60fefd1 | textbox | Name
7a19beda-7990-50d5-81fa-39e9e636c474 | textbox | IP-address
87ae5ce3-4502-51ef-ac28-17c073f62f38 | textbox | Port
879eaf1d-28a6-4fde-9664-fbb294ed8b64 | section | HPQ SETTINGS - COMMISSIONING
130dd36c-7c37-427b-8b71-821de375cf40 | checkpoint | ENABLE IGBT OPERATION
2804fef0-99e5-520d-a966-13d2363cd68e | textbox | HPQ - Master
44b23f6e-ddae-5a16-ac48-43dea385a12c | textbox | HPQ - Slave
0cf8fd51-73c9-4723-ba93-255d06fbd55c | checkpoint | CONNECTION TYPE
3971ddd9-6700-5491-a0b8-f19fd9e7c97c | textbox | HPQ - Master
d3515166-31ff-5a80-9153-b0698221716c | textbox | HPQ - Slave
3dd0881c-745a-4040-a4e1-3752caaed872 | checkpoint | ELECTRICAL CONNECTION (3W/4W)
e8e7ae92-d882-54e6-8d56-788287bc90da | textbox | HPQ - Master
aa0e910d-a340-5e95-b324-928e65560020 | textbox | HPQ - Slave
f699d9a3-ec48-47ed-ae40-c66a8565b38c | checkpoint | CONFIRMED FREQUENCY
70d0a339-0a4b-51cd-893f-b41b7ff50074 | textbox | HPQ - Master
19b2981d-b2a2-5067-8ace-eb5236ef03de | textbox | HPQ - Slave
710d9421-587e-4ca9-b7d4-6922911db2ab | checkpoint | Confirmed voltage
e6eeb6f8-def7-5ddb-99b3-bbbc8b92a813 | textbox | HPQ - Master
fb4acc70-319b-5bc8-aeda-545262308a02 | textbox | HPQ - Slave
8a032045-752e-4647-ab6c-4da1f707e636 | checkpoint | COMPENSATION MODE
a3f85df5-90a2-5b36-9c05-ef63e5bfd8c5 | textbox | HPQ - Master
13c9c949-66e8-570c-9497-dbafc8036689 | textbox | HPQ - Slave
56ad98d2-e693-45d6-954e-fcf3072c60ab | checkpoint | BALANCING DEGREE
2d12aef0-5ac7-55bc-b066-f19427ffef39 | textbox | HPQ - Master
6f421892-85d4-5db5-a729-269c3daee532 | textbox | HPQ - Slave
3bd05f6f-5f47-47d6-9173-3867cc5c806f | checkpoint | X1 CT-RATIO (CUSTOMER CTS)
1d3de979-b734-595c-8465-bf19435776e1 | textbox | HPQ - Master
05d2a478-d5a0-50d7-b401-4537ee3a6131 | textbox | HPQ - Slave
fa1db2ac-b6da-4792-82e7-fd6494cf3e34 | checkpoint | TOTAL INSTALLED CURRENT
a11aff1f-257c-5873-90c9-e460fb7b2e28 | textbox | HPQ - Master
5f8f5e63-2faf-569e-97f7-19178d47f28e | textbox | HPQ - Slave
26a01378-b507-4db7-99a4-e407f6610556 | checkpoint | X3 CT-RATIO (AUXILIARY CTS)
e071f555-be3e-53bd-b69b-d9cef45efc73 | textbox | HPQ - Master
accb7a2c-4a99-5c2b-be5a-0bbb2f68af2e | textbox | HPQ - Slave
09c4f1d2-f25e-497b-ab50-71d8d545f2fe | checkpoint | ENABLE AUTOSTART
41cc0bf4-c7a9-57e7-80f8-5837686192de | textbox | HPQ - Master
bb0a6946-49da-5640-b868-7a33d4d091f0 | textbox | HPQ - Slave
33c54340-9c98-4621-935a-32d807cb746f | checkpoint | ENABLE AUTOACK
b9ebfd66-2a37-540a-a691-f681765732a9 | textbox | HPQ - Master
4d40f651-f58f-5861-a00c-a33510a02289 | textbox | HPQ - Slave
7577ab5e-5944-40bf-80ca-9e765eb75869 | checkpoint | ENABLE STAND-BY
56b89459-5bcc-5ae9-9a1e-bd6be758625d | textbox | HPQ - Master
836642b1-8c5c-5ee4-b7a6-a10ef67fc5cc | textbox | HPQ - Slave
401b894a-40d1-405f-b2d7-f33156b2bc32 | checkpoint | STAND BY TRIGGER LEVEL
dff94467-f7f4-59e4-9204-a53b48f4f688 | textbox | HPQ - Master
737a103a-593c-5f60-8b66-989df2b7cb79 | textbox | HPQ - Slave
69ba6814-614e-4df5-a217-00fe85991f0f | checkpoint | X1 CT-POLARITY L1
39f94ced-5bb0-57d7-bed0-3a7c2223e469 | textbox | HPQ - Master
d5fdc1b9-4e70-574b-a39c-82fc2f4c03aa | textbox | HPQ - Slave
a3fa35f4-dbd9-477c-af6b-0540f3e9e124 | checkpoint | X1 CT-POLARITY L2
024304da-c987-5b6c-a7fa-4132afcac5d8 | textbox | HPQ - Master
427e1724-0558-5e8a-bf2c-cfef9c0d609a | textbox | HPQ - Slave
6ee8a9fc-ec41-44d3-bb43-d366679b56c8 | checkpoint | X1 CT-POLARITY L3
6d7d901c-3923-5680-89e6-75466904278f | textbox | HPQ - Master
b31ac628-be7e-5f00-942f-ee6c006f1398 | textbox | HPQ - Slave
cb700ba1-e06a-4ee3-b3d8-057f21cb0e5c | checkpoint | DIGITAL OUTPUT 0
2cc53712-8a74-5b1f-ad78-a1395e570052 | textbox | HPQ - Master
2fecd719-0895-5049-aa1e-549b8580ce6c | textbox | HPQ - Slave
b37b2299-d3df-4414-b6f6-2febd0fccb89 | checkpoint | DIGITAL OUTPUT 1
850c7a94-5bfb-545f-8f28-23ca37e0959a | textbox | HPQ - Master
2da47957-259f-5bc2-8358-ec958e0dfc53 | textbox | HPQ - Slave
1e2c861d-9896-4f68-a6de-fdcc885f5b90 | checkpoint | DIGITAL OUTPUT 2
aa114f5c-1ffd-5cd4-ada8-fd2f06c44f18 | textbox | HPQ - Master
74da8d13-c717-5946-bd95-5ae5bf056e59 | textbox | HPQ - Slave
8fcb54e0-34f9-4d2a-aa56-74afdc264e09 | checkpoint | DIGITAL OUTPUT 3
012031c9-275e-51e0-a89d-1524037092e2 | textbox | HPQ - Master
28435717-7171-5edb-be2c-d26d4cc16b5c | textbox | HPQ - Slave
e9dfb7c2-2d06-49d7-9ec7-e59ce8a21347 | checkpoint | DIGITAL INPUT 1
04c1b174-e865-5787-a0b6-55a123a188b1 | textbox | HPQ - Master
008a4bc8-794b-5731-87ed-7f8c2083d58d | textbox | HPQ - Slave
fa57b953-ed5d-4ebe-a517-22f4573e7462 | checkpoint | DIGITAL INPUT 2
5c496551-d9e5-5d52-9c05-8da593748fa0 | textbox | HPQ - Master
523de987-7439-575a-ab0d-7545914c24c8 | textbox | HPQ - Slave
4f45beec-c69e-47e4-a6be-23fc862a291b | checkpoint | DIGITAL INPUT 3
ebf88969-e7c3-5381-ba6c-bcb2ca0794b7 | textbox | HPQ - Master
218011dd-9a6e-59ba-bad7-b570b4ecbb26 | textbox | HPQ - Slave
27fba68a-3978-4a07-addd-407ff407cd7a | section | HPQ SETTINGS - HPQ PARAMETERS
202f38b5-2eda-4e59-8679-327dafeeab1f | checkpoint | Enable HPQ
fceebb82-8d6f-5664-9cce-482473ff0da5 | textbox | HPQ - Master
cab293e0-07cc-5ee2-9afd-c6658fa78836 | textbox | HPQ - Slave
42ac24b3-6329-4344-9637-401001e24bfe | checkpoint | HPQ-MODE
fc3e43c8-70c9-5d78-906d-4b95583e188b | textbox | HPQ - Master
9a822b95-1374-5bb1-914f-16c34237bd02 | textbox | HPQ - Slave
5cb5a807-4a46-4ec5-b5ba-2d8e0ee04dad | checkpoint | UNIT ROLE
790c5389-c3a9-541f-9c01-7c03df63b34c | textbox | HPQ - Master
4ca94cc7-1059-5fc3-a9eb-f916e09ff06a | textbox | HPQ - Slave
854aada5-0315-4e47-a30c-2a7eeaa44626 | checkpoint | ENABLE FO
b14a9921-6a23-53a2-bec2-a20bdfb6159a | textbox | HPQ - Master
8d2be7e7-bd9d-5a3c-8632-f7272fb1b35f | textbox | HPQ - Slave
42e7a6fb-e20f-42c2-934c-14fe61470d77 | checkpoint | OVERVOLTAGE LIMIT
88675dd1-5406-5871-8cde-aa44d265bfd3 | textbox | HPQ - Master
3c483812-b234-5987-9fd6-dfa2cd7cefbb | textbox | HPQ - Slave
59faa39b-5682-4783-b06e-6949334096e1 | checkpoint | THDU TRIP LIMIT
593a508c-332c-5651-8497-12356fe77491 | textbox | HPQ - Master
d2ae3ed8-9de9-57a2-ab6b-3490631ecc42 | textbox | HPQ - Slave
45df0b92-056f-470a-8833-fc57f4b4513e | checkpoint | STEP COUNT
3f50ee12-060a-5b17-925b-0b66c931e952 | textbox | HPQ - Master
b42af45b-2d5e-5b04-8a64-2b8b9fa6d313 | textbox | HPQ - Slave
8bb751ce-57b4-466f-aeba-6605cb0ebce8 | checkpoint | STEP SIZE
655edc38-6c15-5a39-af98-1e609ade2a52 | textbox | HPQ - Master
a241db98-8b92-53eb-ab6e-33b8041ce7d6 | textbox | HPQ - Slave
4b97e645-ecf5-4516-9d70-d186b1afc876 | checkpoint | SERIES REACTOR
c28c8d09-aef5-599b-a8c4-397cff4a8c96 | textbox | HPQ - Master
08a726b4-fbdf-52a8-bea3-eb11eeafbdda | textbox | HPQ - Slave
99b439d2-dd39-4624-9098-8472d6993549 | checkpoint | RATED CAPACITOR VOLTAGE
4030a904-2531-5dac-9037-6895c6c5bf6a | textbox | HPQ - Master
8e19f234-8343-574b-899b-5b26373f1a0a | textbox | HPQ - Slave
b0b468f5-877c-40bd-99a3-3e4e2e4bcb43 | checkpoint | HYSTERESIS LIMIT
57840964-d0f9-5570-8b05-4d30ad8ccc1e | textbox | HPQ - Master
4e9a3f2f-9e82-598c-b085-4a3ecb7fad2f | textbox | HPQ - Slave
e90e600c-9ab9-43e9-b7f9-92e9e59b57b6 | checkpoint | DISCHARGE TIME
178024ab-cb97-5433-b5ec-30b3d0504f90 | textbox | HPQ - Master
4db140ce-4148-56a5-a258-2f525d39c9a5 | textbox | HPQ - Slave
8cc3e62e-0146-4ca8-85b5-9f14b7c8a07d | checkpoint | ENABLE LAST DO AS TRIP
199652fd-4501-52db-8bc8-65df40845f9b | textbox | HPQ - Master
f6ba91d7-e7c3-54f6-923b-09416410cf67 | textbox | HPQ - Slave
0c993197-985c-403c-87a8-6ef3c9480fec | checkpoint | CONNECTION ALARM COUNT
5a899517-b4e9-5079-8e18-389642507fe4 | textbox | HPQ - Master
175685f1-e6f5-5653-9682-30e1204e219e | textbox | HPQ - Slave
98a1cf7b-7ae8-4807-8743-cc5c5130bdcc | checkpoint | TARGET POWER FACTOR
1f7ac9c6-f849-5dc3-8c1e-acaf818500a4 | textbox | HPQ - Master
cd1066ff-d60f-59c7-aa91-03d871ff531a | textbox | HPQ - Slave
339c5d50-f9db-488a-9bc5-3c31986fce2c | checkpoint | CAPACITIVE POWER FACTOR
b4e74a60-47d9-5cbf-8bd8-65e6ca5f383a | textbox | HPQ - Master
dbe32c86-df53-5498-9569-de31a289fcdd | textbox | HPQ - Slave
b0b7dad1-285f-4f7c-a0ec-ebbccde82ee9 | checkpoint | SECONDARY POWER FACTOR
0ec0ce8a-2df9-547a-a717-679150756bab | textbox | HPQ - Master
ef1877f7-9b8e-5d9c-a3e0-990ffcbc83c6 | textbox | HPQ - Slave
c2f8be31-3429-4f71-ab5c-b94e23e0d05d | checkpoint | PRIORITY CURRENT LEVEL
003c067b-24aa-5b64-9467-7f6b52edac98 | textbox | HPQ - Master
63a10430-351a-57a0-b446-7a4db68a1761 | textbox | HPQ - Slave
7dd7b3de-e678-4e54-8ba8-cffe99e57d1c | section | HPQ SETTINGS - COMPENSATION DEGREE
147ff577-0ef7-48df-8280-3c8321a039f7 | checkpoint | Ih2
0c93da54-0460-51f0-9716-2bb27e3c0a69 | textbox | HPQ - Master
e3c752bd-f429-5286-954b-c1ec7402242b | textbox | HPQ - Slave
9781b4f3-da08-4039-a546-ded95d1541f4 | checkpoint | Ih3
dd0da493-57eb-52a6-a1bc-02fa098c4848 | textbox | HPQ - Master
2583cb97-0835-5bd9-9710-9ebe784547eb | textbox | HPQ - Slave
ea985fd4-8717-4797-b056-c8aa62f44d3d | checkpoint | Ih4
7b93cdde-bcba-5df2-a2a5-b9fc3343132d | textbox | HPQ - Master
8650cecc-07b5-5c05-9b45-19e3a0d7c0f6 | textbox | HPQ - Slave
15e3a6d4-f7c1-4275-adb6-5b2c4ca1ca55 | checkpoint | Ih5
fe1522e8-650a-5c87-abdc-20cdd2f7597f | textbox | HPQ - Master
071eda75-efc3-5b14-aeea-c64bd3d69db5 | textbox | HPQ - Slave
792c28bf-f37a-4018-bccf-140dd199ee12 | checkpoint | Ih6
64e3be44-73b9-5770-af62-c7a778ef87fc | textbox | HPQ - Master
b7b8c7af-a918-51dd-96ef-6ea29767b796 | textbox | HPQ - Slave
fd8b3a27-8d78-4ee0-ab58-4e67f7570faf | checkpoint | Ih7
3d556409-dbdc-56df-bc1d-1a918dc0cfa0 | textbox | HPQ - Master
858e0eb6-92ab-57c0-8ac7-a89c8c06d2d9 | textbox | HPQ - Slave
209f6d6f-e260-45b3-90d9-fac0cfcf0b86 | checkpoint | Ih8
8f23f540-5e75-5f22-ad29-1b80686ee718 | textbox | HPQ - Master
6697e502-d53c-5efb-b3fe-5d7e377aafaf | textbox | HPQ - Slave
fac7e50c-640b-4775-bcb6-18f1888407c3 | checkpoint | Ih9
74ee786b-f837-5800-aa37-b18015c726aa | textbox | HPQ - Master
5f77c28e-a881-5775-a971-d048ff589882 | textbox | HPQ - Slave
db46a7b9-947c-404d-a66f-797630185758 | checkpoint | Ih10
e098d777-335f-571d-95ef-b3a8a4c712e3 | textbox | HPQ - Master
5b316997-9d6f-5576-a4d6-b92d41fd6b9e | textbox | HPQ - Slave
53c43281-125e-476b-b9d9-fe2084bc13c5 | checkpoint | Ih11
16e7bdd4-9329-5ce9-ad81-eaa19de8e269 | textbox | HPQ - Master
f4ea953c-7b68-58cc-a088-6dd560a834c4 | textbox | HPQ - Slave
eef7c206-1c33-47d8-ae49-c7ad3cc23cdf | checkpoint | Ih12
167c1679-6128-57c6-894c-80391fbf7a6f | textbox | HPQ - Master
318df3e1-04da-5b5e-bb73-0680735c6fdf | textbox | HPQ - Slave
246dde42-4aab-4524-a767-7fb45e70d0ac | checkpoint | Ih13
38e4f721-0d13-55af-8fe2-cad068d8646e | textbox | HPQ - Master
b9906752-bdb2-510d-add2-2a0e454e424a | textbox | HPQ - Slave
180bc7ab-ca6a-4a1d-a800-ed2b52df8405 | checkpoint | Ih14
ef4b4159-24a2-5d48-8a4e-6e4d56da7f23 | textbox | HPQ - Master
5cdf1d93-2b03-5d07-94a4-a9099f076b86 | textbox | HPQ - Slave
86a1a7eb-2072-4c4a-9b2e-f20e27725d8b | checkpoint | Ih15
55909781-3aaa-5a99-9aa9-ec9e6ce396dc | textbox | HPQ - Master
4a1cdadf-4881-5109-81df-1f75fef82278 | textbox | HPQ - Slave
d6ee6c86-f92b-4b84-9858-93a62d4a1eea | checkpoint | Ih16
1101c207-f808-52cb-b785-4d751e10e19d | textbox | HPQ - Master
ce53ddf6-b45b-565c-8713-60d638c050e4 | textbox | HPQ - Slave
c42cc0d1-b2bb-436a-9c91-c38462d8cc27 | checkpoint | Ih17
12cc0387-b996-5a59-81a5-11de6028a69a | textbox | HPQ - Master
7c520715-6572-5ea5-b977-6eb905ef020e | textbox | HPQ - Slave
08d88b7b-530d-4716-a7e9-127225b8db49 | checkpoint | Ih18
6c59ffb2-f39f-5269-8591-0845078b532f | textbox | HPQ - Master
cfb2b880-9fb8-5fea-be59-63c10911d49c | textbox | HPQ - Slave
50aaecd9-b3ca-49fd-a775-1d5f1651be53 | checkpoint | Ih19
44aa7aa7-2ca6-5491-bd7c-5419a41d0ecb | textbox | HPQ - Master
69e24997-a632-50bf-826b-1c4ad2d1eae8 | textbox | HPQ - Slave
d33853a0-02aa-4d51-9214-bf4d14a28591 | checkpoint | Ih20
5e728ea7-235e-5686-9054-280f6a598c81 | textbox | HPQ - Master
af3494e6-60bd-5e41-ab49-dab510386ce9 | textbox | HPQ - Slave
42ae131c-c6d1-4c3a-8f7e-6f8783c63290 | checkpoint | Ih21
7c98b47c-2227-567d-8e4c-d520c18fcdaf | textbox | HPQ - Master
80f57129-27ca-53d8-9686-20502ca4464c | textbox | HPQ - Slave
f3e940d4-6b8a-4e8e-a171-475728bebe47 | checkpoint | Ih22
6af0bac3-0b02-55f7-abbe-0aed5e6a50ac | textbox | HPQ - Master
dcf46165-e420-537a-a624-2805fccf2d14 | textbox | HPQ - Slave
c24f0f52-89f7-43a4-9e9f-6a2904245955 | checkpoint | Ih23
f5cf8f64-8076-5503-b102-3551d4356cc3 | textbox | HPQ - Master
4535595b-06e4-59f8-9adb-24c23679650e | textbox | HPQ - Slave
e4574bfa-14d6-4218-ba05-315e10f10b76 | checkpoint | Ih24
32e5de77-6b5d-5fe7-9e45-0e38274d20ee | textbox | HPQ - Master
46601ebb-8761-5e6d-af51-d4b0ee6b946c | textbox | HPQ - Slave
bca5476d-b4a5-4f67-9f49-2e06c2a77182 | checkpoint | Ih25
3a47c6a6-9d11-500c-9b32-b0228476989a | textbox | HPQ - Master
3b24d501-8414-5fd6-827f-02eb9ce4b0c4 | textbox | HPQ - Slave
4c5e2923-7d7f-4005-ba2b-4ad0d9787524 | checkpoint | Ih1
03342ffd-ede9-52fd-b850-ccc62b6e1c5e | textbox | HPQ - Master
da5f4a06-54f4-598f-830e-e1a60a1a9003 | textbox | HPQ - Slave
060f8b4c-7666-4fef-bae4-8334fa66bfa5 | section | POWER QUALITY PARAMETERS
95f9369f-413e-4612-8f7d-c2f42b64d4d9 | checkpoint | HAPFC Mode - "STOP"
4c9e2365-fa63-5878-b0a4-93fcb3f967d1 | textbox | THD_V, L1
b4114c37-c85a-5c4b-bee9-a9ffb6bdb311 | textbox | THD_V, L2
db8eab11-492e-550b-b26d-c3cb443ba8ff | textbox | THD_V, L3
8f4ef435-bf12-58e7-90d1-441413d69ca1 | textbox | THD_I, L1
6c61c43e-3e86-5e11-8282-b1ea3a327235 | textbox | THD_I, L2
e70aee6c-a8d4-5a5b-82ac-1cc53cfd472b | textbox | THD_I, L3
829a49ca-fc8f-5143-9227-376606019fc6 | textbox | PF
56b45949-14e9-41b9-9774-92cef3f13508 | checkpoint | HAPFC Mode - "RUN"
f3fb12ec-5ce4-56df-b88f-6a1715a5a50a | textbox | THD_V, L1
548c17ba-f255-5acf-b71a-797849d7e4bf | textbox | THD_V, L2
95a90edd-fb84-5f0b-928c-100673e1b5db | textbox | THD_V, L3
26be0161-27d6-5467-af88-39f10319ed31 | textbox | THD_I, L1
d5893299-a9bc-585e-a1f4-59ad52db474f | textbox | THD_I, L2
9193d364-b47b-54ea-a2be-27af442d9431 | textbox | THD_I, L3
145caa05-d833-58c8-a520-6c3f2c5c3fa7 | textbox | PF
a532d3a2-6f9a-4d96-931a-544bdc10ff0c | section | VOLTAGE WHEN SYSTEM OPERATING
4c0ef4c2-e697-4ae2-9643-5a2c3bd73f08 | checkpoint | LINE VOLTAGE
e222d102-7817-5fbd-ac02-ca7970d8d684 | textbox | L1-L2
0e91800c-0108-50f4-9a62-8a9b23c4d67b | textbox | L1-L3
349f0dd4-381c-5e28-a058-6a94afbe7d50 | textbox | L2-L3
bb02435b-3398-47bd-b546-d45ed267cbba | checkpoint | PHASE VOLTAGE
a0e1060e-b8e7-56f3-bf52-20bd8a4e71c6 | textbox | L1-L2
c3a2e032-a5aa-5665-ae12-2139c187ec3e | textbox | L1-L3
d628c41c-dc9c-512b-bdcf-7ebe5540fecd | textbox | L2-L3
44ec4e1a-8460-4a17-af12-d6fe5f943a46 | section | FUNCTIONAL TEST
cf8c124c-5d28-41a3-9c0b-f357a701b80b | checkpoint | FUNCTIONAL TEST
a4491653-0e8d-4538-99ea-9c4f61455a02 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000017 - MATV | itp | LEVEL
c1a25960-6dd8-43b2-9e98-2b4bdd36a4c0 | section | MATV
9bcebeea-037e-4320-94d4-c11827047578 | checkpoint | QLTY
9f4e519d-35e5-5f34-bdac-dfc19368ffad | textbox | Prg
038bea77-5887-5916-a7e0-026d99007b0b | textbox | Mode
449130db-2b64-5027-be6e-b06e99d5f2a7 | textbox | Freq. [MHz]
0d577c0d-3d0f-5a08-8cd0-3040f89006a8 | textbox | Prg.Name
aae12011-8bde-5f94-af5e-4e6a890da67c | textbox | Local Osc [MHz]
96498960-1065-5cc7-a687-4d1d64a9c0c6 | textbox | S.Rate or CH.BW.
b96adde9-917b-57cf-9f1a-b968108969da | textbox | Lnb Pol SEGMENTS
6710e214-9e20-5807-8ded-3f8bcc62212d | textbox | DiSEqC LAYER
8d3a3f41-1ae1-50cb-85c2-cf1502f4e797 | textbox | Stand. or Constel
78731852-733c-50b2-b8eb-497e5f4b734e | textbox | Level or Power [dBuV]
238ef39d-a953-5c3a-b755-945cfe8bc0de | textbox | C/N MER EVM [dB]
ad9fd651-8a87-547f-88e9-456b20ea0cdb | textbox | bBER aBER PER
690f7ec4-aef1-573f-9f3c-3eae94103b18 | textbox | N.MA. [dB]
6081df97-f53f-5e0c-8780-8688a401eb47 | textbox | FEC HP/LP CODE RATE
01f92c05-ee41-47a8-9447-14c632c6c579 | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000019 - Fibre Optic Cabling | itp | CABLE #
c91b0eb3-1793-4c21-8eae-c55874257b66 | section | FIBRE OPTIC CABLING
f9926649-2c23-4064-bed8-6e203478cd6d | checkpoint | PRE-REQUISITE WORKS
51b6a449-9a66-5f34-84f7-722817cc7cb6 | note | Confirm All Work Has Been Completed
f29fcbb5-291e-4615-a2be-1c51852575e7 | checkpoint | INSTALLATION CHECKS
d1b70229-037a-5e73-a9e0-08174094bef7 | note | Visual Inspection – No damage, outlet installed correctly
dbe90d71-c2d9-4725-98f3-71faf9188f59 | checkpoint | VERIFICATION & TESTING
a35a5c16-9be7-5ee1-b88c-251f79676829 | note | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
93cfe0f0-59af-5252-9e5e-c937be18a956 | button | LABELLING COMPLETE | YES,NO
86bac528-52a4-5742-b3d3-af3a052bb165 | button | FLUKE TEST PASS | YES,NO
beb7026b-c4bf-429d-97a8-16ba1920d0ac | checklist | SMCSWSPS-HEY-OSN-ED-ITP-000020 - Comms Copper Cabling | itp | CABLE #
e759e3fe-53e2-4091-98a8-f8e7885aabc3 | section | FIBRE OPTIC CABLING
364b0853-8808-4b34-9bc9-cc71b5ee824f | checkpoint | PRE-REQUISITE WORKS
da9489bf-0e58-56aa-9d6d-7e3167ce1c14 | note | Confirm All Work Has Been Completed
3e8d1c50-91c7-429a-b703-78caa9c64ec2 | checkpoint | INSTALLATION CHECKS
34d8fc00-b10e-5db4-9844-74162ef43425 | note | Visual Inspection – No damage, outlet installed correctly
a3a7c41e-ebe3-4a07-81bd-7e92d7ac8517 | checkpoint | VERIFICATION & TESTING
3a44051d-dd28-58ab-b7cd-688ee4fbdb5f | note | REFER TO SEPARATE FLUKE TEST SHEETS FOR TESTING RESULTS
5e9d8060-f437-5fd2-b0ab-bad8f23b8161 | button | LABELLING COMPLETE | YES,NO
5469449d-4449-55e4-a235-7392d12669e6 | button | FLUKE TEST PASS | YES,NO