## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 84f1edd6-92d1-4095-b761-3c20f7184d5e |  | checklist | Combined Services HDPE Natural Gas Installation |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation | 0945f706-e66f-4b50-8d17-9a9730a1c2a3
checkpoint-status | 0a3175aa-fe41-4b3d-90b1-f8f0094544c9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | a8cc2176-8380-4925-bd8a-218cd6b96d04 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | c2633378-7b57-4d29-842e-850f3303719b |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 1362d58b-790a-5bf7-ae6c-46c24049fcec |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | e6094e81-94ca-4d9d-950c-39e28deaa4bc |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 8494e1a3-1f51-4714-ba4f-d8880c45c0f3 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | d060a17a-9506-475f-9663-83bcb0f89d02 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b842a126-9259-4258-b424-da306dfbbf3d |  | checkpoint | Installation of Valves
label | e6b327b2-1ab3-50da-8e5a-1f74e07840a1 |  | note | Valves Installed as per approved drawings
label | ac7906b2-b8cc-5c24-b10d-c7629c2465ea |  | note | All works have been completed by a registered gas fitter ?
checkpoint-status | 7a8d2d0b-1a5b-40ae-be98-4c3fbfa7742d |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 3b47c0f9-7509-41f8-aad2-7c04494e4d10 |  | checkpoint | As-Builts Completed.
holdpoint | 770763b2-60b2-4a52-bd9c-629cb339c4fb |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 2071fdce-71e6-48f5-a16e-3e869c90e011 |  | checklist | Electrical and Communications Conduit Installation |  |  |  |  | Yes | Electrical and Communications Conduit Installation | 0ac1c466-5cab-4995-b8c8-2e310a39fd64
checkpoint-status | 89ca0071-978f-46b2-a4e2-2e7e94dc2d8c |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 2bd8548e-95dd-488d-93b9-ad086383f072 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b40091b8-fcd4-44c9-a134-579c66a61246 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | b7700a38-cba9-450c-9482-923f55821e7a |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | bd2227c6-325f-427c-a471-1bfb352116d2 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | a9e6b61f-846b-4aa4-a4fe-f8efb63ed756 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | 7a0ee8dc-b02f-4d17-aa02-3eb795f97afb |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 301b1e76-1927-4a3c-a012-7277bee08cec |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 80bb38ef-e6fc-440e-830d-ffa071494bb6 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 3e601c5a-5007-4205-8db0-449f1d223a2b |  | checkpoint | As-built drawings completed.
holdpoint | 1d6b6049-ac4b-4177-bc81-571764e33f00 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Flushing Site Details |  |  |  |  | Yes | Flushing Site Details | 14fe8838-0657-45a5-959d-923620a048b7
checkpoint-status |  |  | checkpoint | Flushing Information collected correctly
text | 289b83e9-905e-5b54-adb3-84011ecd1acc |  | textbox | Job number
text | 5ec7edeb-0317-599e-88ec-2c344a1ec671 |  | textbox | Job name
text | 436bc10a-f71f-543b-9d67-f07f69730ebc |  | textbox | Builder
select | 7a6a72aa-c4d6-59a6-8039-7d88d302e2af |  | dropdown | System Type | Domestic Cold Water, Chilled Water, Heating Hot Water, Low Temperature Heating Hot Water, High Temperature Heating Hot Water, Fire Hydrant
text | 23d61856-42db-5087-8235-0ded2de7eb91 |  | textbox | System Volume (Litre)
text | f1069765-4da1-581f-88ea-b3a7bc1e2607 |  | textbox | Location
text | 9ba3bf1f-f8fe-5a0c-9513-23d0d4b60fa8 |  | textbox | Drawing
boolean | 55b9b059-090d-5647-9bf3-25f4d6279e25 |  | tickbox | CIBSE Commissioning Code W
boolean | 103dc8dd-38e3-51b3-a839-4946c8884f2d |  | tickbox | BSRIA BG 29/2012
checklist-flat | e6cf7c50-39e1-487f-9128-e634e4ab7b73 |  | checklist | Communications Underground Conduits Installation checklist V2 |  |  |  |  | Yes | Communications Underground Conduits Installation checklist V2 | 14ff041b-7ebb-4c25-bd5f-827fcd408852
checkpoint-status | 95f88952-3d91-4561-ac09-b999249df6ef |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 607fd13a-3934-42ae-8f7c-1187f52a65b5 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 0de3202a-8d31-49a6-86bc-4252a1098c2b |  | checkpoint | Location
label | 56939f75-866d-592a-b46a-2e182b0c6ced |  | note | Shall be as shown on the drawings,
label | 58de8721-0e3c-5fe7-9970-a60cbab47d88 |  | note | Shall be as instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction.
checkpoint-status | 4ddb7381-3aac-4e73-b9af-24668596f627 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | 66c9e073-44ea-4846-8ba0-f08f7c31931e |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status | 2a636d9d-005b-46c4-a2f7-0148f7f14a37 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | a7476b81-82bb-4081-b01e-7fc664a8f891 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | 2b3c24a4-52e1-453e-b4bc-f4edb217914a |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | fa099bf4-067b-4968-8032-d6dbff6f8526 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 9446e641-7c2d-41b7-b3b5-4e76027cc87f |  | checkpoint | Bedding of Conduit and Pit
label | dc6ea2f4-4865-5541-811c-10d48cd9c23e |  | note | Conduits and pits shall be bedded on approved bedding material.
label | 7b516200-ea94-5b70-b184-aaf8bab421ad |  | note | Bedding material shall be 150mm above top of conduit
checkpoint-status | 53e0e8b3-2c81-4b20-8876-16e510a14885 |  | checkpoint | Conduit Pits
label | a305ecc0-da54-5e0e-aada-9750acaa0e26 |  | note | Conduit entering and exiting a pit shall conform to the locations and dimensions shown on construction drawings and specifications.
label | 2d053dee-1b78-5831-b86c-c195527ec0cb |  | note | Conduits shall protrude into pits at least 50 mm and not more than 100 mm.
label | 8c1e675d-07dd-5d7e-95e9-d435ea19ed57 |  | note | Where practicable, conduits shall enter and exit a pit at the same height and orientation.
label | c080c9d6-762b-5e30-ae05-386b2d7785fb |  | note | Sealing around conduits where they enter the pit is to be undertaken on the inside and outside of the pit.
checkpoint-status | 15f9ec4c-c500-41a6-8be2-cf0fb4e5e64a |  | checkpoint | Bell mouths to be installed where possible and correctly colour coded.
checkpoint-status | b5d535b8-7174-4b26-8591-9ce53fbdd488 |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 8deb4b60-3083-469a-8db2-37ceac93a574 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | ebac3d61-30c8-47c3-a1c2-2f5b541e5456 |  | checkpoint | As-built drawings completed.
holdpoint | 11e04522-7237-47b1-bd64-73bdc3b94712 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 9ed59ce6-b523-4a22-9240-6d8641c687d3 |  | checklist | Natural Gas Gastight Air Pressure Test - Test 2 @ 315kPa |  |  |  |  | Yes | Natural Gas Gastight Air Pressure Test - Test 2 @ 315kPa | 17246dbb-fdeb-4b41-b034-77013a4e8448
checkpoint-status | 95a8e075-6cb0-4a8c-b66d-197662dcead4 |  | checkpoint | Ensure the system is disconnected at the meter or from the cylinder
checkpoint-status | 71c204e8-4089-4364-924d-ba55ba0d3746 |  | checkpoint | Ensure all open ends are capped or plugged.
checkpoint-status | 10197af8-29a3-4641-9991-36aa7a8b84c1 |  | checkpoint | Ensure all gas appliances are isolated.
text | 0dfd952f-ee02-5cf2-8ea1-2f9467639463 |  | textbox | Connect a suitable test instrument. Serial No...... | text
checkpoint-status | 1405ffc3-1683-4a07-a906-119edf1160e7 |  | checkpoint | Raise pressure to 1.5 times the operating pressure to 315 kPa
checkpoint-status | 28181492-65f9-4693-af42-c47f3c6782cc |  | checkpoint | Isolate the pressure source and allow suitable period 2 minutes for the temperature of the testing medium within the consumer piping to stabilise.
text | 83937dff-cc9f-5772-b34b-2a0a088be993 |  | textbox | Measure the loss of pressure during the test period of 10 minutes | kPa
checkpoint-status | 3faf869a-8979-4be6-967f-663856e78468 |  | checkpoint | If no pressure loss during the 10 minute period the pipework can be considered gastight.
holdpoint | e6a84e1e-eb6f-4bbd-8bfa-8e4b77fa1d54 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 910b4d2f-20e6-4202-b30f-e5a98f1673b7 |  | checklist | Butt Welding |  |  |  |  | Yes | Butt Welding | 1af85a7b-4718-4fbb-9bfd-d718da1b261e
checkpoint-status | c8dee859-39ca-4784-9e6e-7d9941180258 |  | checkpoint | Weld Details Completed
text | ed0b2069-38ae-51a6-b0c2-c74383a77503 |  | textbox | Weld Number
select | 654e0c4e-ae75-5efb-9283-fce9597f1eee |  | dropdown | Weld Completed By: | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
select | d7bd3611-6574-5e7b-985b-31213b80e0b3 |  | dropdown | Welding Machine # | Machine 1, Machine 2, Machine 3
text | 1ef3ca77-bad6-5887-9679-d203af4d134f |  | textbox | Certificate #
checkpoint-status | 9348f672-5bb8-48af-8f81-f1ebc2d0197e |  | checkpoint | Pre-weld checks - Visual Inspection of Pipe
label | c297085c-730f-5bd0-a703-add028ac308b |  | note | Ensure branding markings correct
text | 72f28d58-c2ea-537b-88a4-d9afc569fad0 |  | textbox | Record pipe batch number as labelled on the pipe.
text | 72602a86-7457-55e5-9585-0023a698231b |  | textbox | Record pipe wall thickness and inspect.
label | aa5c60b5-1bda-547e-b1ba-b0ddb3e8d4df |  | note | External surfaces are free from scratches deeper than 10% of wall thickness.
label | 307a431e-3d7e-5560-bb54-19623f62c94f |  | note | Inspect internal surface of pipe for scratches.
label | 741c3ce7-5ff4-5c6d-a4a4-44176bfa9235 |  | note | Inspect pipe for cracks.
label | 31efab25-044f-586a-afc0-b20d72a11a63 |  | note | Inspect internal ridges or ripples exceeding 0.5mm in height.
label | 69994fdc-2df3-5a06-889c-37bd5e3df477 |  | note | Clean and wipe pipe with Isopropanol.
label | 78fbbf96-1404-5ecd-bb1b-106fd6853b90 |  | note | Inspect pipe ends are dry from any water content.
checkpoint-status | 73772ba4-d361-4e96-8692-3d8c064313f8 |  | checkpoint | Pre-Weld Checks - Weld Machine Checks
checkpoint-status | 305a8ae4-dd9b-47d5-a05a-c98a7c967f08 |  | checkpoint | Heater plate temperature checks taken and recorded
label | 1392f678-f011-5811-8d91-60940c6de348 |  | note | Ensure pipe ends are capped, welding area isolated to regulate cooling and prevent airborne contaminants.
checkpoint-status | 1ea12469-42df-4f80-8fdc-0a2f3f53ec8c |  | checkpoint | Post Weld - Visual Checks
label | 76f5e0b6-ffdb-5394-8452-e2113022e127 |  | note | Alignment of pipes is less than 10% of pipe wall thickness?
label | d23a7c58-7cf9-5b49-93d3-f2f4774a6d5d |  | note | Fusion beads symmetrical on both sides of weld
label | 8a940c97-118c-5404-a362-346945f8027d |  | note | Ensure Beads are fully rolled over
label | e44185ee-cac1-5d5e-881e-703a3e83133c |  | note | Inspect for cracks in beads and welds are free of pitting and bubbling.
label | f6237a4a-5669-50c3-8fc2-c13123f6f9ee |  | note | Inspect for inclusions or other obvious faults present.
label | ab1817be-06cf-55e1-9e24-276ba3926f96 |  | note | Internal weld beads removed from pipe?
checkpoint-status | 0c3354d5-b811-4786-a402-b6cc6a3c35f5 |  | checkpoint | Weld Records and Inspections
label | bd6b904f-1749-5199-a285-561c0b2364f8 |  | note | Data logger records printed, checked and attached?
label | a35d4317-dd9a-5182-809b-b0cc5628a06c |  | note | Weld completed, inspected by AE Smith Supervisor and CPB ?
holdpoint | adfc0216-485c-4223-9d0d-7e70004f848a |  | signoff | Post weld checks by CPB and AE Smith - Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | Combined Services - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | zSYS - Combined Services - DCW Pipework Hydrostatic Pressure Test (old version) | 20f33fdd-15b4-4171-99e8-78861382ce8d
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 19ac87af-243d-572f-a653-83a9e1a4ffce |  | note | Resp. - CPB
label | cf901e95-73a1-504e-a5c6-fb26910a26a3 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | bdd4ff24-eacb-549b-a1be-d376211d9a79 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | e614f261-4a77-56b0-b094-f7c1467eea9e |  | note | Method - Document Review
label | 4d960283-91f4-5c1f-aad4-bea161398e7a |  | note | Frequency - By Building/Site Wide
label | 78f681c7-0947-5d88-83d2-4a4d0aaa2c27 |  | note | HP - CPB
label | 5a225285-eebf-53d5-9d83-338414346937 |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB Signature
checkpoint-status |  |  | checkpoint | 1.2 - General
label | 0c8cdb2d-3851-5263-b2ee-9e581c7a45d2 |  | note | Resp. - SE
label | 851ae1eb-0252-57ac-8174-629afb629202 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | b1cb5f6f-7f97-5d22-8254-2264e3e9afc7 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 67e1a4db-e59b-5196-806d-65453c73fb89 |  | note | • Specifications & QA Documents Approved
label | a6e6d10a-4dd7-5f08-bd9b-75a34c85d529 |  | note | • Drawings are confirmed
label | e2564e4f-9e66-5a82-b3b4-6b121f83ddd4 |  | note | • Equipment fit for purpose
label | fba30701-aa48-511c-a401-2c139a92772d |  | note | Method - DR
label | dbdd23b8-f3eb-5f1d-93a0-3b831773bc91 |  | note | Frequency - Each material
label | 209d28c2-dfb6-59d7-a210-b502a302b9d5 |  | note | HP - CPB
label | 34b1d896-5235-5867-8544-013745aa702e |  | note | Records - Aconex approval
label | 7f088090-4990-5ad0-b56b-42d6f94c688d |  | note | • Incoming Inspection Checklists
label | f0f2cdce-0ca5-5583-957e-30a45324ee1b |  | note | • Drawing Register
holdpoint |  |  | signoff | CPB Signature
checkpoint-group |  |  | section | 2.0 CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | 2.1 - Confirm Flushing & Disinfection of Pipework
label | 72531d12-085f-5c45-b5cc-b17c6e859357 |  | note | Resp. - SUP
label | 9e858156-c965-5bab-8f85-bd5f482c8f09 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0001
label | 4abfea50-035b-5dd2-b587-81ae7b234397 |  | note | Conformance Criteria - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
label | 832665de-c21d-5898-9630-05d477173feb |  | note | 2. Ensure system sterilization completed.
label | c01ab33d-314f-5899-850a-230ff5fc7a6e |  | note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
label | c0e389e0-13f9-5a73-a0fb-2a44f2a4e618 |  | note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
label | e6abbc2d-7620-5145-8199-0d530480568e |  | note | Method - V + DR
label | 892f35e1-f3f3-5041-9a47-79054e3eb608 |  | note | Frequency - Once
label | 103c4304-a3be-553c-88c1-76107d7c956a |  | note | WP - AE Smith
label | e6862dcb-21ce-510d-96e0-4a6a8a7be229 |  | note | HP - CPB
label | 2f2e16bd-c93e-5e7f-b4e5-c816cd957692 |  | note | Records - CMP + Check Sheet
holdpoint |  |  | signoff | CPB HP
checkpoint-status |  |  | checkpoint | 2.2 - Accept delivery of pump to site
label | 4d766ea8-1a2c-5892-a29c-ce28c931e3a5 |  | note | Resp. - SUP
label | c4100db4-9025-5cdd-9812-ce57d9c59d12 |  | note | Referenced Documentation -
label | a4bdf4e4-b135-5412-ba1e-a0c61afed78f |  | note | Conformance Criteria - 5. Check pump is rated for pressure test
label | 4d6615b0-1f11-533a-9898-47995e03af0a |  | note | 6. Check all supplied attachments are correct and in good order
label | 71439bb7-78f4-58f0-9b0b-a8c5e006a400 |  | note | 7. Check fluid levels & fill as necessary
label | ea9c20f4-9519-58c4-b303-fb825cb4ff05 |  | note | Method - V
label | 8a82729e-a7dc-528f-81c6-0b61d64ccc54 |  | note | Frequency - Once
label | dff18c7c-ef2e-55f2-987b-0739fb87e5a1 |  | note | WP - AE Smith
label | ac0712af-4b80-5cd7-bd37-0b9751b9ff3d |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 2.3 - Isolate: Mains water Storage Tanks
label | ba8ee030-aefd-5b22-884a-71d6a9b1a7b2 |  | note | Resp. - SUP
label | 417e997d-3d69-5aa5-90e9-e04512e53ea7 |  | note | Referenced Documentation - AEC-NZ1005-TNK-DWD- HYD-006
label | b445bb73-fdbe-50c3-aecd-56ee3c8d061f |  | note | Conformance Criteria - 1. Check Mains water is isolated
label | 165b88e4-f1df-5fbc-af5f-f7b410c6b27a |  | note | 2. Check Storage Tank is isolated
label | 55ac4c47-ce02-5686-9596-cea6b1755f78 |  | note | Method - V
label | 50b7ca24-dba6-549c-88ae-1d56e0408e17 |  | note | Frequency - Once
label | 94c80baf-27cb-5699-ab8c-1bf5bab50f06 |  | note | WP - AE Smith
label | 504fc2d8-d3f7-51b4-8f3c-e51670fc3aca |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.4 - Connect pump to DWC ring mains
label | 25b34559-6867-5785-b39a-adb1b4c2f4ab |  | note | Resp. - SUP
label | c588961e-79f3-58ab-94ea-ee2c64ffe413 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | b92aab96-7c76-5628-ab0d-cb0adf74b6c0 |  | note | Conformance Criteria - Confirm connections are safe and correct
label | 3a5bb5bb-20be-5eb0-b48c-43735286d000 |  | note | Method - V
label | 9c3dff67-8341-5c6e-a7c7-4a3f06bc63be |  | note | Frequency - Once
label | 8e73f2e5-e0b4-5d11-b3f0-86d8fa849833 |  | note | WP - AE Smith
label | 15cb1b7f-492b-5c9e-9ca6-a7d61aa6a523 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.5 - Connect calibrated gauges for pressure test
label | 04e2a4ad-5aae-549b-b79f-ecfeb3fbd4d7 |  | note | Resp. - SUP
label | ae2d15c7-eda3-5fec-a0cc-66927afa0eff |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | faaa4e54-fbbe-5d22-83a4-c6a7277ae6ee |  | note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
label | 76298ff8-8e55-5b96-afdc-782a4f0092c0 |  | note | Method - V + DR
label | 2650e6dd-2e1a-5027-833c-1c7ec6e52678 |  | note | Frequency - Each test
label | acbbb092-8be3-5e9e-a300-eb0dd7b25ac5 |  | note | WP - AE Smith
label | aecd5eeb-a5bc-52cc-87e8-f77cbc77f1b5 |  | note | Records - Check Sheet + Document
checkpoint-group |  |  | section | 3.0 HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | 3.1 - Fill DWC ring mains with domestic water
label | e45db890-4dc1-5f55-8af2-883732e33eb4 |  | note | Resp. - SUP
label | 0b75b99d-ab08-50ed-b61a-f80c32fb9049 |  | note | Referenced Documentation -
label | be5a3e49-d9cb-5d88-84c5-65a3b6cd8b96 |  | note | Conformance Criteria - Completely fill closed loop system with water releasing all air from the Taps at each Building
label | 255cdedf-224b-5b64-8cb6-73bb5f938bb8 |  | note | Method - V
label | 8fbca535-bdcb-5cb0-9b3c-026de8306a2c |  | note | Frequency - Every time system is opened
label | 9e0d319a-5859-55fc-b117-a632c01ce427 |  | note | WP - AE Smith
label | 4b3878b2-46f6-5f75-b89d-a2e0fa5b8dfe |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.2 - Gradually increase system pressure to 1550kPa
label | 83b3a4c7-0236-5f7e-9289-96b53ac4897f |  | note | Resp. - SUP
label | 50a7aaf5-239d-597e-979d-6a17fa04d18c |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | 1c7bb123-129d-51ac-aba1-102e9698d8d6 |  | note | Conformance Criteria - Slowly raise system pressure to 1550kPa
label | 39439daa-90d4-5033-9480-8ebf92f9d86a |  | note | • Checking for any signs of leaks or pressure drops
label | 6ba1a119-e0e3-5919-aaa4-57bd7ce74139 |  | note | Method - V+M
label | 408c38a0-840b-556d-8afe-d385ac8d2165 |  | note | Frequency - Constantly Monitored
label | 51a01a2c-f6ed-5617-8aa1-23afffadab36 |  | note | WP - AE Smith
label | 757de123-290f-5b35-98d1-bb506d1ef9fe |  | note | Records - Check sheet
checkpoint-group |  |  | section | 4.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 4.1 - Testing Results
label | 5188c3cf-e1fd-5863-b940-b4f4cc427ec3 |  | note | Resp. - SE SUP
label | adeb08ea-c7e8-519f-897b-8fdee0f7d60c |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | 7db23b81-5261-5530-acd8-e079263a96a7 |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | 2e769fa2-16c9-585b-98cf-55defa2f9069 |  | note | Method - DR
label | a50ad101-e98b-5119-a0d2-5a470c5073bf |  | note | Frequency - Each lot
label | 1e734ca2-f2b9-5c9b-92f2-91e23ee3aa31 |  | note | WP - AE Smith
label | 1dee6e54-2db2-54c7-9ade-d9bde686b8be |  | note | HP - AE Smith / CPB / IR
label | edb5a434-f1f5-51e7-b3f4-92e37f66f425 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | CPB Signature & separate IR Signature
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0028- Tank farm installation |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0028- Tank farm installation | 275cd636-4931-416b-a583-234531c660dd
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 95c03c35-29d1-5465-a0f2-70e9182a673e |  | note | Resp. - CPB
label | 4ca692b3-184e-5f75-8959-43d7f9586b15 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | 7e587dce-586e-5586-a6f5-96c9b2dae896 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | 22c77015-e2f9-5530-bfe6-561b852a5efd |  | note | Method - Document Review
label | dfb250c5-9fea-5cb7-aec4-6a49af9c68d1 |  | note | Frequency - By Building/ Site Wide
label | f468596d-10eb-5abf-a866-2fdc287f997c |  | note | Hold Point - CPB
label | 7c8316e3-0a79-5ca2-b5f4-e76e2eadafaf |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - General
label | cdb3df0d-ea2c-51c3-ac70-ec86a05b24ff |  | note | Resp. - SE
label | 8bfe6d5a-3860-5215-a251-58cce5d1644b |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 6c16dd66-d6ff-50e7-ace4-aa537905cd50 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works. • Specifications & QA Documents Approved • Drawings are confirmed • Equipment fit for purpose
label | 0eb95fbb-8eb3-5f1f-a6f2-a19846a64a32 |  | note | Method - DR
label | 6c300ac1-1a3b-563f-bae7-7a6e870c94b5 |  | note | Frequency - Each material
label | a4cf9d61-e22e-5577-87a6-0e17f76b0dd7 |  | note | Hold Point - CPB
label | fce2375a-0177-58e6-9500-02faa612a5b8 |  | note | Records - Aconex approval Incoming Inspection Checklists Drawing Register
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Installation
checkpoint-status |  |  | checkpoint | 2.1 - HDPE Support system & seismic Loops
label | 192d46de-a5d2-514e-95f0-28791352363f |  | note | Resp. - SUP
label | 8a14aeb6-1d59-5ec5-bc83-30b221b9373c |  | note | Referenced Documentation - AES-NZ1005-TNK-DSH-SEI-0001 AES-NZ1005-STE-DSH-SEI-0002
label | 7c71fc82-8845-5467-a5d4-cc382755a7d3 |  | note | Conformance Criteria - Check the piping support system has been installed as per the Modframe design
label | cd917723-f488-5f4f-a524-1bff186ddcd4 |  | note | Method - V
label | 6f6ff675-ab9f-5dc6-b4d7-2c959b9a216a |  | note | Frequency - Once
label | 867de450-d5d7-5a7d-b83d-50c7d9d3aee6 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.2 - HDPE installation and testing
label | 00f67fbe-c67a-5f07-ad9d-4ebe3517ff67 |  | note | Resp. - SUP
label | 029dbbc0-2912-51de-accf-422b2068f178 |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004
label | c7173d16-931d-5093-b915-c4e98b4676a0 |  | note | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-004 for the installation and testing of HDPE pipework
label | 57d49d9b-6105-5352-b6cd-f26197ca6f88 |  | note | Method - V
label | a455da33-0b31-5dc2-b98d-7474148f0b2f |  | note | Frequency - Once
label | 2bcc7c9c-2402-58e6-9dad-641deff1127b |  | note | WP - AE Smith
label | 6f4a58cc-496e-5cb7-90ff-f7f98f8d236c |  | note | Hold Point - CPB
label | 53989aed-4fb4-571c-b5cf-a7679b1eb9d5 |  | note | Records - FRT +weld test reports +QCC (refer site wide testing check lists)
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Confirm DCW flushing and disinfection complete
label | 08fde75b-644b-53e0-b741-2ab0565f6431 |  | note | Resp. - SUP
label | d801b86a-99c8-5b2f-89fd-5deb394c1d09 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0001 NZT5007-STE-HSSP-0001
label | 68602bab-0661-513d-9a4e-35c365465552 |  | note | Conformance Criteria - Completed with the flushing and disinfection of the site wide ring main Refer to the Flushing and Disinfection commissioning plan
label | c590c1e5-c867-5761-9b03-0693e619d28c |  | note | Method - V + DR
label | 83a1187e-33ce-560b-b3b6-dac72afea331 |  | note | Frequency - Once
label | 62b77010-f46c-52a2-baee-96e9ab4fbe3b |  | note | WP - AE Smith
label | dee1de7e-70f3-598d-90b6-dd6afb821a53 |  | note | Hold Point - CPB
label | 94205c5b-a181-55f4-937e-6f27ed9f0626 |  | note | Records - CMP + Check Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Confirm Hydrostatic pressure testing complete
label | 58cdc08b-064a-5eaa-94ab-927b416bca92 |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0024
label | 78e72945-8b46-5d5c-bf18-13fbde99e0b8 |  | note | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-0024 for Hydrostatic pressure testing
label | 7c3bcee4-cb53-5d8c-818f-37f6f66f1055 |  | note | Method - V+M
label | a85a8521-6ecb-58d3-8ba6-fa9e3e63a242 |  | note | Frequency - Once
label | e993ac71-b925-58ce-bb7c-8828b1adb6ac |  | note | WP - AE Smith
label | 7a2d10cf-8c1b-5c41-a44d-c4fd97456e07 |  | note | Hold Point - AE Smith / CPB / IR
label | c65dbcdd-99e7-5227-b5e4-57c1b39e4bed |  | note | Records - Check Sheet + Photos
checkpoint-status |  |  | checkpoint | 2.5 - Electrical Installation Complete
label | f1e978df-222b-5e83-be2f-6ead26544007 |  | note | Resp. - SUP
label | 198a8288-8968-5454-888b-86d39acd2770 |  | note | Referenced Documentation - AEC-NZ1005-STE-SPC-ELE- 0002 AS/NZS 3000:2007 AES-NZ1005-TNK-SHD-ELE-0002
label | 696aed68-f691-59f8-a301-d3a7e2ec1c61 |  | note | Conformance Criteria - HSSB installed. Mains terminated Feeds run to filter controls Feeds run to pump drive board Feeds run to chlorine dosing units Labelled & Tested
label | 41866f09-3dd3-5065-af2a-0c5af3c22cd4 |  | note | Method - V + FTR
label | 210296cb-9f7e-54bd-93f1-b1e02faf4605 |  | note | Frequency - Once
label | f0089f56-4c82-5953-9fd7-80f86f477796 |  | note | WP - Ae Smith
label | 582cfa1d-22ab-5c77-a88d-93303dba0720 |  | note | Hold Point - CPB
label | bcb59e1e-22db-5b1b-9fb8-a22cb30e3882 |  | note | Records - Check Sheet + COC
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Chlorine dosing Install & commissioning (Include PRVs)
label | 981e161a-0eaa-58b1-ab0e-0d60202504c1 |  | note | Resp. - SUP
label | 614c5acf-3c3f-5a80-92ee-5b28034ec541 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | 41d25aed-5ab7-5a54-880c-fb7f3b4088a2 |  | note | Conformance Criteria - 1. Access is suitable to service dosing equipment 2. All electrical checks are complete and permanent power is on 3. BMS connection is complete by others 4. Pipe work checks are complete 5. Isolation is provided to enable either system to be maintained seperately without affecting the operation of the other 6. Equipment mountings are complete 7. Pressure reducing valves are installed in the correct flow direction and set to desired pressure 8. Dosing control sensors are installed. 9. Non return valves are installed in the correct flow direction 10. Dosing specalist to commission and provide report 11. BMS monitoring is commissioned 12. Confirm treated water meets the requirements of the NZ drinking water standard.
label | 33903c87-c67b-5b53-89f0-5a418617a862 |  | note | Method - V
label | 2fb41893-969e-5bfa-8b8a-8015c7bbbc77 |  | note | Frequency - Once
label | 30513888-7523-558e-8565-c32cc201d43f |  | note | WP - AE Smith
label | 90605087-8882-5b31-80b9-0f453dc29a96 |  | note | Records - Check Sheet + FTR + LTR + CMP Report
checkpoint-status |  |  | checkpoint | 2.7 - Domestic Cold water Pumps & Drives
label | af447179-2973-5b09-8e4d-b24c8c483fd7 |  | note | Resp. - SUP
label | 06d67e8b-6b02-5c1c-84d7-92d79b76c3bd |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | 01e28adc-78bf-5eb9-bfc9-8cdb1f04197c |  | note | Conformance Criteria - 1. Confirm pumps & drives are as approved submission. 2. Installation is as per shop drawings. 3. Motor drive board installed & wiring to pumps complete. 4. All electrical checks are complete and permanent power is on 5. Pipe work checks are complete 6. Pump mounting and vibration pads and seismic restraints are complete 7. Non return valves are installed in the correct flow direction 8. Isolation is provided to allow maintenance of any individual pump 9. Grundfos to commission and provide report 10. BMS monitoring is commissioned
label | 08985e41-d80f-54f0-9b5c-13d82ab9c0a3 |  | note | Method - V + FT
label | 339b8fb5-ef97-5c7c-b904-830522a38143 |  | note | Frequency - Once
label | 941603d2-83bf-5921-a701-f5f37b32c61e |  | note | WP - AE Smith
label | 641fe04b-8f51-5e5a-b5ba-221735aedd6e |  | note | Records - Check Sheet + FTR + CMP Report
checkpoint-status |  |  | checkpoint | 2.8 - Primary and secondary Filtration systems
label | 16ce8c55-7872-5b10-98fc-cdf87c6b7656 |  | note | Resp. - SUP
label | 95fdd5af-ff5f-520f-bed4-aaa522c2d940 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001
label | 8cffd523-6154-5296-9796-03d81d3858fe |  | note | Conformance Criteria - 1. Confirm filters are as approved submission 2. Installation is as per approved drawings 3. Pipe work connection checks are complete and without leaks 4. Mountings are complete 5. Non return valves are installed in the correct flow direction 6. Isolation is provided to allow maintenance of any filter 7. Backflow drains provided 8. Southland Filters to test and commission filters and provide report 9. BMS monitoring is commissioned
label | cdd19de9-e35e-5230-8421-e1bce3c236ab |  | note | Method - V + FT
label | 57694407-4834-503a-a701-532e9ceb4ad2 |  | note | Frequency - Once
label | 6c984b24-ee39-5bba-b4fc-8f4ff9fc5c5e |  | note | WP - AE Smith
label | d7849f46-efd8-55c5-9041-569582cd9e82 |  | note | Records - Check Sheet + M + FTR + CMP Report
checkpoint-status |  |  | checkpoint | 2.9 - Motorised control valves
label | 0e23d777-923d-5479-8e66-d64e1ee87da4 |  | note | Resp. - SUP
label | d356e585-ae82-59f3-a3cb-b1d5a0eae8a2 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 8a09e93b-40f8-54aa-99d4-760345b41873 |  | note | Conformance Criteria - 1. Confirm valves are as approved submission 2. Installation is as per approved drawings 3. All electrical checks are complete and permanent power is on 4. Pipe work connection checks are complete and without leak 5. BMS control is opertional- check motorised valve positions in normal and emergency operating modes 6. Plantroom bypass Button is operational – check motorised valve positions in activated and deactivated modes. 7. Check button is clearly labelled.
label | 192ab821-debe-501c-9845-2d5298ee418d |  | note | Method - V
label | a75aa62d-f0ee-5cfa-9a12-1a52e67a9195 |  | note | Frequency - Once
label | d2e52312-1c86-54b7-b55b-38e879e70cfd |  | note | WP - AE Smith
label | c48a78da-1a78-59b8-b2ca-6969828a443f |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.1 - Potable Water Tank Level Control valves
label | aaa3fd01-dad9-5ca8-b57c-990ddc175536 |  | note | Resp. - SUP
label | 086b3981-5303-5984-b893-3c704b51d377 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | c4e7bb69-0e22-52f0-b289-13cc58beba82 |  | note | Conformance Criteria - 1. Confirm control valves are as approved submission 2. Installation is as per design 3. Float valves are adjusted to to ensure overflow state does not occur
label | 60059d1c-51c5-5e77-ae9f-a94f7ae8be26 |  | note | Method - V
label | b2871bed-3216-5d0d-a431-0775f640b8e3 |  | note | Frequency - Once
label | 98b87e5f-cfb4-51eb-be94-87e8738d228f |  | note | WP - AE Smith
label | 35da07cc-7390-527f-8271-960d61f857b7 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.11 - Alarm indication on and tank level montoring on BMS
label | f7e78a71-489e-5e44-abea-c29960d4aa41 |  | note | Resp. - SUP
label | 6bbbb000-69d7-5476-acc2-f1a8bc110fb6 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 5afb247d-47de-5c48-83f4-0a154d20d51c |  | note | Conformance Criteria - 1. Tank level monitors are installed as specified 2. Tank level monitors are connected to the BMS by others 3. Verify BMS level output
label | ca2ca0bb-4338-5287-9ed1-e731f50b8244 |  | note | Method - V
label | f760730b-6305-5133-96df-60ec016a0647 |  | note | Frequency - Once
label | 0b0916ba-6a08-5a48-a6a2-25488624e236 |  | note | WP - AE Smith
label | 50a7ada1-2413-5eef-bed7-139e4f486b2e |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.12 - Back flow preventors
label | 62c240f9-9420-5533-a8ba-3f29d3e3bb74 |  | note | Resp. - SUP
label | 8ae5e09a-c1cd-548b-b0e5-2f8d0aba2a29 |  | note | Referenced Documentation - AS/NZS 3500.1:2018
label | f0ac9454-097d-560d-a81f-8fc8baf5e1a8 |  | note | Conformance Criteria - 1. Confirm backflow preventors are as approved submission 2. Installed as per design 3. Pipe work connections are complete and without leak 4. Check flow direction 5. Check strainers are clear 6. IQP test
label | db9e58bb-9fc0-53a7-a454-146773531bb7 |  | note | Method - V + DR + FTR
label | 60f80b49-60ac-5f8a-9b1c-023beb337adf |  | note | Frequency - Once
label | 93f70996-83a2-5970-83a8-1c573577f080 |  | note | WP - AE Smith
label | 0b7076be-6d28-58f0-8115-f6664fba6d19 |  | note | Records - Check Sheet + IQP - FTR
checkpoint-status |  |  | checkpoint | 2.13 - Wash bay supply & RPZ
label | 811209a5-1b95-50ca-bbe6-81f07fb95a3d |  | note | Resp. - SUP
label | 5038b748-67ca-5a6e-b1d1-3fe87b9499bd |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004 AES-NZ1005-STE-ITP-PMT-027 AS/NZS 3500.1:2018
label | 449128ac-e4cc-56ac-9bbd-6390111ca08b |  | note | Conformance Criteria - 1. Confirm pipe work has been installed, tested, flushed and disinfected as per items 2.2, 2.3 and 2.4 2. Confirm RPZ Back flow preventor has been installed tested as per item 2.11
label | 1892fb8a-c808-5a8c-bfc3-ff8c092306aa |  | note | Method - V + DR
label | b4aa27cb-7795-5c3d-b384-493f1b889e1c |  | note | Frequency - Once
label | dc0a93c4-ffbd-5eba-9527-d5e0a0357a26 |  | note | WP - AE Smith
label | d51e4fac-388f-575e-950e-a33d9c0b6908 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.14 - “As built” drawings
label | 78c9878f-0f19-5a5d-9199-40c452628362 |  | note | Resp. - SUP
label | 737a2fe8-1506-55dd-85d6-85eb2ab7528d |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 17a503e3-49a8-578f-aa0e-c258b6400814 |  | note | Conformance Criteria - 1. Mark up construction drawings with as constructed changes.
label | 1befdaff-82a0-5804-87bb-fa9681f60331 |  | note | Method - V
label | 7e85a78e-c8e5-55b4-a9f1-cc4a57bb3109 |  | note | Frequency - Once
label | 33ee688e-247b-5d93-8f9e-dcdfde73609c |  | note | WP - AE Smith
label | e17698f6-7ded-53bb-bbd1-5477038f2c71 |  | note | Records - Check sheet
checkpoint-group |  |  | section | 3.0 Completion Testing
checkpoint-status |  |  | checkpoint | 3.1 - Works Completion Test WCT 54
label | 26e57458-d55b-58b4-a2ce-491cc011b6ef |  | note | Resp. - SUP
label | 3a4c75a7-53b3-59ef-9b62-34673b767a5c |  | note | Referenced Documentation - Schedule 11 WCT 54 (e)(f)
label | a6a2e322-1278-59a2-9954-689e533cdac0 |  | note | Conformance Criteria - The EIS for the New Waikeria Facility have been installed in accordance with the FDD. This includes EIS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the following systems: (e) general power; (f) earthing system;
label | d3aabe33-2104-5755-8e1b-201fb7746f0a |  | note | Method - FTR + V + DR
label | 27a51a3d-e230-5d65-8301-66703d936cc4 |  | note | Frequency - Once
label | d3d8958e-a168-52e3-b1c9-063a41bbaf4a |  | note | WP - AE Smith / LJE
label | 0c397805-b4c9-50ff-ac04-8eed95ec4183 |  | note | Hold Point - AE Smith / CPB / IR
label | ee7ced37-177d-558b-ac9d-74b381b509a9 |  | note | Records - Check Sheet + QA documents + COC
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Works Completion Test WCT 68
label | aa006489-7eb6-5f06-98fb-6b9076fd8477 |  | note | Resp. - SUP
label | 41e510d8-d8ed-5ed6-8f05-36c168d95ed0 |  | note | Referenced Documentation - Schedule 11 WCT 68 (a)
label | bf181cc0-a4e8-5b5f-9ba6-c857040ced4a |  | note | Conformance Criteria - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the – · pressure test all cold and domestic hot water pipe lines, · operation of all valves, backflow devices, pressure devices; · BMS connections to building management systems; · tank control systems testing; and · water metering testing. Independant reviewer to: (i) Attend and witness a selection of PDS commissioning at the Independent Reviewer’s discretion (Contractor to invite Independent Reviewer to all); and (ii) Receive and review
label | 9dad1392-55fe-543b-bf3b-7d41e50dfa44 |  | note | Method - DR + V
label | 6121a6ef-0fb3-52ee-89be-78c775d67785 |  | note | Frequency - Each lot
label | b9039dbd-4c5d-54a9-9f9a-75bd1ceeb84d |  | note | WP - AE Smith
label | 450b8b8c-69dc-5510-8504-8d9821fa3747 |  | note | Hold Point - AE Smith / CPB / IR
label | ba297999-8088-5ac0-bde1-990693836ffd |  | note | Records - Check Sheet QA Documents IQP certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Works Completion Test WCT 80 Potable Water storage tank and Pump
label | 7667cc4e-b894-59b5-9089-669fc69562b9 |  | note | Resp. - SUP
label | b0607850-07ba-52a9-afcc-3abd2982da63 |  | note | Referenced Documentation - Schedule 11 WCT 80
label | 8e249453-8aa5-597b-85e2-8ac39200aa1b |  | note | Conformance Criteria - Demonstrate operation of potable water storage tanks and pumps, providing onsite potable water for a minimum of 72 hours at normal demand in the event that mains water supply to the site is compromised. Activate emergency supply remotely with the BMS Independent Reviewer to (a) Attend and witness verification testing. (b) Receive and review documentary evidence of quantity.
label | 09dd7a34-77c4-5467-8976-aaf53b3ef5be |  | note | Method - V+M+FT
label | 5bd1a397-611a-5598-ab75-fb3bfdeb3d5c |  | note | Frequency - Once
label | 31261d8f-e28d-5c81-8e18-869c6d9aef1b |  | note | WP - AE Smith
label | aefbdabd-8b74-518d-b7bf-08ff424aea1c |  | note | Hold Point - AE Smith / CPB / IR
label | 74abf133-1c40-5f10-b9ec-e269fd7a1564 |  | note | Records - Check Sheet QA Documents
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Works Completion Test WCT 81 Tanker connection point
label | 821d1bd8-042a-5c38-8c11-e7ddbbee0a4b |  | note | Resp. - SUP
label | 20934bce-39c0-5443-963c-d53bbe38da2c |  | note | Referenced Documentation - Schedule 11 WCT 81
label | c84f47d9-97ff-5bc7-90bd-8ca2fdf1a0f2 |  | note | Conformance Criteria - Verify the tanker connection points to the potable water storage tanks are provided. Independent reviewer to visually verify
label | e0730b2b-4394-53cb-876f-6889202a380b |  | note | Method - V+M
label | 81d17050-a81b-5932-9c70-5d0d5ae8218d |  | note | Frequency - Once
label | 683d04e1-c537-5277-86ba-2eee93c364e0 |  | note | WP - AE Smith
label | c9d43442-1f93-5b08-b15a-9f4168388962 |  | note | Hold Point - AE Smith / CPB / IR
label | 614d411c-e983-5121-8375-99cf91d3c625 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Works Completion Test WCT 82 Loss of mains.
label | 8167ec07-a0c0-5f1f-944d-d7d2b21dbc71 |  | note | Resp. - SUP
label | d7aa8fd1-38ce-5a41-b495-94197d3311c7 |  | note | Referenced Documentation - Schedule 11 WCT 82
label | 32656522-2e1a-5f8f-bc6e-b0e44dc6c0f4 |  | note | Conformance Criteria - Simulate loss of mains supply by isolating the incoming mains supply. Verify The potable water pump operates to supply water in the event of loss of water supply from the site system. The test will evidence that the valve from the storage tank opens, the potable water pump starts up on generator power, and the pumps ramps up and down to maintain a pressurised potable water main to the New Waikeria Facility Site. Outlets within the New Waikeria Facility Site will be opened to simulate water consumption on the New Waikeria Facility Site. Independent reviewer to attend and witness
label | 0c74c92f-8e5a-5e50-9a25-e74a8f063708 |  | note | Method - V+M+FT
label | 23efde4b-c9ec-54fd-969c-d82d61bfda46 |  | note | Frequency - Once
label | d971affd-6967-5d9e-b0e9-22bb36a91b69 |  | note | WP - AE Smith
label | ba527f8d-cadc-5598-8f79-c64905ba815b |  | note | Hold Point - AE Smith / CPB / IR
label | f07bf638-6e45-5e84-8dff-7ad1c727aab4 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 4.1 - Testing Results
label | bd97d3e3-0766-5dda-8178-efe400b060b0 |  | note | Resp. - SUP
label | c56c73a1-136e-5a77-acda-e46ca3c7a529 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | bbeecf94-d8d8-53bc-91e4-af2cee8c457e |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | 802f6f91-9726-55f8-b1b6-09c4f48a5490 |  | note | Method - DR
label | 3ed96557-4ccc-5489-84f8-aa14ffbd64aa |  | note | Frequency - Each lot
label | ea39dc51-06a1-5b72-ad14-675c6da46070 |  | note | WP - AE Smith
label | 9d5e791a-e0ad-57dd-a641-aa58ed43314e |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Dosing system
label | 24e0a98a-0aea-567a-873a-e8a1fb315dd0 |  | note | Resp. - SUP
label | 47a52078-cf60-55de-b348-22614792b249 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 DWSNZ-2005:2018
label | c6d9df4e-5a11-5682-8580-c82b2b680444 |  | note | Conformance Criteria - Dosing testing and commissioning report shall be provided. Water testing results shall be provided
label | 5dae1f9e-434d-508a-9bd0-4c7331c705ab |  | note | Method - DR
label | 15cd0111-b3ac-514c-9ae8-b8a145dd9b0f |  | note | Frequency - Once
label | 41fb9d8e-06a8-5997-b043-bcd276231c28 |  | note | WP - AE Smith
label | df41fda0-a528-5f7b-804c-d9e4c41d0744 |  | note | Hold Point - AE Smith / CPB / IR
label | c064f686-3036-587f-9d58-111cb6931871 |  | note | Records - Check Sheet, + FTR +LTR
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.3 - DCW Pressure Pump set
label | aa956840-b499-5cd7-87a6-d309f708b2de |  | note | Resp. - SUP
label | 2d50a6b9-2b50-55cd-b189-7ba3aa6e18ce |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 02693f44-75fb-5249-b8aa-3cdebdf4a119 |  | note | Conformance Criteria - DCW Pressure pumpset testing and commissioning results shall be provided
label | ca18dd2d-f53a-5e5a-ab10-102a50d326aa |  | note | Method - DR
label | 42a4445a-7541-5379-a7a9-a3910e1e5fd3 |  | note | Frequency - Once
label | 3702ea7b-06aa-5eff-b317-1cf19907d24c |  | note | WP - AE Smith
label | 407c798a-08da-5d15-928b-d66b2da12dca |  | note | Records - Check Sheet +FTR
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.4 - Emergency water supply activation
label | 8d82624b-2f0f-5267-a7a9-5ffbaf20bbbe |  | note | Resp. - SUP
label | 3b77e290-32a2-5955-a480-e479245d8e1f |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | ee045807-04c7-5738-af23-5b4ea7ae2be6 |  | note | Conformance Criteria - Verification of emegency water supply activation
label | e2fe3f2a-93e7-5114-8d57-d0822120f569 |  | note | Method - DR
label | e12685e2-3b35-5338-8ca1-939ea992e052 |  | note | Frequency - Once
label | edf86615-0a9a-508e-8e74-e6e54ffa2d6b |  | note | WP - AE Smith / HWL
label | c50ff0c4-6865-5ffb-9e63-c5313a03cbb5 |  | note | Hold Point - CPB
label | 15efe97f-f5c4-5fd4-9769-8090985d986b |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.5 - Manual Bypass Button
label | dc30c6c2-a663-5a2f-8608-801b50c58ea0 |  | note | Resp. - SUP
label | b36195b8-7a10-5ba6-b312-1b266f888c1e |  | note | Referenced Documentation - AEC-NZT5007-TNKHSDG-1006
label | 0596fb98-464c-58c0-9420-1aa21b87c39a |  | note | Conformance Criteria - Verification of mains supply by passing treatment system by manual activation of plantroom Bypass button
label | af8aad52-a79a-5335-9655-083531a347d3 |  | note | Method - DR
label | 138f9626-c314-5777-9c1e-2e23da22419f |  | note | Frequency - Once
label | bb7720d4-d82c-5d81-83ca-2e0559476023 |  | note | WP - AE Smith
label | c2d33cd6-e4d9-5ad9-89ab-a624b8490b35 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 4.6 - Backflow Preventors
label | 570d8640-c110-52ea-b25a-17953a471309 |  | note | Resp. - SUP
label | bea5bbf9-4a62-5ff3-a6ad-797886e38edb |  | note | Referenced Documentation - AS/NZS 3500.1:2018
label | e41f839c-6ebd-5c6c-8cd7-2457dbeebadb |  | note | Conformance Criteria - Backflow testing
label | 9378016d-69b9-5ce9-9749-c28873fbb61c |  | note | Method - FT
label | cc8f6c54-6ca8-50cb-a32a-a14e56d88600 |  | note | Frequency - Once
label | a50e9fde-5c61-55de-8663-03b3e17299d8 |  | note | WP - AE Smith
label | 503dff1d-c2fa-5c6c-b294-8849b21642f6 |  | note | Records - Check Sheet + IQP Test report / Certificate
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | 2805964d-0a41-4fd3-b4c8-60fcf2eedf6a
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | eac81f01-caa9-51e0-8a52-2f4e60e7f83e |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | 680b52d8-9ab3-53ca-b619-c0746094d77a |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 2d3dea53-c2be-5ae8-8e6f-2b7a52802c9b |  | note | • Specifications & QA Documents Approved
label | f58a724f-a6d0-5c9f-8b06-909b8258afd2 |  | note | • Drawings are confirmed
label | 9a5a8d10-3c45-516d-b23a-e513bb992e9c |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Confirm Flushing & Disinfection of Pipework - CPB Hold Point
label | a902fb7a-36b5-560b-b037-5c03cc7f7b22 |  | note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
label | 213cdc24-3746-57d2-b7ee-7cdac532f6d3 |  | note | 2. Ensure system sterilization completed.
label | 9cfbb5ae-696c-59e7-90f5-189278751158 |  | note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
label | 8cd7eef6-f3ed-5e3d-b471-4f5a3e83c3f5 |  | note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | f2320319-13d4-5366-aa41-6eaed3873ba6 |  | note | CRITERIA - 5. Check pump is rated for pressure test
label | f1a01ce9-ed3f-5239-8372-4babd6be1ade |  | note | 6. Check all supplied attachments are correct and in good order
label | aadb637f-cfb6-5628-8e2a-e3b6763c70f9 |  | note | 7. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Isolate: Mains water Storage Tanks
label | 90712620-c4cf-5b3d-8357-5dc88f07a5cf |  | note | CRITERIA - 1. Check Mains water is isolated
label | 47d64684-244f-58c6-b89d-99c7fe9ef523 |  | note | 2. Check Storage Tank is isolated
label | 4dad3f40-4f0d-588e-889e-13000a5ec0f7 |  | note | 3. Check Filters are isolated (10 Bar max rated)
checkpoint-status |  |  | checkpoint | Connect pump to pipework under test
label | 913850fb-5ad7-57b7-8109-f24bffa09b67 |  | note | CRITERIA - Confirm connections are safe and correct, Supervisor to confirm section under test is correct and all other parts of the system not under test correctly isolated
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | 72ef329a-7428-5b9a-aa6c-86b0ca42a5f2 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill DWC ring mains with domestic water
label | b51c3c62-5076-5efb-a440-fde0c0304270 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 1550kPa
label | 5c035ba2-9535-59d9-ad73-8e4f877f8713 |  | note | CRITERIA - Slowly raise system pressure to 1550kPa
label | 8d1bb29d-a4e7-5247-aaf5-ae30223857fd |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 1550kPa pressure (START WITNESSED) - CPB/IR Hold Point
label | 4d680095-e780-5c32-bc4a-c70a76dbe64a |  | note | CRITERIA - Record START time & photograph gauge
label | bdc76a08-a37f-5c3d-8d3c-19b3c275ccc5 |  | note | • All relevant parties to witness starting pressure of 1550kPa
label | e996bf8d-b300-551a-99fc-ebce6e747119 |  | note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint-status |  |  | checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED) - CPB/IR Hold Point
label | 4279b9e1-ba5d-50fb-bb84-3672846cbbb9 |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 89f5180e-5a01-5e96-ab1e-0a916bad4c4b |  | note | • All relevant parties to witness pressure of 1550kPa
label | 020266fc-e59e-5c7e-963a-f5f35f17015e |  | note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | a3bb0505-c608-5676-b0bd-44053c39654e |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | 278c780d-8b5b-5f04-9621-d5a398fa8530 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB Hold Point
label | e7afbd8f-0010-5643-9141-706e69fb68a1 |  | note | CRITERIA - All pipework pressure test reports shall be provided
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 68 - CPB/IR Hold Point
label | a9c3bbbc-f229-5828-a6ac-180d73e82183 |  | note | CRITERIA - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the pressure test all cold and domestic hot water pipe lines
checklist-flat | dcc0a0e2-a987-41a2-9a49-4b9a0a8291ce |  | checklist | Fibre Optic Reticulation Installation |  |  |  |  | Yes | Fibre Optic Reticulation Installation | 2c32f8cc-2882-44eb-8cdf-a7ec59427214
checkpoint-no-status | ea50c611-3d22-4df9-98d0-e5e26bed6a6a |  | checkpoint | MATERIAL COMPLIANCE
checkpoint-status | f60b36e6-f3ef-4c26-b537-827530a9dd30 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | aac2beb8-9302-4d91-9d6a-51e8652e2380 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-no-status | 773c1393-66c7-48dd-a4ae-e7c78fcbcc79 |  | checkpoint | PRE-COMMENCEMENT CHECKS FIBRE OPTIC RETICULATION INSTALLATION
checkpoint-status | 75196549-6658-4d95-87c0-43001170e10b |  | checkpoint | Installation of Conduits and Micro Ducts by AE Smith.
label | 6e3306ca-f6ad-5ae9-a831-09f28e1f9b72 |  | note | AE Smith to install conduits and micro ducts as per their Approved Inspection and Test Plan -.AES-NZ1005-STE-ITP-PMT-0008
holdpoint | 8333e03b-d08b-4806-825e-cb4a7892333d |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 5d7344ba-a806-43de-b5d0-2ba949bf2e48 |  | checkpoint | Location of Fibre Optics Cabling.
label | 1baf003b-c93e-52d7-a80b-b6f534506790 |  | note | Shall be as shown on IFC drawings.
checkpoint-no-status | 9965c21f-8110-4ec5-bf55-7525cdeb1630 |  | checkpoint | FIBRE CABLING AND OFDF INSTALLATION
checkpoint-status | 3b23a8ca-68e7-4b56-b5db-b9051b7ee555 |  | checkpoint | Cable run within buildings
label | c55a07df-10c0-5288-8858-c59003c81dba |  | note | Any cable or micro duct entering further than 10m must be fire retardant cable or converted to fire retardant within 10m.
label | 823f2770-707e-5b92-bdff-24e70ea8d4f7 |  | note | Cable or micro duct 100% supported using approved cable trays.
label | 91865c6d-3116-5130-9bf7-e4f664358b07 |  | note | Cable tied at 500mm intervals
label | 4c5cd313-a3dd-5966-8ce9-7db1e6beb793 |  | note | Warning labels added to fibre to distinguish them from other cables.
checkpoint-status | 1df69611-f89a-4812-a9aa-e36ec6a34713 |  | checkpoint | OFDF's installed (Termination points)
label | f3675da5-600f-5ba6-9973-c84eec8b735d |  | note | Appropriate sized OFDF installed.
label | daeb8d07-4a47-5f7a-8280-4fd734a03253 |  | note | OFDF positioned correctly and secured.
checkpoint-status | abb1528e-4092-4fc9-b42b-017ca770e6e5 |  | checkpoint | Jointing OFDF
label | dbc5f5a3-deaa-5748-b608-65f1fd920f9c |  | note | OFDF's installed
label | 7605e56a-122d-5f9c-ab32-4f74e0f3c0ee |  | note | Fibre lay up and splicing done in accordance with the OFDF manufacturer's specification.
label | f8bdf53f-0af1-5783-a0df-1f5156e19f9c |  | note | OFDF labeling complete.
checkpoint-no-status | 1dff87ef-a938-4ebf-ad55-f566ac4ea6e2 |  | checkpoint | Cable Joining - Fibre
checkpoint-status | 5ce4d746-190e-48ca-a81c-82187a1ab149 |  | checkpoint | Splicing Equipment
label | c996a1d8-0d3b-5185-a887-c045cbff258f |  | note | Record the machine ID in the space provided below.
text | b06a2bc2-6467-5e7c-bc49-91ab06d84046 |  | textbox | Fusion Splicer ID
text | 16097a93-6f39-54e8-a1c6-efa5385d5df9 |  | textbox | Serial No
checkpoint-status | daabd0b5-71cd-42c8-993a-aed1be72be51 |  | checkpoint | Fibre Splicing
label | 0885698e-5033-5c5a-82ca-edef32636872 |  | note | Verify that all fusion splices are heat shrink protected and placed on splice tray and spare fibre managed.
label | a8af401b-d978-5a78-a8eb-07a3bba2a15a |  | note | Bend radius rules applied.
label | 255686d2-080d-5cea-b9c5-0bc329e9afa5 |  | note | Splices stored on trays according to the designer specification.
label | 9ab2356f-093e-50cd-814f-7f23d641cf30 |  | note | Set up and installation of closure as per the system manufacturers specification.
checkpoint-status | c6459e6e-5377-4db0-b549-455af848e744 |  | checkpoint | Labelling
label | 5bb71c4c-1d47-5ed8-9a34-cb8c9cf98d8b |  | note | Verify all trays, fibres, cables, micro ducts and closures are clearly and appropriately labelled.
holdpoint | 151961bd-e4ff-43f3-9410-734c6d8fad98 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 5bea73b8-8b7b-4a6d-b7b1-16c0d423928a |  | checkpoint | Confirm performance of splice before commissioning the new network.
label | 0aac8a3d-5c00-5c19-903a-3898ba49321b |  | note | All fibres terminated at OFDF must be tested for continuity with visual light source.
label | a3e04ba3-4464-540e-8deb-470125d78ccf |  | note | Use power meter and light source at 1310um or 1625um to verify fibre loss
label | 321845c2-844b-5ef6-9b9d-474c17d96fee |  | note | Record all loss per fibre from point to point.
label | 372710e5-56b3-5b1b-88d9-a1a70ae82bc0 |  | note | Where length restraints exist, suitable sized launch and trial reference leads are used to overcome any length constraints while testing
label | 63af48d9-7b42-5d22-ab37-dce171591533 |  | note | OTDR testing completed to identify any irregularities in the fibre which may not be evident on the LSPM test results.
holdpoint | b4c483bb-25bc-435f-be6c-95a8dc1f9152 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | cb34bf14-2e41-472f-b75d-15195f10949f |  | checkpoint | Confirm compliance with the correct Manhole Management Practices.
label | fc15c8a3-f68d-554f-b68b-3f07be0493bb |  | note | Verify the minimum bending radius has not been exceeded within the manhole.
label | 3a795527-2047-5000-90a0-e21df78558c0 |  | note | Joint secured in position that does not obstruct or be affected by future development
label | fc0ce418-cd40-5bb7-8e13-b9c4f4525156 |  | note | Loop of spare cable stored against manhole wall
label | ed024292-d449-54e7-9d63-0e9ddc756628 |  | note | Stored within suitable cable management bracket.
label | 31bbe5ce-6704-5d80-a3b6-989c50e217c0 |  | note | Cable is able to be pulled back down duct in case of a dig up or earthquake.
holdpoint | 5f34810c-6840-4ede-a3ac-25c459aa7789 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 1750a1df-e2cc-4a20-8749-7ce8409e9f81 |  | checkpoint | Confirm correct closure used.
label | f91a7c7b-5cda-51ad-8b1e-4b168ed92d39 |  | note | Verify closure correct for the joint.
checkpoint-status | cafb8fb3-3361-470c-945b-e1ca099fee01 |  | checkpoint | Confirm building entry sealing meets requirements.
label | a43d00e5-c234-5df7-986e-18ee77eda76e |  | note | Verify sealing meets specified requirements
checkpoint-status | 3043761f-aece-4f5c-85ce-40ac02098064 |  | checkpoint | As-Builts Completed.
holdpoint | 0c4df8a8-6a6b-49d5-8519-0a5fb047b29d |  | signoff | Request Sign Off/ Raise Remedial
checklist-flat | 4e9aad78-5be8-4776-b777-04065c0c85f7 |  | checklist | Site Installation Checklist |  |  |  |  | Yes | Site Installation Checklist | 2fe078a4-a810-4b58-a714-b804d8b2ea3e
checkpoint-status | fb85a259-ab1a-4796-bcb5-24353d72f4af |  | checkpoint | No Signs of damage or missing parts on delivery
checkpoint-status | f60e4918-cab3-4e25-a2dd-8d2c061659b7 |  | checkpoint | Riser Type identified & mounting location marked out correctly
checkpoint-status | f73f9025-c4a3-44ee-88b1-a094db337c5d |  | checkpoint | Correct lead length for location and riser type
checkpoint-status | f3f23ef4-fb7d-4c8d-b270-e05b1204c72b |  | checkpoint | Installed level and all 4 bolts secure
checkpoint-status | bd5a2aa5-8222-4125-86aa-c54c164aa83a |  | checkpoint | Insulation cut outs replaced and secured with silver tape
checkpoint-status | 24d56b4a-e8c6-4d47-aa2d-d6438f5be1c7 |  | checkpoint | Site location recorded
checklist-flat | 6652d6e4-22a6-44dd-89b7-d9fad6a9cbf7 |  | checklist | Electrical and Communications Conduit Trench Riser Installation checklist |  |  |  |  | Yes | Electrical and Communications Conduit Trench Riser Installation checklist | 361f1b9f-66ee-4838-867f-e932b5a66fb7
checkpoint-status | bb6a80f2-e56b-42fe-91b4-c3c48af7640f |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | d344d940-9c45-4416-8d0d-709cd2e09d24 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b1c2655c-59f2-4b9d-aa70-f02d8956f8df |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | af235ead-2c4f-498a-9467-7806fd4c8469 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | 3b54bd5e-1b9d-40cc-8133-7a9cdae089d9 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | bf2ffa7e-f109-47b4-bf39-a9e6a4102ccf |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | dbdcf3a6-e1a8-48b3-80f7-022be8bc2258 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | e2b8b3af-7c7d-439c-81cc-ffa9d765f60c |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 18acff54-f214-40d7-8f3f-6605891d1785 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 8c57b926-1fe7-4512-9631-1b5495a5183a |  | checkpoint | As-built drawings completed.
holdpoint | 3522a344-b88d-4993-9a37-38f6669926a3 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 89983eeb-40b8-4d9a-846b-86db75106d69 |  | checklist | Document: |  |  |  |  | Yes | Project Documentation | 39a14167-4ddb-4a2f-9155-27e491efa078
checkpoint-no-status | 78d25478-5723-4f8e-b4d8-3b7b8d9a0cd0 |  | checkpoint | Document Attached
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | 45a5082c-ffa8-445d-9aa6-b205ae90f872
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | 117171df-867b-5739-b085-08665a2873a3 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | 7d897a8a-aa3d-5742-b49f-8adef11b543c |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 303a2161-e9c2-5a9f-9bab-204cda85088b |  | note | • Specifications & QA Documents Approved
label | 5049aaea-8f3c-58e7-a03d-05a76bdf5c02 |  | note | • Drawings are confirmed
label | 260f7e87-b623-5d02-8ae9-1234b4e33a59 |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | 01853570-4b2f-56f8-9c77-c922acaec71b |  | note | CRITERIA - 1. Check pump is rated for pressure test
label | 05d021ec-2d86-575e-b2aa-29d17f055bf0 |  | note | 2. Check all supplied attachments are correct and in good order
label | 30035b62-fc7d-550c-923b-494f3247e412 |  | note | 3. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Connect pump to Fire ring mains
label | 89d9d2cc-d988-5a48-ae32-7949fee9f9b0 |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | 19ef48b6-87ac-597e-8055-cd7202a3aa81 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill Fire ring mains with domestic water
label | f518cc23-76db-59c2-a496-f78a3572d13f |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Valves at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 15.5 Bar
label | 8f271fff-5cc9-506e-9403-7f718224b0b7 |  | note | CRITERIA - Slowly raise system pressure to 15.5 Bar
label | 4874e0dc-8235-5a5a-92eb-cda77514ff5d |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED) - CPB/IR Hold Point
label | 4e5a1e93-1b52-5474-b3c3-cb9ce17107f8 |  | note | CRITERIA - Record START time & photograph gauge
label | 43c10615-295a-5710-b3f5-2e77a0c70f09 |  | note | • All relevant parties to witness starting pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED) - CPB/IR Hold Point
label | d40b3f5a-b86b-5531-9c2c-eb8c32896b6c |  | note | CRITERIA - Record FINISH time & photograph gauge
label | c6bbf5f4-6d66-5c02-8dbc-6ec176747512 |  | note | • All relevant parties to witness pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | 5b28f022-2b33-5d4d-8112-6b56c50d1234 |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | 243fce0f-dfe3-5c5a-bea9-ce3267d9b501 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB/IR Hold Point
label | b3c9ee0e-87b2-5bfd-b4ba-8815475d8214 |  | note | CRITERIA - All pipework pressure test reports shall be provided
checklist-flat | 2baeceb8-38d8-4273-93a3-5e95292911a0 |  | checklist | Pressure Test Report QCC-01.01 |  |  |  |  | Yes | Pressure Test Report QCC-01.01 | 47e74aba-1a0a-48ca-bcd5-30013cba44bf
checkpoint-status | ea703a41-ec2f-42c2-b741-d07e7c401b23 |  | checkpoint | Details of pressure test
text | 125a1f58-fb93-4fca-b207-81062af299ba |  | textbox | System Name/No.
text | 42b4109d-b3ba-450d-a96a-9217ffe123f7 |  | textbox | Location / Drawing No.
text | ddddbb20-aebf-4150-af44-058724908df6 |  | textbox | Test Instrument & Serial Number.
text | 1ffb4b68-825a-4ff9-a9c6-87fa9700d497 |  | textbox | Normal Working Pressure
text | 22d523d8-c31a-4752-ba5d-2a1ebce470fe |  | textbox | Start test ambient temperature
text | c20847d5-6182-4dec-9899-d1888d45e3d4 |  | textbox | Start test date
text | 31e3a80b-edab-4454-bb5f-ac357745cc76 |  | textbox | Start test time
text | 917ef879-4510-4dcc-a2c1-691a80ea5c5f |  | textbox | Start test pressure
text | dd5b4735-e182-4d04-841c-f425c1267348 |  | textbox | Finish test ambient temperature
text | 2c810d16-e75f-4644-99cc-359aa4d8a695 |  | textbox | Finish test date
text | b675deb2-9fad-453e-be71-589c96095ef0 |  | textbox | Finish test time
text | 4e71ffa8-f76f-4832-8216-a4f15f2ff734 |  | textbox | Finish test pressure
text | cbeee8b8-03d5-46b6-a5ea-8522baa6875f |  | textbox | Corrected pressure at test completion
label | 7990a0c7-14a7-4f43-b773-fb56a6ae93c1 |  | note | Attach photos of the gauges as required
label | 6059a464-043f-4bd0-8b04-c2f8cbad5042 |  | note | FORMULA :
label | 71330246-4fe0-4294-921b-beb085d495cb |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 1a04a208-c0e5-4d52-ad08-4300aed9e545 |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | 9f8ea800-f4bb-49af-a8b5-389758071961 |  | note | Pc = kPa
label | 57105522-72b0-4769-8f26-25359e8f238e |  | note | WHERE:-
label | 26a80af3-2173-40a6-9868-00ed118f3db0 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | ed49c168-0d5b-4b0f-a64e-e31771f502a8 |  | note | Pc = CORRECTED PRESSURE
label | 241239a4-61f2-4368-98de-7a04516ebd82 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 8e6e5ef8-edf4-47ec-9cd1-094d5e762d8d |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-flat | dc5debdb-78dd-41df-9d0d-7175d51df667 |  | checklist | Trench Pipe Riser Installation Checklist |  |  |  |  | Yes | Trench Pipe Riser Installation Checklist | 49ab133b-deac-4693-89d0-576f5af3330c
checkpoint-status | 202c1457-00e8-45cc-a9b0-96400a8f8c13 |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status | 7daeeea3-35bf-4161-8815-2566626375ba |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | a5e9b983-bfa3-4fc2-adb2-24dbab8c0672 |  | checkpoint | Confirm trench depth, width and pipe alignment.
checkpoint-status | 2e7a780f-196b-4d1b-a6e0-a1c448c36e7c |  | checkpoint | All pipe flanges are capped, and ball valve installed on pipe ends exiting the trench.
checkpoint-status | 775b3bbe-579b-4041-aa6e-77949cffe878 |  | checkpoint | Each pipe shall be pressure tested prior to installation , Refer to separate pressure test report QCC-01.01
checkpoint-status | 3af545b2-1344-450d-a87c-ce6dd3dfc5f3 |  | checkpoint | 100Kpa of air to remain in pipework to verify no leakage, Refer to separate pressure test report QCC-01.01
checkpoint-status | 8d53cfa0-a2bd-41e4-98cb-e5090f5126fe |  | checkpoint | Number of pipework dimensions shall be shown on drawings.
checkpoint-status | 0f01edef-aad1-4f6a-ba4b-c885a1a8fb93 |  | checkpoint | Location of pipework shall be shown on the drawings.
checkpoint-status | 151b52dd-ba2d-4afb-a04a-cc4aac9b792d |  | checkpoint | Pipework exiting the trench shall conform to the location and dimensions shown on construction drawings and specification.
checkpoint-status | 79d455d7-8c87-49f3-a4b6-389e05da6bf9 |  | checkpoint | Before backfilling inspect all installed pipework and insulation for damage
checkpoint-status | 22c2ead9-6a8c-4fe6-98ef-c247518d52cd |  | checkpoint | Pipework pressure to be verified of no pressure drop prior to connecting to mains pipework
checkpoint-status | d2b04c28-bef1-4754-a1e2-e973211527db |  | checkpoint | As-Builts Completed.
holdpoint | 73c83ccf-d94e-4b6a-aa1e-0e83384c3ca8 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | f2e77ba9-9df5-4f06-9cde-29d9bd27df26 |  | checklist | Natural Gas Purging with Inert Gas (Nitrogen) |  |  |  |  | Yes | Natural Gas Purging with Inert Gas (Nitrogen) | 4da0844f-58b1-4b88-bda5-74d37d0bc073
checkpoint-status | f82ef6ab-f070-4df4-a9d9-2ee3920b08a6 |  | checkpoint | Ensure gastight pressure test has been completed.
checkpoint-status | 41aa16d1-a715-47af-b392-9437461c292a |  | checkpoint | Confirmation that the line has been purged by an inert gas prior to fuel gas.
checkpoint-status | 937ce676-1606-4749-b99e-ae49843066b0 |  | checkpoint | Set up purge point at the valve train
checkpoint-status | 80503391-46c6-4ae3-89be-61ef8a49a391 |  | checkpoint | QA Documentation received from CPB/subcontractor for UT1 prior to purging
checkpoint-status | 9eb9396c-fdc7-4989-9742-e38606150f31 |  | checkpoint | Confirm subcontractor in UT1 has disconnected all appliances and caped all open ends.
checkpoint-status | 80eefac9-41d0-4121-9a49-32b5bdc47826 |  | checkpoint | Confirm valve installed on purge discharge outlet in case of quick shut off is required.
checkpoint-status | 2ca3bcec-7bc5-4627-82ff-02ba4cfd0d7a |  | checkpoint | Confirm purge outlet is open to atmosphere and is 6 meters away from the opening into a building.
checkpoint-status | 6b5f048e-2b76-483d-bee8-61538e190de6 |  | checkpoint | 50-meter diameter barricade is erected to maintain a controlled area around the purge point.
checkpoint-status | 3551723f-5ffa-4c3f-8324-88f5415286f7 |  | checkpoint | Senit gold meter located at the discharge outlet location.
checkpoint-no-status | e7d4607f-934b-4cc4-8896-5268654df900 |  | checkpoint | Purge Details
select | ef30e90e-754a-5e7c-bfab-bdeeb18ae09a |  | dropdown | PURGE SEQUENCE | 1, 2, 3, 4, 5, 6, 7
select | 94bd825b-b6dc-54af-a348-f4347b0750c3 |  | dropdown | Open Building Trench Riser Valve | UT1 , FM1, SPO, KIT, LAU, IND, FM3
checkpoint-no-status | c9c373a8-81b6-4248-a79b-716257599e4a |  | checkpoint | THE FOLLOWING TRENCH RISER VALVES ARE CLOSED
boolean | 0d814f1d-ca52-521b-bff4-dd4b23569904 |  | tickbox | Building Trench Riser Valve UT1
boolean | 68f58327-6e21-570d-894b-c50766914335 |  | tickbox | Building Trench Riser Valve FM1
boolean | e2958f3f-6c73-5529-a8bc-5605f6f802d4 |  | tickbox | Building Trench Riser Valve SPO
boolean | ff15c3f8-cc88-5928-bae9-4686a69dd97a |  | tickbox | Building Trench Riser Valve KIT
boolean | 1014cc37-82c8-5708-82a1-94373451a6e2 |  | tickbox | Building Trench Riser Valve LAU
boolean | 007f846c-6057-513e-b161-d6cbb0621eb3 |  | tickbox | Building Trench Riser Valve IND
boolean | 67f40719-1c23-57ef-b94b-3362f56d0a8d |  | tickbox | Building Trench Riser Valve FM3
checkpoint-status | 01778f42-b03a-4aff-8abd-31e70a0ea215 |  | checkpoint | Open supply valve and commence purge
text | eba3f24a-7ff9-5d1b-a8bd-0045c1616ed3 |  | textbox | Record purge start time | hours:mins
text | b12aafbd-20ec-5e6c-9d96-4511c4a43978 |  | textbox | Record purge finish time when gas purge reads zero | hours:mins
checkpoint-status | 72d798f6-1c00-44b1-8f7f-3c6cbf0e3147 |  | checkpoint | Isolate supply on completion of purge
holdpoint | 74924317-b654-4d38-824b-fa14e7f1ff02 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 68c8296b-1494-4c30-991b-785b37ce0b40 |  | checklist | Project Details |  |  |  |  | Yes | Project Details | 51f170ee-0a3a-41ea-bf26-683743dc17d2
checkpoint-status | 08b8e56a-f13a-4198-99cc-0515de89b333 |  | checkpoint | Project Information
text | b6deda1f-d359-47ad-8507-719dc8afe130 |  | textbox | Project Name:
text | 2c5f2213-0e59-43bb-8f75-04b868c594a1 |  | textbox | Project Address:
text | bb311aed-d63c-427b-9031-081bb148d86b |  | textbox | AE Smith Site Manager:
text | 3ed7586f-75c1-49e4-82a2-88dd04bbeecb |  | textbox | Consultant:
text | 10ea1d41-1768-4262-a1aa-060af1a01618 |  | textbox | Client
checkpoint-no-status | 0d418e81-f3d0-47a5-9552-fb4b3cca3e14 |  | checkpoint | Quality Plan for the Project
checklist-flat | d7025999-b347-4424-aff0-50d8958c8c62 |  | checklist | Communications Underground Conduits Installation checklist V2 Part 2 |  |  |  |  | Yes | Communications Underground Conduits Installation checklist V2 Part 2 | 543994a0-4554-4f0d-830e-bb2ca5dd831d
checkpoint-status | 0ac2703b-76c2-4cf6-9903-02365cab7285 |  | checkpoint | Location
label | faa9a49c-ebcd-599c-aafe-bdea05d0fa39 |  | note | Shall be as shown on the drawings,
label | becae983-912f-56f9-9fd8-50f3d9d5a2c5 |  | note | Shall be as instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction.
checkpoint-status | ced213f1-e7d4-4a95-a6cd-5824d46c6d02 |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status | 9663c5c6-0509-49d6-a0a3-2afd3e9960f3 |  | checkpoint | Bedding of Conduit and Pit
label | 5a209d14-3f94-5e5b-8ca5-740e1588fe1b |  | note | Conduits and pits shall be bedded on approved bedding material.
label | cd52ec9a-d3f6-586f-87c8-98f973e4daa7 |  | note | Bedding material shall be 150mm above top of conduit
checkpoint-status | ebed115d-c43a-46c0-97a7-2127a8796dd2 |  | checkpoint | Conduit Pits
label | 70fcf8d9-e4fd-57e9-b1a0-08ab9b6faa02 |  | note | Conduit entering and exiting a pit shall conform to the locations and dimensions shown on construction drawings and specifications.
label | 643d38b1-68d2-58f5-884f-5371b2352bcf |  | note | Conduits shall protrude into pits at least 50 mm and not more than 100 mm.
label | 2ad6037f-34d2-5412-9127-e543f7c4342e |  | note | Where practicable, conduits shall enter and exit a pit at the same height and orientation.
label | 2d1a47bd-3343-5bea-a8b2-84fa9aa58935 |  | note | Sealing around conduits where they enter the pit is to be undertaken on the inside and outside of the pit.
checkpoint-status | 17a6b29e-6042-461b-9777-a00e018e14fd |  | checkpoint | Bell mouths to be installed where possible and correctly colour coded.
checklist-sectioned |  |  | checklist | Communications Underground Fiber Micro Duct |  |  |  |  | Yes | Communications Underground Fiber Micro Duct | 57ccdebe-2fd4-44f0-b4f5-4628f75f3891
checkpoint-group |  |  | section | Approval
checkpoint-status |  |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-group |  |  | section | Location
checkpoint-status |  |  | checkpoint | As shown on the drawings
checkpoint-status |  |  | checkpoint | Instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction
checkpoint-status |  |  | checkpoint | Confirm trench depth, width and micro duct alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench
checkpoint-status |  |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status |  |  | checkpoint | Number of micro duct dimensions shall be shown on drawings.
checkpoint-status |  |  | checkpoint | Location of micro shall be shown on the drawings.
checkpoint-group |  |  | section | Bedding of Microduct
checkpoint-status |  |  | checkpoint | Duct shall be bedded on approved bedding material
checkpoint-status |  |  | checkpoint | Bedding material shall be 150mm above top of duct
checkpoint-status |  |  | checkpoint | White marker tape installed with the words
checkpoint-status |  |  | checkpoint | WARNING - Communications cable buried below laid in the trench 150mm below ground level.
checkpoint-status |  |  | checkpoint | As-built drawings completed
checklist-flat | ef2c9b78-1c6d-4fa6-8494-8a3d34acbad1 |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation | 587a1ea2-2d98-4741-ba46-97a1e1066ff2
checkpoint-status | b1a4af62-9333-4280-a529-7825350fe64a |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | f5ba4de4-fc2b-425f-848e-50c68f6eafa6 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 3c37ebf1-7478-4272-ac50-916c999f0b14 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 1f5f14d0-0a46-5076-942c-70387bd78029 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 6a4a5612-500c-5daa-bd17-158ae30120b8 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 66dda95b-a0c2-480b-b08d-f6b2b72b9e26 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | a8c24b3e-58e0-422a-96b1-35c9232254ea |  | checkpoint | Location of pipe
label | 45226daf-6ddc-5f22-b9bb-9acd558e6145 |  | note | Shall be as shown on the drawings
label | a5246ab5-35fc-533a-b91d-6751d7cac815 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 407771b4-c998-4e44-8c81-6fa5d0efcd52 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | d1cdc9b0-6e1e-4915-af80-0e2a8f247346 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | f3722075-ca1e-4c00-9c18-2ab560e3d02e |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 199c706a-f340-46b6-9060-509c9f712a10 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | c85e8094-f833-4797-a369-0165404fe739 |  | checkpoint | Install valves, tees and bends
label | be38ee2f-c50f-5cd6-a263-61d2ff548f69 |  | note | Install all connections as per construction drawings
label | 854b0cf7-bceb-5a8c-bf65-f3f39f7a1bac |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | 7000a464-b8f7-44e7-ab56-bfe1c5e247a4 |  | checkpoint | Installation of ductile iron bends
label | 239721b3-cd49-5229-ad74-33b6b8f3e1fe |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | 870c7f91-0842-5318-ae66-2460a7e070f9 |  | note | Ensure correct gaskets are installed.
label | c89b836f-47cb-5356-9c6b-993f45c05393 |  | note | Washers installed on both sides of the flange.
label | 31696213-b74a-56ab-b33d-6caed3a04cbb |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 50ba9efa-0143-40a0-b7fb-23772d49d35f |  | checkpoint | Install Thrust and Anchor Blocks
label | 8d55a9f7-0068-5557-9082-1fefd9343b29 |  | note | Minimum dimensions as per IFC drawings.
label | 03ef9c7c-b704-55b1-94a2-6735ab38d270 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 98962c2f-97c6-4dd8-9289-d82f083be9a5 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | d197186e-5f6a-4ac5-98e6-9da1a5d8fef6 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 61d9d852-7ecd-5861-a244-c91d0f6396dd |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | f7077cef-3021-58ed-b88e-8fec14790ab5 |  | note | Ensure each test length is capped and ball valve installed.
label | e444efc0-92d9-5d01-bda1-d6877f023ef8 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | adc2a524-0490-549e-bf2d-5fc9217af438 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 7b5cfb5a-3e20-44fa-8397-e16bc0dff973 |  | checkpoint | Introduction of Air to 300 kPa
label | 7f2d9410-77f4-5211-b135-0ceb2a497fd4 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | f54a9352-5577-55ab-9ff9-43c105880bad |  | note | Monitor for any drop-in pressure.
label | 4126733c-45e2-5e4c-8b7b-8576d8fe8f17 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9a127470-f19d-4d84-854a-544d47b83642 |  | checkpoint | Increasing Test Pressure
label | 012fd3ad-5953-580b-b117-92a9225d48f5 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 9bce60e2-322f-4ae7-bf33-1d43167fcfbf |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 1f012bda-dc7f-49f3-bead-30c191a85678 |  | checkpoint | Installation of Trace Wire
label | 5f304721-e92b-5fbd-af5a-41c3fc4507fb |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 0e802672-3652-5d6e-8f9d-3987542f091c |  | note | Test Trace Wire following installation.
checkpoint-status | e1706b07-87c1-463b-8e8a-ec10239d8048 |  | checkpoint | As-Builts Completed.
holdpoint | 54c918c7-8c76-4c87-9a13-f313df2a3332 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Flushing Preparation Checklist |  |  |  |  | Yes | Flushing - Flushing Preparation Checklist | 587dc8ad-19c4-4bba-98a9-77ba0d7a5aad
checkpoint-status |  |  | checkpoint | Differential pressure manometer
text | d78a15c7-5884-5207-8f6c-b6fea61d7f5c |  | textbox | Model Number
text | 46f3d739-bf1b-5a70-a321-b6ba30b3b565 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | HydROtwist Portable Digital PH Test Meter
checkpoint-status |  |  | checkpoint | HM Digital Hand Held TDS Temperature Water Test Meter TDS-3
checkpoint-status |  |  | checkpoint | Hm Digital Hand Held Conductivity & Temperature Meter EC-3
checkpoint-status |  |  | checkpoint | 0-14 pH test strips
checkpoint-status |  |  | checkpoint | High level 200 ppm chlorine test strips
checkpoint-status |  |  | checkpoint | Low level 4 ppm chlorine test strips
select | 37e0c501-a9e8-5708-a467-78da0dfb6031 |  | dropdown | Flushing pump | Temporary pump,system pump
checkpoint-status |  |  | checkpoint | Pump is available to run under VSD control.
checkpoint-status |  |  | checkpoint | Pump is wired and ready to be turned on.
checkpoint-status |  |  | checkpoint | Strainer basket(s) is installed with commissioning mesh. / skimmers socks installed.
checkpoint-status |  |  | checkpoint | Skimmers sock is installed on the strainers.
checkpoint-status |  |  | checkpoint | Schematic and layout drawings are available and studied.
checkpoint-status |  |  | checkpoint | Isolation valves are installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valve is installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valves are used to measure waterflows
select | 1617eb5b-9a0a-55f4-a1c0-a65edd81936c |  | dropdown | Any additional method to measure /confirm flushing waterflows. (flushing velocities) | Pump curve,Ultrasonic flow meter,Main Branch valve
checkpoint-status |  |  | checkpoint | Chemicals available on site as detailed in the
checkpoint-status |  |  | checkpoint | Piping system has been pressure tested and passed.
checkpoint-status |  |  | checkpoint | System has been installed as per drawing and schematic. If not mark-up the drawing and upload here.
checkpoint-status |  |  | checkpoint | All high points have air vents installed
checkpoint-status |  |  | checkpoint | All low points have drain cocks installed.
checkpoint-status |  |  | checkpoint | Mains water / make-up water supply pipe is connected at the suction side of the pump downstream of the drain port.
checkpoint-status |  |  | checkpoint | Mains water pipe connection size is 40 mm or bigger.
checkpoint-status |  |  | checkpoint | Mains water pressure is minimum 1.3 Bar at flow.
checkpoint-status |  |  | checkpoint | A backflow prevention valve (check valve) is installed at the mains water supply valve and it is certified.
checkpoint-status |  |  | checkpoint | A local drain is available in the vicinity of the flushing pump.
checkpoint-status |  |  | checkpoint | The drain pipe minimum 40 mm size is connected upstream of the strainer.
checkpoint-status |  |  | checkpoint | A high volume of contaminated water is to be discharged to the sewer drain. A discharge consent is not required and the discharge limits are recorded below in the note sections.
checkpoint-status |  |  | checkpoint | A special council discharge (trade waste water) consent is required and obtained. A copy of permit is attached. The discharge limits are recorded below in the note section.
checkpoint-status |  |  | checkpoint | Sensitive equipment as listed below are isolated (by-passes), and not included in the dynamic and chemical flushing processes.
checkpoint-status |  |  | checkpoint | Coils
checkpoint-status |  |  | checkpoint | Control valves
checkpoint-status |  |  | checkpoint | Heat exchangers
checkpoint-status |  |  | checkpoint | Condensers
checkpoint-status |  |  | checkpoint | Evaporators
checkpoint-status |  |  | checkpoint | Cartridges from any auto-flow control valves
checkpoint-status |  |  | checkpoint | 15 L dosing pot is installed and connected
label | 54237169-e802-5742-ae6d-84114e4c3438 |  | note | BSRIA BG 29/2012 recommends make up water quality as below. Label the sample bottle as "Make-up water sample" and date it.
checkpoint-status |  |  | checkpoint | Sulphate
label | 0ee50d5d-e740-5f1b-9625-d002bedc1029 |  | note | Recommended: <250 mg/L
text | 0b9b1998-7462-5146-bc5b-5b510fcabc23 |  | textbox | Site measurement
text | ed85cca2-3a59-5cc8-a48c-e2fa3ec0a3ca |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | 0b288bf5-2ee7-5dbe-b4c4-c7249f51dbf0 |  | note | Recommended: <250 mg/L
text | 6080c256-790c-5f8b-aaf5-07fab30cc684 |  | textbox | Site measurement
text | 89c5efe5-a5d9-5110-9806-e79d2a8a4b19 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | e0e72b3c-4969-526b-af83-4ef2308b1d43 |  | note | Recommended: 6.0 < x < 8.5
text | b9ce3535-92c3-523a-b6ab-48beb89eafab |  | textbox | Site measurement
text | 6ecff556-1dff-5317-b07e-85f308bee376 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 0377c8a3-4882-5b94-a1fd-d2253175f935 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 026eda17-eae4-5819-a142-020dce10e8b0 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | e8068557-0a53-5205-8d00-75b6aad00c30 |  | note | Recommended: <10000 per ml
text | ecd42f82-30f9-5e44-bd47-7dd5ae2174db |  | textbox | Site measurement
text | e739b723-a43c-50c6-bcb1-bb8cdc4a4182 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | 38b2b70d-e745-5a5c-ad31-26c07e1ad82c |  | note | Recommended: <10 per ml
text | eab1c891-0601-5f89-8304-47594c0024a0 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | System filled with make-up water
checkpoint-status |  |  | checkpoint | Date
checkpoint-status |  |  | checkpoint | Make-up water connection location
checkpoint-status |  |  | checkpoint | Mains water pressure (kPa)
checkpoint-status |  |  | checkpoint | Water drained from furthest terminal until clear water is visible.
text | 1766140e-b890-5128-a109-20b4a850bece |  | textbox | Drain waterflow (l/s)
text | 682606e0-0e3c-5ad0-8c94-034a0fdff0f0 |  | textbox | Drain location
text | 9b36e3ec-c3d9-5510-9620-f97a527382eb |  | textbox | Drain duration (minutes)
text | 5e9a5900-bef0-5c96-8e74-a9bc609460e1 |  | textbox | Calculated drain water volume (L)
checkpoint-status |  |  | checkpoint | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Water drained from all other location same as above
checkpoint-status |  |  | checkpoint | Air vent from all high points.
checklist-sectioned |  |  | checklist | Ductwork Leakage Test Certificate |  |  |  |  | Yes | Ductwork Leakage Test Certificate | 693c4eb3-33e8-4dc7-ba24-8168993fe3eb
checkpoint-group |  |  | section | Part 1- Physical details
checkpoint-status |  |  | checkpoint | Physical details captured correctly
label | 74519125-9a2c-53d2-9ecf-0fad8269952a |  | note | The issue of this certificate is notification that this sytem has passed and ready for witnessing. Its is to be witnessed within 7 days following the test.
text | 47fee560-337e-5b98-a883-1c66b6fc2572 |  | textbox | Section of Ductwork Tested
text | a85236c1-efcb-5efb-9eb6-8fd0b519e63b |  | textbox | Test Standard, Class & Pressurisation
text | b00fec95-3338-5347-b1ae-45615a172ff9 |  | textbox | Test Static Pressure (Pa)
text | b9206adb-4790-54af-a672-98fd9e8596ac |  | textbox | Leakage Factor (l/s/m²)
text | 8ba2fb11-ef05-5082-b364-9a552292e6f3 |  | textbox | Surface area of duct under test (m²)
text | 65b9510c-a0cd-5b53-b664-29d2a3e550a9 |  | textbox | Maximum permitted leage (l/s)
checkpoint-group |  |  | section | Part 2 - Results
checkpoint-status |  |  | checkpoint | Part 2 Completed
text | e0237a89-8d60-58fd-aea0-1cc30f101e41 |  | textbox | Test Rig Details
text | c96bd1a6-ddf7-5ced-be64-cd395ec3fb75 |  | textbox | Test Instrument Manufacturer / Model
text | 78e76c2d-0548-551c-9381-d66a5f0ae03b |  | textbox | Serial number / Calibration date
text | b51f698d-d31d-50da-9051-cc9a82285065 |  | textbox | Actual Duct Static Pressure (Pa)
text | 6173e1b8-c587-5e21-8bae-10b5a9283b66 |  | textbox | Actual Airflow Leakage Rate (l/s)
text | 33120d9b-3e1f-5c11-927c-29ad66bcd36b |  | textbox | Calculated Leakage rate per m2 (l/s/m²)
text | 62aa7527-c858-5794-8999-6d5554e684f7 |  | textbox | Duration of test ( Airflow reading taken at end of test duration )
text | 5feceffa-ec2e-548a-855e-190a79bcefa1 |  | textbox | Test Outcome
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | d65c15db-1b62-549b-8345-6a3e615aca24 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | cfbd47b5-a220-5001-ab01-bd89d19e1785 |  | textbox | Consultant Name
checkpoint-group |  |  | section | Photos
checkpoint-status |  |  | checkpoint | Start of Pressure test
checkpoint-status |  |  | checkpoint | Pressure test after recorded Duration
checkpoint-status |  |  | checkpoint | Photos Attached
checklist-flat |  |  | checklist | B7A - Functional Tests of Terminal Units |  |  |  |  | Yes | B7A - Functional Tests of Terminal Units | 6954d0f3-a33d-4270-9d8b-4152d7e6a836
checkpoint-status |  |  | checkpoint | B7A - Functional Tests of Terminal Units complete
text | aaafa945-726b-5edb-bf83-42fb99736a72 |  | textbox | Plant ref
text | c585a2b3-6038-54af-8d7d-c52d1c477671 |  | textbox | Test by
text | ef465852-7c18-5c42-b489-bd67262b4785 |  | textbox | Test date
text | a6db3e94-f66c-53fb-98d4-c0f20df622b0 |  | textbox | Revision
text | cf0a14d6-5797-528b-83de-189f9682e48d |  | textbox | System
text | b9e01729-4aec-5162-8b48-abddb774f28d |  | textbox | Specified flow (L/min)
text | 7ab4f3d6-2808-5371-8a1d-d75fb1b6e42b |  | textbox | Specified pressure drop (kPa)
checkpoint-status |  |  | checkpoint | In accordance with the contract specification and paragraphs 15.77–15.78
text | 4b7221f0-bdfa-5c77-b675-b878c5c84be8 |  | textbox | Terminal unit number
text | 3de2c38d-ead8-57c0-845f-5b66511ee592 |  | textbox | Room number
checkpoint-status |  |  | checkpoint | Specified flow achieved
boolean | df4a31a9-3b21-531a-b8b0-7aafd3e4422f |  | tickbox | Yes
boolean | b653e85c-9970-571b-9f44-fce4ff57c35f |  | tickbox | No
checkpoint-status |  |  | checkpoint | Specified pressure drop achieved
boolean | 3179e0a1-32fc-541d-89c7-8b66e9563bdb |  | tickbox | Yes
boolean | 11cf11eb-67b5-53f7-8f66-1ba3eea34e22 |  | tickbox | No
text | 2d07dd87-a322-5983-8739-36f4538a6763 |  | textbox | Mechanical function
text | c573a49d-fa41-52ed-986a-a80b60d8b8d0 |  | textbox | Gas specificity
checklist-flat | 99f5d901-3292-48d8-b342-072109d7b27c |  | checklist | Supply and Mount Warden Controlled TMV Valve Sets |  |  |  |  | Yes | Supply and Mount Warden Controlled TMV Valve Sets | 6af321dc-114c-4c76-9073-ace93e39b44f
checkpoint-status | d41c6f6a-f7ca-4c52-a55c-0b0b6587c273 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 47d7527a-7949-4c40-8cdc-cc083abc21d3 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 54fafb86-9824-41bc-a3b7-8aa735ca133b |  | checkpoint | TMV's installaed in correct location
checkpoint-status | 266c62ff-1936-4dd6-802f-91f5ac2adb69 |  | checkpoint | Letter of compliance issued for each TMV valve box
checkpoint-status | 74c6d0df-ba64-47db-96f3-ad01dd2f263c |  | checkpoint | Pressure test report completed and issued for each installed TMV Valve Box.
holdpoint | 35e34662-3cb1-4993-b25f-699ee53e4786 |  | signoff | Sign off by Inspecting Supervisor
checklist-flat | 1ff1eda9-e246-49ea-a63d-3f7a003a5cf1 |  | checklist | Electrofusion Welding |  |  |  |  | Yes | Electrofusion Welding | 6b0cfc5b-b66e-45a0-ae14-fe2b4b35c3ac
checkpoint-status | d12c9200-3934-4fd5-affd-13103cb9a054 |  | checkpoint | Welding details
select | e77830ce-f45a-55a8-8a52-5f6d69e4ba95 |  | dropdown | EF Coupler completed by and recorded. | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
label | 5fd56b78-e9f7-5af6-a50a-a60b0b6e3bcb |  | note | Fusion Machine Used - SR No 402-1348 Caldertech EF welder
text | 3fa48e41-db68-52ab-81c9-804fc5e2807e |  | textbox | Record EF Coupler Used (Size)
checkpoint-status | 1b9c4532-8cf6-4ea3-8480-c96ebb6cfb55 |  | checkpoint | Pipe surface free from scratches, deeper than 10% of the wall thickness ?
checkpoint-status | 7858b33b-4783-4870-b4ea-aed0845ff578 |  | checkpoint | Pipe scraped and marked ?
checkpoint-status | fa06c62f-e8b1-412f-9c43-6714ed83820c |  | checkpoint | Pipe surface cleaned with Isopropyl alcohol?
checkpoint-status | e4e0cca8-6df2-4a79-b3df-d2fd3da92938 |  | checkpoint | Barcode scanned by machine?
checkpoint-status | 2973a4d7-4cbd-4427-b90d-a928bb1181f2 |  | checkpoint | Record cooling time achieved?
checkpoint-status | 053000d2-41d2-4afd-b182-92257266546c |  | checkpoint | Details of E.F Coupler Operator
select | 25ea69af-78dd-5a8e-bc52-08898dcaa0f7 |  | dropdown | Name | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
holdpoint | c555ef4d-303c-46cb-954b-57b8228b5e25 |  | signoff | Signature
checkpoint-status | c2efb854-1674-40de-9085-fa6ab7efb7f1 |  | checkpoint | Post weld checks completed
holdpoint | c62849b8-1925-4dce-a8a5-ea4583b835af |  | signoff | Post weld checks by Client and AE Smith - Request Signoff
checklist-flat | 4a52b449-b2ef-4efa-a22c-629cbfc0b075 |  | checklist | Natural Gas Gastight Air Pressure Test - Test 1 @ 105kPa |  |  |  |  | Yes | Natural Gas Gastight Air Pressure Test - Test 1 @ 105kPa | 72047f19-801d-47f6-a8ea-a16f7d9541f5
checkpoint-status | 85932b8a-13ea-4bb1-919c-75c9055bab99 |  | checkpoint | Ensure the system is disconnected at the meter or from the cylinder
checkpoint-status | 5860c311-3e59-46c9-a942-d5753d75b0c6 |  | checkpoint | Ensure all open ends are capped or plugged.
checkpoint-status | e71a8469-91bc-4d6d-8ab3-8fe1dd2ec686 |  | checkpoint | Ensure all gas appliances are isolated.
text | 95765c47-4bc5-5198-8aad-1b95cb4f442d |  | textbox | Connect a suitable test instrument. Serial No
checkpoint-status | 737a4c73-33f1-4e29-bc20-e7ec43eaf7ac |  | checkpoint | Raise pressure to 1.5 times the operating pressure to 105 kPa
checkpoint-status | a1dfea33-f26d-4b2c-8a53-f2a20f1090eb |  | checkpoint | Isolate the pressure source and allow suitable period 2 minutes for the temperature of the testing medium within the consumer piping to stabilise.
text | b1237850-eac6-57c0-9496-50e700a2ca25 |  | textbox | Measure the loss of pressure during the test period of 10 minutes
checkpoint-status | eb22352d-0d49-4168-9f13-d1a55068a4d8 |  | checkpoint | If no pressure loss during the 10 minute period the pipework can be considered gastight.
holdpoint | 13782acb-c02a-4d81-8561-619a2bf64f88 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 6dac542e-1ef7-4aa7-b92d-fefaecd2d7ff |  | checklist | HV Installation |  |  |  |  | Yes | HV Installation | 7a9e2efc-ebf5-4e42-b488-43c269367df9
checkpoint-status | 5e41a53f-fe99-4df7-b7c5-760dfd4f2cf9 |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | bee2b4c0-a3e8-4756-8d46-24fd544e6b61 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 67eada82-9f2d-5fc9-b91b-17388ec1e278 |  | note | Attach: material inspection checklist
checkpoint-status | 7313e0a9-b340-4bad-b9e3-dae22ca86a7c |  | checkpoint | Inspect trench depth, width & cable rout
label | 9ba1cc9f-ebb8-5253-be3a-e9b966a17f5e |  | note | Shall be as shown on the drawings,
label | aeec7443-74b7-542f-b2b4-5f227aa168d6 |  | note | Attach: Excavation Checklist & Photos
holdpoint | 6f927bdc-7ebc-47c8-b500-dad56bd0c3bb |  | signoff | CPB HP - Documents
checkpoint-status | 96665483-c57d-4682-a2d1-64d49a583978 |  | checkpoint | Testing of cables prior to cable pulling/laying
label | 97d7589e-fcd2-5ecf-a82f-342af82f1b8f |  | note | Drum No
label | 069d4c28-a511-5dde-b558-be8997e29dc3 |  | note | Insulation Resistance Test Result
label | 3f3542b6-327a-509b-ba53-6d2bc2a82f04 |  | note | Attach: Photos
checkpoint-status | fa200367-79ee-40f4-9680-b6e5225c8ac8 |  | checkpoint | Haulage of Cables
label | 5dc9efbe-0997-585d-89fb-65a0783b63c4 |  | note | Pre haul checks
label | 3feba2d0-6b82-5e68-81a3-6aa2e8878cc2 |  | note | Correct Lubricant
label | eb89aa77-e339-5bc4-b4d9-f569060a977d |  | note | Monitor hauling tension - Attach calibration certs
label | 72862ec1-3ec0-5d52-bc06-642caec556bf |  | note | Inspect cable sheath
label | 0038ea0b-e6de-5556-9b7a-fe95ea895b4e |  | note | Inspect sealing of cable
label | 819b5f16-2387-570a-8426-05ea54de71c0 |  | note | Cable location - Attach photos
label | 790840ba-1ad5-57d2-aaa0-3b43ed8a6684 |  | note | Record all cable distances between each cable and to fixed attributes
checkpoint-status | 1987949e-5f5e-4647-a2c3-614b31e393dc |  | checkpoint | Mechanical protection
label | 5c8d7c04-8e3a-5a70-9568-7157415a7082 |  | note | Magslab installed 75mm directly above each cable
label | e4ad5139-4615-5af2-8918-2b30bd111a68 |  | note | Attach photos
holdpoint | 9bb6b2b8-b7ad-4350-8f82-b124d41ece75 |  | signoff | CPB HP - Documents
checkpoint-status | 67b7fee2-be25-41f6-a1a0-1daec0b0c0b3 |  | checkpoint | Cable identification
label | 87bdf48f-bca4-52cf-bf73-92843786f72e |  | note | All cables shall be identified 'Critchley' K type plastic numbered markers, minimum 10mm high lettering
label | 460d0eb1-1c1b-52c4-bd00-51aca560b9bd |  | note | Attach: Photos
holdpoint | c6ec0948-e797-4342-963c-c89d3cb0b04f |  | signoff | CPB HP - Documents
checkpoint-status | fd11a5c6-e283-42bd-aeec-e57ee31dd4f4 |  | checkpoint | Installation of Marker Tape
label | 5d0bffee-67e6-5940-a0e6-5089b6075989 |  | note | Orange cable marker tape complying with AS/NZS 2648 shall be installed approx. 50% of the depth cover above the cables
label | 4bb63330-5a14-5862-8e29-188f9687c330 |  | note | Attach: Photos
holdpoint | b585d66d-fe89-4992-88f1-2459e67ec7b4 |  | signoff | CPB HP - Documents
checkpoint-status | e19359a4-c1bc-4ccc-bc33-f1572bd91855 |  | checkpoint | Cable Install Check prior to Backfill
label | 5eada082-bf69-569e-ac4b-bfa1e7e2b4b3 |  | note | CPB Engineer to complete visual inspection
holdpoint | ca2c604f-7740-4133-8757-c30ca65ed209 |  | signoff | CPB - Visual Check
checkpoint-status | 25883b6a-e754-4bd5-a767-56c320084697 |  | checkpoint | Cable Testing prior to terminating or joining
label | c8be355c-427c-5fda-97f9-2ca5ba4ab6cb |  | note | Sheath integrity test to 2kV
label | e63afd96-57d1-5643-8904-97a0f9c2a757 |  | note | Insulation resistance of Primary insulation to 5kV
label | 94b4110a-228c-5924-8dbd-d0bf2ae474c9 |  | note | Attach: Photos & Earth Installation and test record sheet
holdpoint | 7bc30a42-fd83-4203-b009-30c442d8e370 |  | signoff | CPB HP – Conqa checklist
checkpoint-status | 2b181b41-2851-46d5-994d-724a688e1e36 |  | checkpoint | Visual Inspections
label | be5334cd-3719-5929-8e7a-a4e4b52760b3 |  | note | Phase identification; Earth bonding; Terminals tight; Cable Supports
holdpoint | c1a72c6a-3028-413b-be1f-a7a161c7c20f |  | signoff | CPB - Visual Check
checkpoint-status | 21a7ca66-a425-4fd1-97c0-e1b74ce3b824 |  | checkpoint | Transformer Installation
holdpoint | d922019e-f61a-44d1-bc71-b9cc2e07db91 |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | 2394635f-0110-4b4c-a9df-94d015b29ab0 |  | checkpoint | Switchgear Installation
holdpoint | 6dbe09fd-4731-4df6-a8de-09d65f3ae778 |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | f162c8aa-b297-436f-b59f-bdc075a50da7 |  | checkpoint | HV Auditor Inspection
label | 022f4844-a401-5aea-921a-a02a54f5ae49 |  | note | Attach: written confirmation from HV auditor - electrical install has been tested, safe, in accordance with relevant standards and suitable for energisation
holdpoint | 78dfb426-f72b-4d57-8207-3ea0cc318635 |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | e3486e70-dc9a-4574-8a79-9b1d2de63911 |  | checkpoint | Cable Testing after install and prior to livening
label | 1cc947b7-dabc-550c-b731-5c361c04807f |  | note | Test: Sheath integrity 2kV; Phasing; Polarisation index; Step voltage; VLF AC HV Test; Screen resistance; main conductor resistance
holdpoint | a33d7180-4f94-4633-86df-fca54548d5dd |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | b9ebeda5-31ee-46ea-b60d-2f6cf612d7c8 |  | checkpoint | Cable resistance - Joints & Terminations
label | fdf7d3df-9c5b-513e-90ee-3aab93232967 |  | note | Perform resistance test; test points shall be identified on the test report w/ sketches
label | ed166c35-68a0-56d4-95b0-9601d6299974 |  | note | Resistance shall not be greater than 10micro-ohms
label | b60c764d-36ce-5224-949c-38b9e7ed673a |  | note | Attach: Cable test report
holdpoint | 5be1e180-bed4-4dc1-a84f-d41547afbc01 |  | signoff | CPB HP - Documents
checkpoint-status | bacbae5c-3737-4406-b144-8cbe572cd6d9 |  | checkpoint | Connection to Waipa Networks
holdpoint | 9dc66807-ae1f-4b16-bbd0-cd5434b917fa |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | 57eeb7c5-165a-4261-b3e8-a0fa71a159f4 |  | checkpoint | 11kV Cable tests after livening
holdpoint | 7e3d5842-f34e-4049-9326-6594b1d6fdf9 |  | signoff | CPB HP - Conqa Checklist
checkpoint-status | d74a6d74-ef69-4a37-9678-3b2a40e9fe41 |  | checkpoint | As-built drawings completed.
label | ff3cbfbd-1cf9-525c-bea8-0c4e8c0d641e |  | note | Attach: Asbuilt Transformer record sheet & Electrical equipment record sheet
holdpoint | 18d70359-2c71-4131-bac4-456179cc02ad | Multiple signoffs are not allowed | signoff | CPB HP– As Built Drawing
holdpoint | e6f7d57b-0e43-46bd-8ce2-1959e4b73e07 | Multiple signoffs are not allowed | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 99e32bcc-dff8-4821-bf42-1342827f4028 |  | checkpoint | ITP Sign off Witness Points
label | 9eb28e2c-5bc8-51d0-8db3-4694a584e165 |  | note | 2.1 Inspect trench, depth, width & cable route
label | c82a928c-b67c-5ac7-9247-06a165af2e4b |  | note | 2.2 Testing of cable prior to cable pulling/laying
label | c83b5b23-0621-5c5a-be89-d293d79938d7 |  | note | 3.1 Pre-haul checks
label | 8ff19c73-7b4c-57e7-89f0-4cbb8f093c37 |  | note | 3.2 Confirm correct lubricant is available for use where applicable
label | d2115b63-e91f-5f75-bdea-514fb42fb92a |  | note | 3.3 Monitor hauling tension
label | 6895eb0c-4300-5df7-bc87-832a67127485 |  | note | 3.4 Observe haul
label | ca26c625-013c-5373-a67b-3a781b449111 |  | note | 3.5 Inspect cable sheath during the haul
label | 6889ec92-df87-58f5-a99f-59b3c96d2a50 |  | note | 3.6 Inspect cable sheath at the completion haul
label | 7297a977-d653-516c-bb48-26707312491d |  | note | 3.7 Inspect the sealing of installed cable and remaining cable on cable drum
label | ef31dcb8-068e-52e5-a447-23534cfac4af |  | note | 3.8 Cable location recording
label | fc9a1063-58c3-57c5-8eef-c83911d603e2 |  | note | 4.1 Mechanical protection
label | 0d9dca5a-231c-501f-9e99-d8d9856b6ff1 |  | note | 4.2 Cable identification
label | 24dd2255-737e-588c-9066-3589f3e3dccb |  | note | 4.3 Marker tape installation
label | 6e630681-2660-552c-8480-72c8f9f9ed6d |  | note | 4.4 Cable installation inspection prior to backfilling of trench
label | b104fe15-8b59-5046-ac1f-4554cd92d4a4 |  | note | 5.1 Cable testing prior to terminating or joining
label | a87f7582-a0a7-5692-8f7e-cffe545407cc |  | note | 5.2 Visual inspections
label | 3cd9e16e-af0c-5435-b36c-86951ca89c7d |  | note | 6.1 Transformer installation
label | 10a10127-df21-5d08-bd9f-67d2b0abc164 |  | note | 7.1 Switchgear installation
label | dc121525-d2a1-5197-9f0d-b92787c90c12 |  | note | 8.1 HV auditor inspection
label | 2028fd31-9a68-56fd-9115-e7db102ac1be |  | note | 9.1 Cable testing after installation and prior to livening
label | 330a2f28-8481-546a-8d0f-9f485d02ca9d |  | note | 9.2 Contact resistance
label | 4342ff2d-aea5-5322-98bb-3e88919dbc5b |  | note | 10.1 Connection to Waipa network
label | 4cc66602-2d76-58f4-9500-5f82a5cb5953 |  | note | 11.1 11kV cable tests after livening
label | ca9042b8-cb54-5482-9bb4-90d75a5b3e85 |  | note | 12.1 Conformance records
label | 993107ae-fae3-542a-a72f-ed26bc453589 |  | note | 12.2 As built survey
label | 9661c4b8-9695-5490-b69f-52a768d47bce |  | note | 12.3 WCT 55 switchgear and transformers
holdpoint | b1697bbc-3f6c-40a8-a360-6723b2f631d9 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat |  |  | checklist | Passivisation |  |  |  |  | Yes | Flushing - Passivisation | 7faf5226-d2e4-4bf7-8d92-6e61009dc234
checkpoint-status |  |  | checkpoint | Confirmed all terminals backward & forward flushed
checkpoint-status |  |  | checkpoint | Confirmed the system water quality is as close to the make-up water quality as possible.
checkpoint-status |  |  | checkpoint | Test make-up and system water to compare
checkpoint-status |  |  | checkpoint | pH
text | 5b9ddf78-581b-56d0-9349-980e57b0bbfa |  | textbox | Make-up Water
text | 856f67d9-f3ac-5dd5-927f-4e2cc99de602 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Conductivity
text | 1c86b0c1-4ecf-531d-8a23-38f732d0574b |  | textbox | Make-up Water
text | 26626991-f2d7-53fe-9777-e17fd0d1c74d |  | textbox | System Water
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | b15e3786-b62b-5c61-bb3d-d8472955bf20 |  | textbox | Make-up Water
text | 48b9498e-52b5-5817-9677-e9c8c24889a7 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Inhibitor chemical(s) added.
text | d64ed091-cbb6-5347-aab4-47a3b8789cee |  | textbox | Enter Date & Time
text | f134581e-d43e-5316-b719-24daf3d3f6ce |  | textbox | Name of chemical and SDS
text | 74976cec-a0d0-5f59-8882-4c6a17f435fe |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Biocide chemical(s) added.
text | 4f837257-0e90-5f34-92ee-bfecddf5fa52 |  | textbox | Enter Date & Time
text | f5bb9f15-e00c-5e7d-b388-bacc0971ece1 |  | textbox | Name of chemical and SDS
text | cc0a92dc-e3d8-52ec-927b-d74825f8cea1 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
select | c41e9eb2-074b-553f-b5d5-f1234ca43a00 |  | dropdown | Is there any neutralisation chemical added as per chemical specialist advise? | Yes,No
text | 7317cae6-5685-5c5f-87fb-db31ab6dc28a |  | textbox | If Yes, enter name and quantiy
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Flushing" and dates.
text | 592714f4-f51f-59ec-aa20-c36cff8b44f5 |  | textbox | Enter Date & Time
checkpoint-status |  |  | checkpoint | Sulphate
text | fca13d38-00cf-5838-a78d-56e651b9c34f |  | textbox | Site measurement
text | 31840eb3-3037-5698-891e-42c40f7ef08d |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 9409d69a-233f-51a1-a79f-d4d68053c9ef |  | textbox | Site measurement
text | 498ebed6-0bda-540e-ae66-29d4247df14d |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 4edc80de-6e9f-5ebf-af29-674c9f988917 |  | textbox | Site measurement
text | 4a268dc3-f0fd-5dfc-91a7-7daee2c42410 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 9cfb86c1-5bed-570f-af7f-9cf6144ac70d |  | textbox | Site measurement
text | 865505ab-412b-54bb-9f32-bf7ad2c347aa |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 481d0b09-1919-5e2c-936f-08318b0a4ddc |  | textbox | Site measurement
text | 29285650-5b51-51d0-9898-5c108525dc94 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 70873845-7609-5569-a3cd-3e72716f0fcd |  | textbox | Site measurement
text | c939bed3-47eb-5cc2-899e-7b48a3c32c48 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | ce80a7dc-c388-5185-b32b-221b8a3a736d |  | textbox | Site measurement
text | 07d1def2-b03c-539a-a8e0-25f7e429b336 |  | textbox | Lab test results
checklist-flat |  |  | checklist | B5A - Area valve service units – closure and zoning test |  |  |  |  | Yes | B5A - Area valve service units – closure and zoning test | 8596ba29-3b0e-411f-91fb-e76245161c79
checkpoint-status |  |  | checkpoint | B5A - Area valve service units – closure and zoning test complete
text | cbf343bf-7b54-55c3-abf4-77c30741e79c |  | textbox | Plant ref
text | 187395ab-4a64-5c5e-8913-96e6dfafb80c |  | textbox | Test by
text | 7d5df33b-d85b-540b-b27d-d1368523fe7f |  | textbox | Test date
text | 6221eb20-e7e2-5974-bf72-b3c041fd2b30 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
text | 9ca432e3-8f25-5025-84de-70835a0633b2 |  | textbox | AVSU number
text | ca322564-1c38-5f11-b4ab-71133e0142c8 |  | textbox | Test pressure (kPa)
text | abf79417-c5a7-5a66-81ff-71fd3353c3a7 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 1f991e03-34c7-558a-afa1-47a76d88ed1a |  | textbox | Terminal units controlled (total no)
text | 45d254b6-71b7-5055-937d-3f7a86463023 |  | textbox | Terminal unit labelling
text | 3b622a7e-c412-5d4f-88cc-e119cdc6c1fa |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | ecee2237-d688-5b3d-8ffd-fa4bd2bc7d8c |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 5cf9d787-00b9-5484-84f6-4fe3b934756d |  | textbox | Consultant Name
checklist-flat | 2bc9d924-22b8-40b0-9d16-f370fccd2d86 |  | checklist | TMV Valve Box Installation |  |  |  |  | Yes | TMV Manufacture Checklist | 91090fa6-8c3a-4266-9f98-8e9cb5a9e683
checkpoint-no-status | 44187e23-183e-4cf0-a72e-a16ff136a5da |  | checkpoint | Pipework Installation
checkpoint-status | 5730dde9-a95e-40c7-9cc1-7339f90c2487 |  | checkpoint | Pipe and fittings to be kept clean and free of dirt
checkpoint-status | e0287fdc-ec31-420e-a4ac-13f84665ce49 |  | checkpoint | Cut pipe with correct wheel cutter wheel cutters used on copper pipe are NOT to be used
checkpoint-status | 3339b4ee-3406-4aed-97d5-a7518b5076aa |  | checkpoint | Ensure deburring to inside and outer edge of pipe is complete
checkpoint-status | 20b8d541-3788-4b65-8703-df48b7dfc3bc |  | checkpoint | Ensure o ring is inserted correctly and is EPDM BLACK for potable water
checkpoint-status | ea3dfbdb-40f6-45d4-8859-aabea10bfbc0 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | 7f7463b1-b027-434c-ae17-d16d49b314fb |  | checkpoint | Mark pipework depth prior to pushing into socket this will ensure that it is inserted and fully home when crimped
checkpoint-status | f7a6d8c5-9e12-4b68-8f64-dc797d5bdbcd |  | checkpoint | Crimped to be marked and initialled once complete
checkpoint-status | 94fee24a-e42b-4085-be27-7c99e9c4e613 |  | checkpoint | Solenoids are installed in the correct flow direction
checkpoint-no-status | 781358cc-2435-4919-abab-086c6fd749f4 |  | checkpoint | Electrical
checkpoint-status | 3ea9e53c-8b0e-4ffd-bd08-27b320011767 |  | checkpoint | Each Box to have a 14 metre 8 core cable
checkpoint-status | 6e1b9d82-77d0-4b50-aed2-0c1b7bb63401 |  | checkpoint | Cores 1&2 to be fitted off to Shower solenoid (left)
label | f503694c-76d2-5954-9ec5-8f8423a6a9e3 |  | note | Each connection checked for tightness
checkpoint-status | 543d775d-960a-4680-a95b-ee26ae4bc437 |  | checkpoint | Cores 3&4 to be fitted off to Tempered basin solenoid (centre)
label | 8c19da71-fd03-53a3-832c-a76b4ede508b |  | note | Each connection checked for tightness
checkpoint-status | a0fd7fc8-cd63-4324-b9af-02c134e15746 |  | checkpoint | Cores 5&6 to be fitted off to Cold water basin solenoid (right)
label | b0195085-685a-50e5-bab8-93e85bc01f47 |  | note | Each connection checked for tightness
checkpoint-no-status | 59d4d2cb-3a45-4530-86ce-9a1e038805ae |  | checkpoint | Pressure Testing and Final Checks
checkpoint-status | f59601b6-1455-4322-b892-d4ab10f900a6 |  | checkpoint | Test pipework to 525kPa for 1 hour with a certified gauge.
checkpoint-status | 8b03e58d-a2c4-4e39-856a-61496eea9c77 |  | checkpoint | All solenoids to be tested individually to open and close
checkpoint-status | b069cb8c-8343-46d0-8adf-37662354f419 |  | checkpoint | Check to see all brackets are fastened
checkpoint-status | a97b0ddc-b7b9-46f5-a43d-7fae946c97ad |  | checkpoint | Once water test is complete make sure pipe has been emptied and pipe ends covered to ensure no foreign objects get into pipe
checkpoint-status | 19b12b01-bb94-40ba-8188-7ec7c132d60f |  | checkpoint | Ensure barcode has been put on box and cover installed.
holdpoint | 156c44ea-dfcc-48ec-ba1e-cbbe7808faf7 |  | signoff | Sign off by Inspecting Supervisor.
checklist-flat | 340c1431-d816-450e-a810-341e38b6160d |  | checklist | Pressure Test Report QCC-01.01 |  |  |  |  | Yes | Pressure Test Report QCC-01.01 v2 | 9c9ed62b-9b95-4de3-aecd-af05192c69d2
checkpoint-status | a8cd117c-1cfc-41c8-93dc-cec98954ae43 |  | checkpoint | Details of pressure test
text | 8a172f39-80b5-5a59-b47f-c7a13434497a |  | textbox | System Name/No.
label | 3bd7f3e2-a24f-5d96-a9e4-6bbd0a2e1937 |  | note | Location / Drawing No.: AES-NZ1005-STE-DSH-HYD-003 - Mixing Valve Box Assembly Technical Data
label | c6c77c34-9385-52d9-8eac-676d5d7ebf40 |  | note | Test Instrument & Serial Number.: Gauge IP0612
label | 438162b6-f13c-5e13-8f47-47ca1cad72ba |  | note | Normal Working Pressure: 350kPa
text | ef59d814-894d-55e8-b8c0-e6757c6ef847 |  | textbox | Start test ambient temperature
text | cbd5d80e-d1ca-537b-bddf-9e82e6e91c55 |  | textbox | Start test date
text | a9e0e755-f079-5253-be2c-debe09809aee |  | textbox | Start test time
text | 3a5de358-eb64-51fb-8b41-e70b222a8d5a |  | textbox | Start test pressure
text | a17df4fd-23b2-580c-9638-a7373b4bd170 |  | textbox | Finish test ambient temperature
text | 1c5c8505-3c0f-58c2-8039-ce63221a8ae1 |  | textbox | Finish test date
text | 2e9bed65-9b20-5a42-86d1-5e4fc8821e6e |  | textbox | Finish test time
text | 4018e322-351f-52de-825a-ed4d7dd8c3a3 |  | textbox | Finish test pressure
text | 32b599d0-c5b3-5955-bf30-58eddd764c48 |  | textbox | Corrected pressure at test completion
label | 53984ced-de6e-5100-be8d-d5a6a58b8851 |  | note | Attach photos of the gauges as required
label | c94873b0-033b-5fb8-a2e5-a6c9b57bf1d5 |  | note | FORMULA :
label | 6b1b7a45-cf94-5fa8-9976-29f16ae046a9 |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 0a22f640-1798-5666-941f-914ac722607e |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | a85c4737-d657-550a-878a-06edcd7fbc50 |  | note | Pc = kPa
label | 02650431-97d9-542b-b2de-5ef71d314a69 |  | note | WHERE:-
label | 99a8cac6-2ae0-5916-88a0-05dd025476e9 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | bbc4e9cc-00bf-5d46-9f70-2b8e4db6d4ab |  | note | Pc = CORRECTED PRESSURE
label | 016d05b8-8962-5746-be73-b4a913bb5f48 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 86541b6c-4f7f-5294-9f61-4d8de5c6d812 |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-flat | 93007974-954d-45f7-a8ce-a5d51ebae12a |  | checklist | Combined Services HDPE Natural Gas Installation V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V3 | 9e2e04f7-0d6a-48db-95c8-020c1f39ad6d
checkpoint-status | 81d9d1c3-2ca4-4755-aed4-9dd51ccdcaa9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 0fb1a183-6dbd-482b-be42-c8e0a34072b3 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 09f69685-fc69-4bc7-88c7-9198fe341b83 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 825b3a50-18bf-57e0-97c4-987d3c605216 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b5aa1df9-51c8-5b16-aa17-a51bdc5279b9 |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 909a3597-29fd-4927-8a6d-2ff7e662fdeb |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 99b2c206-aacd-45e1-9a8c-4efd37ea0974 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | f8d40eab-e855-4581-a10a-3da602616382 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 847199ee-28f0-489d-b68f-a6b1ea2692f0 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 9428b30e-e48b-4682-8abc-0cd2f6173d12 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 8a669313-2aef-4a04-9df8-66e7cc9d1a74 |  | checkpoint | Installation of Valves
label | 3003871f-c66e-5f8a-83f1-7d2b5155bc25 |  | note | Valves Installed as per approved drawings
label | cad845f9-dc68-557b-8a8a-22fee268b063 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 6e6e5452-7ee5-4ad6-829e-1e8ba0a7ff6f |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | f3317e12-269d-456a-80a4-13b64429f8bb |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 81c263a5-653a-4ab6-b365-f864ce6ae265 |  | checkpoint | As-constructed survey
label | bd6d1095-6d27-5fc3-bb68-e67c7e640bbe |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checkpoint-status | b4dc20ec-aa59-47ce-a4f7-fc4261ad54b9 |  | checkpoint | As-Builts Completed.
holdpoint | 59d1e029-4656-4fa9-99ab-2651d60b62e9 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | e877be19-0a2b-48be-9cd3-c7d0ffdcd24e |  | checklist | Electrical In-Ground Conduits & Cable Pits |  |  |  |  | Yes | Electrical In-Ground Conduits & Cable Pits | a0cd44b6-befc-425b-8b89-0880e4c25fda
checkpoint-status | 45738f9e-de1e-430d-862d-0aef3eded4ed |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | c7c134c4-a7c3-4338-9dac-528f83618f98 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 2ba1f280-aa6c-555f-b88f-a1b4bf2b6b6a |  | note | Attach: material inspection checklist
checkpoint-status | 5828a8ee-2352-43a8-b68f-be0be74d69dd |  | checkpoint | Location
label | da86c99b-bfd2-52e6-b671-669ddac8cd30 |  | note | Shall be as shown on the drawings,
label | d82a44ea-153b-5c0c-9062-9a83f925aff6 |  | note | Shall be as instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction.
checkpoint-status | efe669d2-dc5c-487f-9bad-7415cfe09b8f |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
label | 0ca40191-2f31-56e9-a4b2-f833d2d15ddd |  | note | Attach: Trench handover document & photos
holdpoint | fe758e84-8eaa-4a3d-aefb-ad7803d44d56 |  | signoff | CPB HP - Documents
checkpoint-status | 1cb5a645-38db-4f4d-a52f-00a14dac3d62 |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status | 6bbbe108-cba7-45be-bfc9-9160c0e34a15 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
label | b88c9bc9-651d-5c9a-bbd5-bee8f6ab81a6 |  | note | Attach: Conduit Layout drawing
checkpoint-status | d0c9c536-1ca9-4027-8172-8ed790971d07 |  | checkpoint | Location of conduits shall be shown on the drawings.
label | 235ad484-226a-5598-ac31-9835569667d6 |  | note | Attach: Photos
checkpoint-status | 5d7d1378-e29b-45a2-b7c1-141be985f99b |  | checkpoint | After installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during installation.
checkpoint-status | 91e0aa03-24a7-434b-91eb-4b468df04cee |  | checkpoint | Bedding of conduit and pull-pits
label | 3aac3982-665d-5880-a1f9-473eab174983 |  | note | Conduits and pits shall be bedded on approved bedding material.
label | 6817f354-ded2-5f61-987d-efc4de90826d |  | note | Bedding material shall be 50mm above and below communication conduits, and 100mm above and below electrical conduits
checkpoint-status | ff86d32e-b235-4e3f-8412-d79cee4e6197 |  | checkpoint | Cable pull- pits
label | 3e057be5-2529-5ee4-9838-7a0832dfa315 |  | note | Conduit entering and exiting a pit shall conform to the locations and dimensions shown on construction drawings and specifications.
label | 8a4f1440-c6df-5d39-99ed-017d8a62a705 |  | note | Where practicable, conduits shall enter and exit a pit at the same height and orientation.
label | 156f4224-2dc8-5f1b-b69d-4fd16e1ba8e4 |  | note | Sealing around conduits where they enter the pit is to be undertaken on the inside and outside of the pit.
label | 76f68f13-edc8-5c5c-b14a-1895e43c90c3 |  | note | Attach: Photos
holdpoint | 75a4b549-0b04-49e1-98c9-dbae3c6acba2 |  | signoff | CPB HP – Conqa checklist
checkpoint-status | fad3e6d4-33b2-4363-8b36-6ca124fa89b1 |  | checkpoint | Bell mouths to be installed where possible and correctly colour coded.
holdpoint | 567397ee-cf84-4a82-a2ca-81c421b0994c |  | signoff | CPB HP – Conqa checklist
checkpoint-status | a4c00335-a3d6-4841-8ccb-425cadc58140 |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
label | 70e6cd71-6137-594c-85a4-62d998b699f9 |  | note | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | e4edafe1-01d9-4f8e-8823-067caefd1521 |  | checkpoint | As-built drawings completed.
holdpoint | 9778b1ff-9e97-4dcd-98f9-d2191cb23c21 |  | signoff | CPB HP– As Built Drawing
checkpoint-status | 39ebf948-1ced-4786-a170-64c4d38c9b58 |  | checkpoint | ITP Sign off Witness Points
label | 5154cff1-3595-53c3-848d-75572bd24e90 |  | note | 2.1 Location
label | 38297db6-6670-5437-91e1-7579d0918693 |  | note | 2.3 Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
label | 8feadbb3-e6cf-571e-8bda-3bd19baf4e9b |  | note | 3.1 Number of conduit dimensions shall be shown on drawings.
label | 96a7d919-e7ec-50c0-99bf-e3db404ea080 |  | note | 3.2 Location of conduits shall be shown on the drawings.
label | 68918265-5cd0-5db2-83aa-e12cc29c8914 |  | note | 3.3 After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
label | 14d31b6d-b739-5770-b6b0-cdf306909b4c |  | note | 3.4 Bedding of Conduit and Pull-Pits
label | cb257ad3-4031-52e4-a974-50c5e636c688 |  | note | 3.7 A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
holdpoint | bc995af8-035a-463a-8453-de19f5c18775 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat | 8a703e42-eea5-4695-a289-390aedacb47f |  | checklist | Natural Gas Purging with Natural Gas |  |  |  |  | Yes | Natural Gas Purging with Natural Gas | b07dd55b-9d63-475b-8912-b0f1fe050338
checkpoint-status | 839464d5-d6df-4122-a8f6-be05a6c0545e |  | checkpoint | Ensure gastight pressure test has been completed.
checkpoint-status | d5cf176f-dc1d-425f-bd78-412d61799fb3 |  | checkpoint | Confirmation that the line has been purged by an inert gas prior to fuel gas.
checkpoint-status | 9a9af8a9-bfec-4a11-9cbf-cf59b7be42cc |  | checkpoint | Set up purge point at the valve train
checkpoint-status | f49251b5-4117-480a-b2fb-8dd4c0c48acd |  | checkpoint | QA Documentation received from CPB/subcontractor for UT1 prior to purging
checkpoint-status | 676dc12f-90f7-43fa-84a6-6a29a94323e8 |  | checkpoint | Confirm subcontractor in UT1 has disconnected all appliances and caped all open ends.
checkpoint-status | 856c1fa9-52c2-4e86-928e-bf9c70eba166 |  | checkpoint | Confirm valve installed on purge discharge outlet in case of quick shut off is required.
checkpoint-status | af67d2d3-0594-4e35-b446-2c2b7b21b4fe |  | checkpoint | Confirm purge outlet is open to atmosphere and is 6 meters away from the opening into a building.
checkpoint-status | 0d4a5024-5ebc-4cf6-9040-f901d8a66870 |  | checkpoint | 50-meter diameter barricade is erected to maintain a controlled area around the purge point.
checkpoint-status | 88c86b81-7ea9-4a4c-95ff-8e151622285c |  | checkpoint | Senit gold meter located at the discharge outlet location.
checkpoint-no-status | eec02252-3a0b-4408-9839-a72ab3723143 |  | checkpoint | Purge Details
select | 0d877613-1a86-5e30-aa43-54a531cb6d9f |  | dropdown | PURGE SEQUENCE | 1, 2, 3, 4, 5, 6, 7
select | 091cdb29-44ca-5607-a0fa-1969361d392e |  | dropdown | Open Building Trench Riser Valve | UT1 , FM1, SPO, KIT, LAU, IND, FM3
checkpoint-no-status | 71492d8b-6d04-4800-aca8-e0fec6dbd679 |  | checkpoint | THE FOLLOWING TRENCH RISER VALVES ARE CLOSED
boolean | f3bfb8e3-69d3-56e5-8991-616488cb0b1b |  | tickbox | Building Trench Riser Valve UT1
boolean | d40ee01a-f51b-5d0a-92aa-0619b9fccca1 |  | tickbox | Building Trench Riser Valve FM1
boolean | 6a6d3dcb-412a-512d-b3e6-b70a496ba7d8 |  | tickbox | Building Trench Riser Valve SPO
boolean | a73282e7-bb4a-5dea-8845-e4d8496de114 |  | tickbox | Building Trench Riser Valve KIT
boolean | fa043d00-f3ad-59db-8f5d-9b1ec4f4d201 |  | tickbox | Building Trench Riser Valve LAU
boolean | a76587e1-2cab-5262-b52f-a1ef3750d377 |  | tickbox | Building Trench Riser Valve IND
boolean | 90aaca35-6465-56a7-9df8-393b0835439e |  | tickbox | Building Trench Riser Valve FM3
checkpoint-status | dabdbfdb-454f-48a5-8dc2-5e5ff091f2df |  | checkpoint | Open supply valve and commence purge
text | 6089d9ea-bf7f-5c53-afe2-e773cd267b7c |  | textbox | Record purge start time | hours:mins
text | 0475d1db-2beb-5767-8e60-fc5741e98b5e |  | textbox | Record purge finish time when gas purge reads zero | hours:mins
checkpoint-status | 62c1dd50-49e9-427c-b31c-cbda264dbfc7 |  | checkpoint | Isolate supply on completion of purge
holdpoint | ceb46cc5-ce14-41f3-91ff-2decb7ae9541 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Combined Services Warden Controls |  |  |  |  | Yes | Combined Services Warden Controls | b201be90-27ff-4ae4-8ba7-55a99cd30c3d
checkpoint-status |  |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status |  |  | checkpoint | Wiring cell lighting to cell DB interface relays
label | d630c5e3-2fb6-5d2b-8d40-360ef18bd663 |  | note | Specified type / cores of cable used
label | 7684dc73-f8ca-5270-9e1a-a4e855b25ebb |  | note | Location, spacing, & routing correct
label | be2bebb4-dd17-5803-abae-a3005183828b |  | note | Cables secured on cable trays
label | 73acb246-453b-55de-993b-764e28232efa |  | note | No damage to outer insulation
label | a0b37c82-6224-5b45-a0f2-2eb8dd9a8391 |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Wiring IPTV cables to cell DB interface relays
label | e4188d23-2220-52b8-aa3c-ec58cfa34b95 |  | note | Specified type / cores of cable used
label | 88189cf8-259c-5636-8bd4-0124912eb146 |  | note | Location, spacing, & routing correct
label | 8eb14041-3141-5f42-8d81-4d44fb09c3bc |  | note | Cables secured on cable trays
label | 384148af-5f36-52dd-9726-ff43f6b5838e |  | note | No damage to outer insulation
label | 3a870771-5387-5545-b939-cf0dfe11411f |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Install and wire cell piezo to cell DB interface relays
label | 00b80e69-7523-5c41-9bcb-e64d1f00cf8d |  | note | Specified type / cores of cable used
label | c2d0e3ea-7aa3-5de7-93f3-47786ed99b19 |  | note | Location, spacing, & routing correct
label | a5fded9a-ec2c-5b42-928a-79354e5ce0c5 |  | note | Cables secured on cable trays
label | 77e1ae32-3cef-5883-9503-582272743411 |  | note | No damage to outer insulation
label | 49bb5210-b84c-5a46-8234-ecc091ea6ac1 |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Install and wire outside of cell piezo to cell DB interface relays
label | 033d5b80-1bf5-5457-bb0d-abfb88fc2050 |  | note | Specified type / cores of cable used
label | dc182092-3b56-5543-9e06-02e9298415e2 |  | note | Location, spacing, & routing correct
label | 9af218b6-da12-5a46-b8cd-07d0ace8a610 |  | note | Cables secured on cable trays
label | 490ce726-b382-568a-a315-123ed0a2c10f |  | note | No damage to outer insulation
label | 9c703b92-d293-55cb-864f-142f4da82b1d |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Wire TMV box cables to cell DB interface relays
label | e8b9d7f0-daa4-5a66-8482-fbcae29f5cb4 |  | note | Location, spacing, & routing correct
label | 2f4dc59c-3442-5a4d-9968-363d0f39d58f |  | note | Cables secured on cable trays
label | e6f87a19-97cf-5aa5-9de1-7f54ab19547e |  | note | No damage to outer insulation
label | 1604783b-33b1-5dbb-8cda-65c119c5319f |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Wire flush pipe solenoids to cell DB interface relays
label | b1ea32c1-b11e-5ed9-91eb-2cfc3b549936 |  | note | Location, spacing, & routing correct
label | dc9046db-f38f-5d1e-bfcd-192ba6992a24 |  | note | Cables secured on cable trays
label | f7f6fbaa-e7ac-5968-910a-d642a4ec7544 |  | note | No damage to outer insulation
label | 7c59a381-98fc-595d-9e3c-9b94dc5e9a4e |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Install PC400 units and 24v transformers in enclosures and mount on site. Power supply connected from general power
label | f0ed27cd-dedc-53fb-8dc7-c910e24848bd |  | note | Terminations correct
label | de86d9f6-a99f-5d98-a8e0-38f6f45019b5 |  | note | Earthing correct (in case of conductive enclosure)
label | 4132985d-13ae-53b7-a560-809d25decbcc |  | note | Power supply tested
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Wire cell control boxes to PC400 with 3 core comms cable
label | 53074b9f-b2ac-59d1-886a-d10122a94154 |  | note | Specified type / cores of cable used
label | 297a15f9-d7a9-5582-b782-f9a093bd3295 |  | note | Location, spacing, & routing correct
label | e2c60c8d-9f4d-5e09-b406-85d296232b28 |  | note | Separation distance from power
label | 1ec676e1-5bd1-5548-a98e-59becfa556d9 |  | note | Cables secured on cable trays
label | 9fe6dd83-ec05-518a-bdaa-819ec75c5793 |  | note | Comms shields grounded
label | b452737a-ce4e-5047-82ce-b9eb22b4cd0f |  | note | No damage to outer insulation
label | 4ce2d4b6-171e-582f-98f8-24c104dca40d |  | note | End to end continuity testing
label | 8f823f6e-d285-5f4d-b6c0-86585898fa63 |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Wire PC400 to BMS network switch with CAT6
label | b2984f9a-ba16-52f8-a59c-745e63134f67 |  | note | Specified type / cores of cable used
label | 2b118c4c-f28a-569c-9ccc-601ead1cb0b3 |  | note | Location, spacing, & routing correct
label | febfad0f-4190-563b-a7d6-75366c6a7b4e |  | note | Separation distance from power
label | 96a2ac20-6596-57ac-95fe-d759f6ef89f8 |  | note | Cables secured on cable trays
label | 166a3f42-d63b-5e9f-bae0-176d721365fc |  | note | Comms shields grounded
label | 9d2e6253-8ebd-5c69-89c9-7030d4271663 |  | note | No damage to outer insulation
label | e277180f-eeb5-542d-a125-44ca5aa21444 |  | note | End to end continuity testing
label | 0b3ce4af-b305-5990-9394-b4592d05fd7c |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | Install touchscreen units & connect to power supply provided
label | e3fd4c67-31cc-58a5-9fa6-80c9ff11d9cd |  | note | Terminations correct
label | 8abe9598-82ef-5d15-8856-60b324c97f2b |  | note | Earthing correct (in case of conductive enclosure)
label | 6ca795dc-d0f9-5fff-b83e-2ef49a933081 |  | note | Power supply tested
checkpoint-status |  |  | checkpoint | Wire touchscreen units to BMS network switch with CAT6
label | 1c0cdc55-0a1d-5850-86b0-485a11f0b5c7 |  | note | Specified type / cores of cable used
label | 5fea1485-2b81-5dbf-baae-0835ee4f86cf |  | note | Location, spacing, & routing correct
label | 8a63612d-6b4a-5e99-a7a1-e00addbf7b69 |  | note | Separation distance from power
label | 63d18fa2-538d-5ce0-9fe9-12930edb449f |  | note | Cables secured on cable trays
label | 4c62b030-69cb-51c3-93b8-35b2da832a5e |  | note | Comms shields grounded
label | 1c50742f-9850-5a9b-a44c-af23a58d5590 |  | note | No damage to outer insulation
label | 1af27a35-9365-57a5-96e8-7daf31e00c86 |  | note | End to end continuity testing
label | 0c48163d-ca19-50d6-97ee-baf65c7cbf29 |  | note | Correct labelling
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status |  |  | checkpoint | As-Builts Completed.
holdpoint |  |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 8df4d3ed-8bdb-42e9-82de-d0cadc06e703 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation | c59fc557-bdab-44f8-852b-9636f393cf97
checkpoint-status | 88aab074-4f9b-4b8f-af51-d9dfac6b3502 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 9821c007-9bb4-4899-9614-341aeb89b8a4 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | fe27d8b3-08b7-4627-b452-9f3b9422a956 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 07b77797-8e68-51d9-bbab-3132752b323b |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 3b234dcd-c22a-501f-8c17-d16aa255515d |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 91e6e5c8-e3ff-419c-bcdb-1ccdeff16853 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 8374cde8-87ad-4308-8bd3-9aab6a8b5215 |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 4ba606c3-8b94-467a-98b9-fbe836c376fe |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 764e962b-7a44-4270-8e15-d45cd60d953d |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 56002e45-3f38-4506-b07e-dc135eebfd25 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 239e460a-38bb-4026-8238-4e376ad68e1b |  | checkpoint | Install , valves , tees and bends
label | 0e66742e-a83c-5d42-9f25-fb8bd39b6481 |  | note | Connections are installed as per construction drawings ?
label | bc4c2568-5c29-5e09-b0a6-8d2f6c3291ae |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | 9ae200d9-5be7-467d-b70a-3d30b0e1b9fa |  | checkpoint | Install Thrust and Anchor Blocks
label | f5b9a63c-9e9c-5841-8f31-a94c30988d13 |  | note | Minimum dimensions as per IFC Drawing
label | 1760354d-13a2-514c-97d3-bf85c79c5bf5 |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
checkpoint-status | 546e181e-3cbe-445a-8c63-ac427c4a8326 |  | checkpoint | Installation of Trace Wire
label | 09559862-89ff-5d80-a66a-f6d7332fc9ad |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | af65ec56-f26a-53b8-8c1b-c4b5c5d9e4c3 |  | note | Test Trace Wire as per Specification 5.20.4
checkpoint-status | 43c5c3ba-5577-48e8-85c3-117493d2f341 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 5aefd7da-0039-43f7-b437-bd7df113469a |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 4aa36fa4-391c-5bb3-8d6c-fa352e525984 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | b8890980-9f9a-5ce9-8395-52d9cd5b8536 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | e3b5fa41-e2fb-51b7-8b95-3452191f218f |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | ead78483-f92f-4b36-b23a-adfb58f0f1dc |  | checkpoint | Introduction of Air to 300 kPa
label | 79189b3f-1d8e-549f-832b-9e2b0634fe7a |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 2feb764b-e689-5fc1-8640-310579e4bef8 |  | note | Monitor for any drop-in pressure.
label | 2e18c498-037e-5efa-ba31-659e46249caa |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 83ef3bf4-9dfb-4ec4-86f9-42c83a98f86e |  | checkpoint | Increasing Test Pressure
label | a3685c7d-a037-5926-9d6c-6ea0910903c4 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 756c2522-ea15-4d0a-bd76-10d472ab7564 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 6511feda-4264-4326-8a39-d87f24253226 |  | checkpoint | As-Builts Completed.
holdpoint | c33cd4b4-345b-4bd1-bd95-b0d833bf9b58 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B5B - Line Valve Assemblies – Closure and Zoning Tests |  |  |  |  | Yes | B5B - Line Valve Assemblies – Closure and Zoning Tests | c8bb60ea-8bb2-41b4-90b5-e63b6d0273dd
checkpoint-status |  |  | checkpoint | B5B - Line Valve Assemblies – Closure and Zoning Tests complete
text | 679e6b9e-f357-5c54-abb6-e0f2fe0403b8 |  | textbox | Plant ref
text | 25531676-60a8-59d9-a61f-39a3b355fa51 |  | textbox | Test by
text | 584309f8-fa41-5c84-af23-ebbb64c5a5b3 |  | textbox | Test date
text | d4cc820c-d1db-512a-ba30-ca98b04dcf80 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the LVAs was tested in accordance with paragraphs 15.63–15.65 on the pipeline system as follows:
text | 5e07613d-b1a1-58d8-bf12-15c4c8f69655 |  | textbox | LVA number
text | f8ddbf31-9f43-53be-b761-ad9a3108128d |  | textbox | Test pressure (kPa)
text | 83eddcd6-78e5-50ca-b9c9-b3c34d7dc36a |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 35dd3b89-8093-5fe5-8cde-b0d8a70ee385 |  | textbox | Terminal units controlled (total no)
text | 89ed74d7-470e-5c4f-a466-b610dca7440b |  | textbox | Terminal unit labelling
text | 72dd5014-7f19-518a-a9d4-662a905dea9f |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 6ff8de63-907a-55ce-8f28-34a3de453404 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 43629857-fa73-5bd2-9eb7-eb52ec5220a2 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | Back-Flush |  |  |  |  | Yes | Flushing - Back-Flush | caaa9de6-1ce4-4d1a-8f48-5b63060b0f54
checkpoint-status |  |  | checkpoint | Chemical cleaning is completed and clear water is visible at the main drain valve.
checkpoint-status |  |  | checkpoint | Terminals backward and forward flushed and water drained at the terminals until clear water is visible.
text | 79c71eac-ef72-5b4f-a41a-caa45db7da2d |  | textbox | List the terminals backward & forward flushed.
checkpoint-status |  |  | checkpoint | Water sample is taken from the furthest terminal, and labeled as "Back-flushed terminal" and dates.
text | d1440617-fc81-563b-8b91-5d6c59f291ed |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Sulphate
text | edfb545e-9b69-544c-9e46-94f6c79a253e |  | textbox | Site measurement
text | fb67b5f7-0acf-559b-b04e-a48ce74570a9 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 87c73cfc-959c-58c4-87cc-4dac9bdc8150 |  | textbox | Site measurement
text | 0a6fb746-77e8-5439-aa38-d67d007ca61a |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 5cb36cea-3baf-5da3-9329-4ffc1cf42248 |  | textbox | Site measurement
text | 39adfb71-ee10-5842-afa2-6525559060fb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 1c54ecab-72ec-5aca-83c5-b8b3e7b2e137 |  | textbox | Site measurement
text | 37fa0001-0888-5fe5-a0a3-33590781069d |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 6c7e929a-a204-503d-abd1-78133b98fc63 |  | textbox | Site measurement
text | 280cf04f-3e77-5adb-b3fe-701be04429c8 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | b23ece62-3b59-5df3-93a4-39a917845a68 |  | textbox | Site measurement
text | 32a65d99-e4e7-5b30-9796-ef96af824401 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 69bbef48-d8c8-5919-8150-d5d1784cd5ae |  | textbox | Site measurement
text | 4a8a6c89-72a6-5ecd-9885-d0fbe741f7e4 |  | textbox | Lab test results
checklist-flat | 0ef15cad-43cb-46c7-b3ce-b6c7d3e17366 |  | checklist | Combined Services Cable Hauling And Fibre Blowing Through Ducts And Micro Ducts |  |  |  |  | Yes | Combined Services Cable Hauling And Fibre Blowing Through Ducts And Micro Ducts | cad74d21-d645-4deb-bc70-ab9c316f01a7
checkpoint-no-status | ebd71efc-4911-4047-9763-42156804e410 |  | checkpoint | MATERIAL COMPLIANCE
checkpoint-status | 38d61c81-04df-4a51-bbd6-f4744d46acc1 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | e13811e2-9c7b-4e8f-ad0a-ffa555ac3464 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-no-status | 654739a8-8599-4cdb-9e1a-888be03eef5b |  | checkpoint | PRE-COMMENCEMENT CHECKS FIBRE OPTIC RETICULATION INSTALLATION
checkpoint-status | d78d366f-00fc-41e4-add2-7807ef65202a |  | checkpoint | Installation of Conduits and Micro Ducts by AE Smith.
label | de1b4d9f-6175-5265-bfd2-5f576a681fd9 |  | note | AE Smith to install conduits and micro ducts as per their Approved Inspection and Test Plan -.AES-NZ1005-STE-ITP-PMT-0008
holdpoint | f95b3dec-1e0a-4ebb-b355-e5a01e1e9bff |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 56667adf-743e-4280-9dde-8e67912efb3f |  | checkpoint | Location of Conduits and Micro Duct for Cables to be Hauled.
label | 9775f5a2-5c82-5aa7-b2ec-92d58bc9404b |  | note | Shall be as shown on IFC drawings.
checkpoint-no-status | c3620eef-99a5-4bfc-af53-944eac3276aa |  | checkpoint | HAULAGE OF CABLES
checkpoint-status | 4f1eab1f-8bd9-473b-8110-20509265ae0b |  | checkpoint | Pre-haul checks.
label | a291a942-961d-5146-9a6d-e6c6d5732195 |  | note | Verify cable or micro duct is in good order and condition.
label | 8b9f27a1-9c94-5177-93c3-f92f8af4c305 |  | note | Verify duct line is intact and free of debris.
label | 70069732-119b-57d4-b846-729bc49afb25 |  | note | Temp between -5° + 40°C
checkpoint-status | 3d03faae-6fb4-4a29-9499-a6f0e511cc7c |  | checkpoint | Confirm the correct lubricant is available for use, where applicable.
label | cc8e6a8c-29a8-5ff4-947f-6481e0a06bef |  | note | A Verify correct type, and that sufficient quantities are available on-site.
checkpoint-status | 072afb40-b348-4f21-8814-cb06e95fcdc5 |  | checkpoint | Monitor hauling tension.
label | 5ebbc9bd-a1cd-5f6e-95db-7070d6e729c3 |  | note | Tension gauge must have a valid Calibration Certificate. Attach Calibration Certificate.
label | 306baa91-7a00-55ce-b861-3a91e50c461c |  | note | Indicated tension must not exceed the cable manufacturer’s recommended maximum haul tension.
checkpoint-status | 6384477d-cec8-440d-8bc1-1f8137e7eef7 |  | checkpoint | Fibre Blowing
label | 32155a80-091a-5bd0-8663-fca209a26447 |  | note | Follow in accordance with manufacturer's guidelines.
checkpoint-status | 4d208367-9974-4d49-a108-42de735d1345 |  | checkpoint | Observe the haul.
label | b956bf99-a727-579c-9c1e-33641a82ef10 |  | note | Stop the haul if a potential risk of damage to the cable or micro duct is identified.
label | b45d8379-04d5-58e3-bf7e-6c2902a144b3 |  | note | Monitor bending radius
checkpoint-status | afd72358-f0b5-41d8-87b2-906479d91111 |  | checkpoint | Inspect cable sheath during the haul.
label | 2dc48e72-4bf0-5623-a843-db3006c86a90 |  | note | Stop the haul if any damage is identified.
checkpoint-status | 128b2dd6-10b2-43ee-9262-28f4a48d8ca0 |  | checkpoint | Inspect cable sheath at the completion of the haul.
label | 0f6018e3-12ce-5b8d-864a-73501b0e2391 |  | note | Identify any signs of damage.
checkpoint-status | 5dbbf6f6-6666-432f-a48f-e6cc82c726c4 |  | checkpoint | Inspect the sealing of cable or micro duct ends.
label | 9971821a-7dab-5b2c-9e96-486551736630 |  | note | Sealing meets specified requirements.
holdpoint | 0c9d133b-bd5c-4a8e-a40c-ee80688a6fe6 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | a7f681b7-bbb8-4d38-9151-ee0141cbb281 |  | checkpoint | As-Builts Completed.
holdpoint | 96eb2e1a-368f-4619-ad83-2cea9a4f6999 |  | signoff | Request Sign Off/ Raise Remedial
checklist-flat | 1614c5ff-3700-40b1-949f-abc2cb5aad38 |  | checklist | Combined Services Trench ( Excavation, Backfilling, and Compaction) |  |  |  |  | Yes | Combined Services Trench ( Excavation, Backfilling, and Compaction) | cf8b6400-5884-46e5-bb97-7625facf426b
checkpoint-status | 6a7ffee3-1afb-4978-811b-0d2eeb4c5dec |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 1000cfbc-6c9f-46a4-b6ac-1d32c28f094b |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | d10fe8ee-e600-451b-bf6e-141f4b6b2253 |  | checkpoint | Location
label | fe175828-c69e-5f9d-8b17-db8cd09b87ab |  | note | Shall be as shown on IFC drawings.
label | 469e367e-e21e-5c23-94ca-48dc581b2b19 |  | note | Excavation Checklist to be submitted
holdpoint | b018bd10-7630-4565-b322-1b27e3d2e56c |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 37066727-2128-4d6e-b823-c8fbc826f7bf |  | checkpoint | Remove and replace unsuitable materials (if required)
label | 61363ec1-635b-51be-847b-7d0efc7fb0f2 |  | note | Undercut weak or unstable ground and place it with suitable soil in layers of maximum 200mm depth
label | fe8c9c68-83b2-554a-b2a6-4c961a21de04 |  | note | Trench bottom shall be free of stones and edges of any stones, tools, objects which may fall into the trench and damage the cable
label | 95ff6391-5ad6-529b-ab88-ae1fb42c39f2 |  | note | Keep trenches free of surface water
holdpoint | e702e809-3710-4c31-8439-ae863541c565 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 86ddb1cf-797c-4987-ae86-b2714a84cb7d |  | checkpoint | Minimum trench width and depth maintained
label | 689fd412-f0ea-5fd8-8e48-8be05758b467 |  | note | The formation of the trenches shall be in accordance with project drawings and specifications
label | 246a230f-0981-5ab3-b606-0ed42dd0da5f |  | note | Minimum trench width to be the pipe internal diameter plus 400mm to permit all operations for dewatering, placing of bedding and jointing of pipes
label | f77d8971-dc28-52e3-b364-071a87922657 |  | note | Electrical :minimum 400mm (ESDG-2701)
label | 66b4d222-92fb-55d8-b905-77bf89447242 |  | note | Communications : minimum 300mm (CSSP-0001 CL6.1)
holdpoint | 0376ba2e-f4ca-4368-b13a-59ada23794b6 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 73020531-61b1-4048-8fcb-cc28f1b1af1d |  | checkpoint | Placement of bedding material
label | 791e633c-5fa0-5086-875d-6d85c04c2412 |  | note | Sand Bedding and cover of :
label | 747ab134-fbef-559d-a2ff-a2f652e34fdc |  | note | Electrical Conduits - 100mm below and above conduits
label | f36e4b80-4a88-5f2e-a686-381ba48f5832 |  | note | Communications Conduits - 50mm below and above conduits
label | 870072d2-ea38-53a5-be03-3fffe312558a |  | note | Electrical pull-pit bedding - To consist of a 1:4 cement & sand base extending a minimum of 100mm around the pit, and 150mm deep
label | 019ea4d5-8e42-5197-baba-61a169c2830b |  | note | (eg. T66H pit = 663mm x 663mm therefore the base must be >= 763 mm x 763mm deep)
label | a4421cc1-19a3-552a-bef3-862ca9603b29 |  | note | Communication pull pit bedding - to consist of a 1:4 cement & sand base
label | ca4fd1dd-16b9-5f3c-b8f4-807e6ebf37ff |  | note | C5 & C2: a base extending a minimum of 100mm around the pit, and 150mm deep
label | 95278f82-e78e-5c0c-9f7a-892ea329a3a1 |  | note | (eg. C5 pit = 590mm x 840mm therefore the base must be >+ 690mm x 940mm @ 150mm deep)
label | 43314ea2-1b89-57ff-ac7c-b3567ecc85a0 |  | note | C1: a base extending a minimum of 100mm around the pit, and 300mm deep
holdpoint | 4634dd71-df76-4ee0-b143-58690a221fc0 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 0812cd21-3bfd-4b34-8952-5ef4c4a432ae |  | checkpoint | Placement of pull-pit drainage
label | cb4f341c-535f-5185-85aa-2ef2a759547a |  | note | Cable pits - Drainage metal smp minimum size 300x300x2000mm , offset to pit base
label | c2e63444-a67a-5e48-a75f-52e6eb76e09b |  | note | Electrical - Drainage metal sump to be same size as cement & sand base, offset to pit base
checkpoint-status | 29c7a48d-0152-4482-af27-8af40646c376 |  | checkpoint | Placement of Concrete Haunches on conduit entries
label | 20526853-e680-5871-b333-7e90e5b13281 |  | note | Electrical Pits
label | 9086079d-8839-5437-b542-d493cf005c9c |  | note | Only required for multiple conduit entries, as specified by manufacturer
label | e44852a0-35a8-5d76-8332-6ba02b469ef9 |  | note | Must be 25Mpa concrete. This will be achieved using bags of premix cement and the required ratio of 1.7-2L:1 bag(20kg Cemix Multicrete)
label | 81f49970-b5b0-5e63-819c-ef81cbf5ac64 |  | note | Minimum of 100mm concrete encasing is recommended around the pipes and 200mm measured of from the pit wall.
checkpoint-status | ca5b3766-21c8-41a4-92ea-a1777db4645d |  | checkpoint | Installation of Conduits
label | 390dbb66-e7e6-5d46-a891-a68f01d19024 |  | note | Installation have been tested and proved satisfactory.
holdpoint | 0e067f22-8c95-4425-a598-9533f434b92a |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | ae6bdfb3-73e3-4980-8635-503585db313b |  | checkpoint | Installation of Concrete Collars
label | bbd44fd9-1884-5295-9aac-5c7751bd04f0 |  | note | Ensure minimum concrete strength of the collar is 25MPa. this will be achieved using bags of premix cement and the required ratio of 1.7-2L:1bag (20kg Cemix Multicrete)
label | 60b7c4be-fedd-57a7-842f-41fd9bd84615 |  | note | Concrete should be vibrated to eliminate air pockets
label | 7f9bd9d4-28fd-5df7-9211-3ffae9c3936c |  | note | the finished level of the concrete collar must be flush with the top of the cable pit frame
holdpoint | 5a5ac356-c276-41c7-95e4-9dd6dd9a9e32 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | 7aaae54f-808d-4fb5-bcec-9c04b92a7463 |  | checkpoint | Fill material placed and compacted
label | 1acbda73-d63b-5971-930a-2f0994997f76 |  | note | Backfill shall be built up in layers and compacted evenly in 300mm compacted lifts above the services with approved material. Lifts to be 150mm where manual compaction methods are adopted
label | bbffa174-54f8-549c-9054-791fe84cfbb3 |  | note | Backfilling materials shall be free from stones or rocks larger than 50mm, or other materials which might prevent proper compaction
label | ba36c211-880f-51a7-ac0f-a73547a21965 |  | note | backfilling materials shall be free from fossil content, clay, vegetation, and its roots, waste materials.
label | d9d19f2b-8cc7-566f-b58b-27360f3b59df |  | note | Mechanical compaction of the fill material directly above the pipe shall not be used until the depth of cover above the top of the pipe is adequate to prevent damage
label | d1a3fb96-7785-5613-a047-46573e99d406 |  | note | Hand held compaction equipment to be used until 400mm cover is achieved to avoid damage to services.
label | 9dbd6d84-0793-5818-8a78-568008da4128 |  | note | Test target >90% MDD beneath landscape areas and >95% beneath roads. Material to be placed to a degree of compaction which is not less than that of the material prior to excavation
holdpoint | 6308d382-ebcf-4d04-a454-b8dadf286b80 |  | signoff | Request Sign Off/ Raise Remedial
checkpoint-status | aa43d0a6-1e16-430f-aed3-398b6c4acc6d |  | checkpoint | As-built drawings completed.
holdpoint | fddffb4c-4740-4432-9ac5-658afda734a7 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Photos |  |  |  |  | Yes | SYS - Photo Upload Test | d0fb64f9-713a-44a8-8007-ea12b19354cf
checkpoint-status |  |  | checkpoint | Upload Photos
checklist-flat | 906012cf-8e3c-41a4-a05e-60e2ad901754 |  | checklist | LV Installation |  |  |  |  | Yes | LV Installation | d77654dd-b372-4044-82a9-a17a62cbfc63
checkpoint-status | 67a18bd9-4ed5-431f-90dd-b8bdf6bedcb3 |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | 0a5ab205-78a8-4e05-9cc1-170ff83bd404 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | cbe3027d-6461-5e35-9244-b2810994f0d1 |  | note | Attach: material inspection checklist
checkpoint-status | 175fdef7-2c06-4ce6-8641-a6ed2d475074 |  | checkpoint | Inspect trench depth, width & cable rout
label | fb2192ef-bc1f-531b-aaba-3cd7de1d3751 |  | note | Shall be as shown on the drawings,
label | 64331e1a-bf3e-5db4-827f-bf4a5e68e73c |  | note | Attach: Excavation Checklist & Photos
holdpoint | 695a32be-c112-45a4-ade6-db0a009ceea8 |  | signoff | CPB HP - Documents
checkpoint-status | fef55cdc-7a2d-4b65-87ac-817b6b634592 |  | checkpoint | Drum Delivery Test Certificate
label | 55f1b4b2-9a76-5d5a-aa29-6222cf6b4e05 |  | note | Attach documentation
checkpoint-status | 06dbbefe-8811-492c-84fd-d78e8efb1905 |  | checkpoint | Pre-haul Checks
label | 665c80aa-4c1a-51fa-b573-74aa64e4176f |  | note | Verify Cable is in good order and condition prior to haulage
checkpoint-status | cf0d4d9b-070c-4b8f-b6b5-8c24f2d60aa8 |  | checkpoint | Confirm correct lubricant available for use, where applicable
label | eeecd397-70cd-588c-a4b1-bcd24dee9381 |  | note | Verify correct type, and that sufficient quantities are available
checkpoint-status | a1deda35-7b15-4988-aba1-d9212900d167 |  | checkpoint | Observe the Haul
label | 80943828-c29a-550f-a03d-c9962258a6e8 |  | note | Stop the haul if a potential risk of damage is identified
checkpoint-status | a79c3f92-0c73-4aef-bfd4-4486ee8db3af |  | checkpoint | Inspect cable sheath during the haul
label | b9b1fd8e-a90d-5412-8f2c-afbf29afc616 |  | note | Stop the haul if any damage is identified
checkpoint-status | 91ffe436-db4e-4fd4-b6fc-6b2f444c51d3 |  | checkpoint | Inspect cable sheath at the completion of the haul
label | d6c01240-9842-5de0-a845-ec6ee4a4978a |  | note | identity an signs of damage
checkpoint-status | 3456a4df-bbb7-40fc-a607-58867e1e7aa0 |  | checkpoint | Install Seismic Loop
label | aa4f16f2-2352-5430-906c-2173c4888b7a |  | note | Visual Inspections
checkpoint-status | faa25146-a365-4f9e-8a3c-d2104f7ab8d3 |  | checkpoint | Install cables into building and contain to prevent damage
label | 0537f3aa-e917-5b4b-a696-80876fd0984c |  | note | Visual Inspections
checkpoint-status | 5952f1fe-0235-4bbf-a785-24adb99ef523 |  | checkpoint | Install lime & compact
label | bc0ca3fb-96a0-5571-99fd-2f40de8f912d |  | note | Visual Inspections
label | a519364c-9b17-5e9e-b0e4-2879239c9c4c |  | note | Check bedding depth
checkpoint-status | 46df5797-ce5e-4622-907e-9ee756eb24d4 |  | checkpoint | Install Mag slab
label | 94d7134d-7ec4-55be-b88e-7ba1a583e649 |  | note | Visual Inspections
label | 2fadbe0a-e33d-5fe0-9028-b073022a07dc |  | note | Make sure Mag slab is covering the buried cabes
checkpoint-status | 8002564e-ec89-4bee-ba18-57e8772971b9 |  | checkpoint | Test cables installed
label | 37967333-e3b0-5fe4-aa8d-ce947c9f7997 |  | note | Insulation Resistance Test
label | 0c970289-b668-5938-830f-ee5a301ffaae |  | note | Continuity Test
checkpoint-status | 87537382-0b6a-493c-bf54-7d3806b40b0f |  | checkpoint | ITP Sign off Witness Points
label | 851812f8-e88e-5002-b1ee-e97f930aa81c |  | note | 2.1 Inspect trench, depth, width & cable route
label | bb2a3abd-e0ed-5b3d-8565-1e2eacb358d7 |  | note | 2.2 Testing of cable prior to cable pulling/laying
label | 928f284c-8457-532a-a66c-345ef87dc8a8 |  | note | 3.1 Pre-haul checks
label | 7e989fef-e0a9-5e7b-bd5e-ad4b2b5e43a3 |  | note | 3.2 Confirm correct lubricant is available for use where applicable
label | 6dd1615f-b708-559c-b122-edda9cf14ff6 |  | note | 3.3 Observe haul
label | b1e38277-6acc-5903-b001-0f1ebfcde592 |  | note | 3.4 Inspect cable sheath during the haul
label | 8f106930-9b37-5581-9964-bb328ddae05d |  | note | 3.5 Inspect cable sheath at the completion haul
label | 4fa1efe7-598c-55a3-93de-da295d3a23dd |  | note | 3.6Install Seismic Loop
label | 2dd349e4-9908-5fea-bad6-a312dd3af5f1 |  | note | 3.7 Install cables into Building and contain to prevent damage
label | d17a6aae-794c-5a3e-b92f-5f808c779d99 |  | note | 3.8 Install lime & compact
label | 466b66f9-2fe8-549c-aa90-b45a7e871cb3 |  | note | 3.9 Install Mag slab
label | 21b79791-3ac1-5812-9333-cb7c6442f9fc |  | note | 3.10 Test cables installed
holdpoint | 508d8267-bb5b-4e4d-8c92-9d1fda23a300 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | b2f1abc0-a346-44e6-9733-85847a8d931b |  | checkpoint | Inspection by Supervisor
label | a1299e1d-e8c7-5ee8-8b8e-f24354308dfa |  | note | QA check sheets, visual inspection and test requirements to AS/NZS 3000:2007 measurements verified
holdpoint | e29362d3-085d-40b5-baad-cbbbe9abec34 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 2a6f8d3f-b278-4c28-9f6a-02c67787f6ae |  | checkpoint | Notice of completion
label | 57bea21f-67c3-5fda-892d-4411d4af1ba5 |  | note | Had back trench to CPB at Mag slab demarcation point.
holdpoint | b3548222-044f-4463-9621-de5b90fd8303 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat |  |  | checklist | Electrical Services – LV Cable Install, Terminations & Testing |  |  |  |  | Yes | Electrical Services – LV Cable Install, Terminations & Testing | daf35787-0dfb-414c-b9a3-12a07ebbbdbc
checkpoint-status |  |  | checkpoint | 1.1 RDM & Consent Approval
label | cfbaa542-a282-550b-a54d-bd818aebdd8d |  | note | RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | 1.2 All materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
checkpoint-status |  |  | checkpoint | 2.1 Direct buried cable ITP & Certificate of Compliance Completed (AES) Drum delivery test certificate
checkpoint-status |  |  | checkpoint | 2.2 Cable containment available and ready for cable install
checkpoint-status |  |  | checkpoint | 3.1 Inspection of cables
label | 8847ca76-31dd-5032-a56e-aa5e64194858 |  | note | Verify cable in good order and condition prior to trying to containment
checkpoint-status |  |  | checkpoint | 3.2 tie cables into containment
label | b8d5d48e-5cec-52d5-8bb4-e64b74e90075 |  | note | Fix cables using approved cable ties / clamps
checkpoint-status |  |  | checkpoint | 3.3 Label cables
label | 8b60ce60-3ff1-5762-ac0b-6fccdb79f3e9 |  | note | Affix correct labelling to each cable every 15m, and change of direction
checkpoint-status |  |  | checkpoint | 4.1 Check drawings and final termination point prior to cutting cables to length
checkpoint-status |  |  | checkpoint | 4.2 Terminate cables with correct lugs
label | 23184670-7a9a-5e7a-a3db-04ff8f532a54 |  | note | Use correct sized lugs, and crimping tool for the cable size
checkpoint-status |  |  | checkpoint | 4.3 Heat shrink terminations
label | a1674ede-c579-5072-921f-328649f554af |  | note | Red
label | ff8003e6-75e3-5edc-8c2b-c661e3a94fd8 |  | note | White
label | b9f330f2-7d95-53b3-8738-ba0364f3cf80 |  | note | Blue
label | 73e68aaf-d560-565f-b055-ff16b9341c00 |  | note | Black
label | 870d76df-88a5-5c54-910c-4157d549d15a |  | note | Green/Yellow
checkpoint-status |  |  | checkpoint | 5.1 Final connection to board
label | 78c9cd81-48c0-53f6-b14e-f20701946feb |  | note | Tighten, torque, and mark bolts and nuts on each connection
checkpoint-status |  |  | checkpoint | 5.2 Pre-livening testing
label | 629425d9-80a4-5d2c-9e76-006b2d3d357b |  | note | Point to point testing
label | 8c953236-7a3d-5521-a05d-6d0e513ff9dc |  | note | Insulation Resistance
label | e40d3ce2-b4ef-5b21-aafb-de02dd14ee17 |  | note | QA check sheets, signed by supervisor, visual inspection and test requirements to AS/NZS 3000:2007, measurements verified
checkpoint-status |  |  | checkpoint | 5.3 Live Testing
label | 1fd8c88f-4276-535c-947a-7ec4f27b59dc |  | note | Polarity
label | 0171dc38-67bb-5c14-a63c-7bb366aba271 |  | note | Phase rotation
label | abb2ac38-41f8-5665-ad48-23c53ecbce68 |  | note | Earth fault loop impedance
label | 7e2ef7e5-6486-5308-aeaa-42d2d099d47b |  | note | QA check sheets, signed by supervisor, visual inspection and test requirements to AS/NZS 3000:2007, measurements verified
checklist-flat | 10ed7224-c711-4507-9897-7f27ab667212 |  | checklist | Combined Services HDPE Fire Pipework Installation |  |  |  |  | Yes | Combined Services HDPE Fire Pipework Installation | e09c19c4-f149-42ee-a51e-24c713d97a1c
checkpoint-status | 8022e9fd-0aa8-40e4-b447-451b1340c5ab |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 697497df-c6fd-4c50-a7ba-01daccadcc52 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b7edc8b5-9cd9-4ab6-badb-3ce5419219ce |  | checkpoint | Inspect trench depth, width and pipe alignment
label | ba51a8d2-8504-5e37-b3ba-d1d60c9f3349 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b066f345-ca72-5060-aa63-a1d2218c4aad |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 8821beff-0771-4f4b-b472-80a336648a61 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 83f5d64d-2c67-449d-804e-409f76640c0f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 19a7d8c9-46b4-45f7-8a92-80b7fba56b53 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 43e9ca16-c620-463b-a4e6-31ff9c21c8e2 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 675a37db-f46f-4999-844b-a19492446763 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 2e7c517a-6630-4d4c-9f35-c39b71dc9d99 |  | checkpoint | Installation of tees and bends
label | 5829e92a-c37e-5b9c-b12c-9750e2b9ec8a |  | note | Install all connection tees as per construction drawings
label | 6b3eea05-4075-56c7-94ff-341987301bca |  | note | Ductile iron bends to be installed on pipework above 300ND
checkpoint-status | bb98b517-ae47-44dd-9126-61d2f259c681 |  | checkpoint | Installation of Hydrants and Hydrant Valves
label | f3b2e1c5-8ef0-5303-9483-9a983e177ad6 |  | note | Mount hydrants on approved types of hydrant tees with risers if necessary so that the top of each hydrant is within 100mm of the finished ground surface level
label | 81829216-8aa1-5604-8fe9-c0a077d8703d |  | note | In-ground hydrants and hydrant valves are installed in secure toby boxes and on isolation spurs.
checkpoint-status | 4fd587cb-7603-4b00-83e1-e114d3ac1749 |  | checkpoint | Install Thrust and Anchor Blocks
label | dd6e72d1-065c-55b8-93e0-97ea38ddba0e |  | note | Minimum dimensions as per IFC drawings.
label | 9645f101-c57a-5f3b-bf48-2e5cbc987eda |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 33bc3bce-aa56-4bb5-9420-3d899912c43d |  | checkpoint | Installation of Trace Wire
label | 5eeda8b3-da8c-5a3e-9923-82b712c44fd6 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 2f79e2d4-5294-58e3-8f5e-b7d3b92ad862 |  | note | Test Trace Wire following installation.
checkpoint-status | 3c335720-2666-47ab-8c1e-0937e7627ff3 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 737feebe-f37b-4742-8fbd-ad0653cea5f2 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 439a9998-c367-5685-8e62-fd18afcd4b86 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 1d153018-38ac-5852-ae19-c7ec6607660b |  | note | Ensure each test length is capped and ball valve installed.
label | beff4f06-94da-5d94-83db-ef98f6d4004d |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 057e71b5-c379-52e2-8b62-bf8d89f736b6 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 393f7ca7-7580-424b-acad-adf968ac53c5 |  | checkpoint | Introduction of Air to 300 kPa
label | 3815b57e-a832-56b4-9683-0ff70760e3cc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 269a0052-2d5a-5769-865d-5cdbb745c26c |  | note | Monitor for any drop-in pressure.
label | ffb241e8-2908-5f9f-b29e-e700fdf574b0 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 30df5c34-da48-446e-be8d-a9f8b5337ebe |  | checkpoint | Increasing Test Pressure
label | 34bba2a1-fc69-5d6a-8b65-f2b4d5467462 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 2c204f13-a04c-4849-a220-22c6afbe940c |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | cd4c256c-d202-4b65-b743-1cad32ad3393 |  | checkpoint | As-Builts Completed.
holdpoint | b5d480b0-8354-4f62-a3ba-04b22a6d7f1f |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Dynamic Flushing Checklist |  |  |  |  | Yes | Flushing - Dynamic Flushing Checklist | e500a8d8-f8c9-4bbc-b1d4-4afdc037a33a
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | 566c4bfa-a547-5eea-baec-be841ba5eac1 |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Turn the pump on and run it at 20 Hz (or at minimum speed)
checkpoint-status |  |  | checkpoint | Increase the pump speed to 50 Hz and measure the total waterflow
text | 931c174c-ce25-526f-bcea-6a3ec10501ac |  | textbox | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Circulate water for 2-4 hours by sampling the drain water quality. Record the duration.
label | 43914555-0892-5f07-954e-79ecaa36d8b8 |  | note | The duration of this process depends on the size of the system and may required to be extended.
text | aa924949-86d3-5c70-beb9-bc84f8023be8 |  | textbox | Duration
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the dynamic flushing
checklist-sectioned |  |  | checklist | Combined Services - Fire Inground Ring Main Pipework |  |  |  |  | Yes | zSYS - Combined Services - Fire Inground Ring Main Pipework (old version) | ec8ad873-4aee-4ade-bab0-c37181fc5bba
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 6517022b-8aae-57ec-9dfb-4542817ab5e8 |  | note | Resp. - CPB
label | cc7685a9-a962-57cc-ba67-99064cba3ca0 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | 5b3ab7c9-dccd-56f5-a6bb-69c3693ebcee |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | 983b6432-266c-5f6a-9386-8ecf6c9b05bb |  | note | Method - Document Review
label | fc7fb250-14d3-53d2-9613-d34299c72b44 |  | note | Frequency - By Building/Site Wide
label | 1c45b1de-51e6-5e0a-be8b-10186456768b |  | note | HP - CPB
label | d68ca3cc-3557-523e-83a3-365761ddb03e |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB Signature
checkpoint-status |  |  | checkpoint | 1.2 - General
label | 112783d0-60f3-5e03-aa51-6e2801a01825 |  | note | Resp. - SE
label | da45884e-bb63-576b-bc4f-eddf68f71c88 |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | e100f8ea-502a-5c51-986e-80d80c2c3a27 |  | note | • NZS 4541:2013
label | 90f2f29e-206b-5105-97ff-4477309a93e2 |  | note | • AS/NZS 2566.2
label | c2585275-490c-51c9-876f-3bce629f89f9 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | e36bea65-8b0a-534e-9b33-2d54264e7113 |  | note | • Specifications & QA Documents Approved
label | 6920b5b5-41f1-56eb-9911-d559d1a833f7 |  | note | • Drawings are confirmed
label | 20ac6dd0-3e27-5717-a627-b7f06fb19499 |  | note | • Equipment fit for purpose
label | 281de2ec-f944-5937-bc57-ba4fb631fa8c |  | note | Method - DR
label | fcefd8af-d012-5892-a170-05186c9c9545 |  | note | Frequency - Each material
label | 0cb2bd6c-6851-5f95-acae-2245410b77ed |  | note | HP - CPB
label | 3e8e2929-f3f8-58e8-a39a-899ec8617537 |  | note | Records - Aconex approval
label | d0745ce1-7618-5ace-9e1e-caf43a00ae38 |  | note | • Incoming Inspection Checklists
label | f26268c2-88e4-59e8-8e3d-1d9f41989e2e |  | note | • Drawing Register
holdpoint |  |  | signoff | CPB Signature
checkpoint-group |  |  | section | 2.0 CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | 2.1 - Accept delivery of pump to site
label | 6ed2a123-f707-51f3-8a0c-9226349e9fff |  | note | Resp. - SUP
label | 2188a5b3-0177-5c9a-9f06-e035a104ff26 |  | note | Referenced Documentation -
label | 6365d820-dcdb-50f2-95f7-89b3570381c6 |  | note | Conformance Criteria - 1. Check pump is rated for pressure test
label | 8382cab1-4a95-562a-949b-b045ba6f40fe |  | note | 2. Check all supplied attachments are correct and in good order
label | 58618485-fc35-5c63-aa41-ada56af1ed14 |  | note | 3. Check fluid levels & fill as necessary
label | 431868ec-0715-5993-831a-ce02573ce87c |  | note | Method - V
label | 3e2a6b56-edf0-579e-880c-b5e6321d3e97 |  | note | Frequency - Once
label | a6206c9a-1d7b-5796-ab50-c9858eb7f102 |  | note | WP - AE Smith
label | 6cab3dd0-2634-5337-ae08-78bd3bd27b43 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 2.2 - Connect pump to Fire ring mains
label | 59fceec5-02aa-5472-9665-b76d1b4d4bf8 |  | note | Resp. - SUP
label | d7b8147c-e9d7-5602-a503-8b495b02ed1e |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | c3124a82-ca3e-5b4e-8b59-2108f9f2ad1b |  | note | Conformance Criteria - Confirm connections are safe and correct
label | d992ef99-86fa-5ff8-9097-652b44bf621c |  | note | Method - V
label | 81a7f326-eb1f-553b-ba8a-d4b6d197e730 |  | note | Frequency - Once
label | 3851a017-4ade-540f-befd-90696bc19ee7 |  | note | WP - AE Smith
label | cede8b64-04c4-58e0-859e-c36a3dc24927 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.3 - Connect calibrated gauges for pressure test
label | 0557cc32-6308-5261-b7eb-f8697731321e |  | note | Resp. - SUP
label | feb86771-312b-5d91-b6ca-bcfd1717f465 |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | e7d44fa2-6267-5855-8575-4d5b6b393d1b |  | note | • AS/NZS 2566.2
label | f229b98f-4a60-5248-8a25-c65ca22f587c |  | note | • Clause 109.2 NZS 4541:2013
label | e3a43ce1-14a4-58d8-a18e-6f6f4d85a8be |  | note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
label | 87639447-30fd-508c-93ec-c8276ae52afc |  | note | Method - V + DR
label | fe86c9c3-78ba-5fac-9880-2c66488eab9c |  | note | Frequency - Each test
label | 8e19e18a-45ee-59c2-ada3-b4d33043d7d2 |  | note | WP - AE Smith
label | b6005dda-4071-581a-92af-70424ed5982b |  | note | Records - Check Sheet + Document
checkpoint-group |  |  | section | 3.0 HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | 3.1 - Fill Fire ring mains with domestic water
label | ea02e5a1-0d46-556b-ad10-f0ae0fdc132d |  | note | Resp. - SUP
label | 56ce310d-5cc1-5bbb-b217-3c8041023872 |  | note | Referenced Documentation -
label | 85d95a20-78f0-5998-8409-455596b49c42 |  | note | Conformance Criteria - Completely fill closed loop system with water releasing all air from the Valves at each Building
label | 2a9b35f3-6d67-59e7-883d-33cb91dc252f |  | note | Method - V
label | edfc2f88-f5a0-5c17-bf6c-d93dfb756d33 |  | note | Frequency - Every time system is opened
label | c0d036b9-f7f4-5225-b733-88f05a792372 |  | note | WP - AE Smith
label | 51240498-03eb-5eb5-84da-e86ce53e4248 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.2 - Gradually increase system pressure to 15.5 Bar
label | bb8985a3-1c05-5dfa-86e0-6f78f6fb2afa |  | note | Resp. - SUP
label | b3f858f4-8b63-5d83-b730-9990cf4f196a |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | 2dc91784-a24b-5cc2-85ae-e7e51a3ac0f1 |  | note | • AS/NZS 2566.2
label | e1b8c905-c6cb-5f93-86f3-2377cedf79a7 |  | note | • Clause 109.2:NZS 4541:2013
label | e0dc7fd1-b40d-585c-ad83-9ebc468c48a3 |  | note | Conformance Criteria - Slowly raise system pressure to 15.5 Bar
label | 22c02e84-75b9-5f1d-a0ed-90c46a98e347 |  | note | • Checking for any signs of leaks or pressure drops
label | 6bce83d0-7826-5572-b082-16ebbe3f7dd5 |  | note | Method - V+M
label | 38b86480-b2fa-5e06-8cda-81ce096f5e49 |  | note | Frequency - Constantly Monitored
label | 890d856b-1d85-5f7f-a684-b4e3037431f9 |  | note | WP - AE Smith
label | 506ad1b7-fd4c-508b-b17a-0d9fd565e910 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 3.3 - Stabilize 15.5 Bar pressure (START WITNESSED)
label | a8dc452d-2ae6-53d2-a079-ec9169346c77 |  | note | Resp. - SUP
label | 6212e418-065b-59a5-b90a-2150439e1592 |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | 2e599b5e-edaf-5296-8273-d66bffa83048 |  | note | • AS/NZS 2566.2
label | 131b945f-fd29-5501-9a9a-1d859939ed42 |  | note | • Clause 109.2:NZS 4541:2013
label | 020862d4-add8-5726-9c67-34445cd3bff6 |  | note | Conformance Criteria - Record START time & photograph gauge
label | f8f9ce34-7660-56a1-80a4-b62eb7b99aa8 |  | note | • All relevant parties to witness starting pressure of 15.5 Bar
label | 647a267c-1796-5546-920c-05c1db6af5a1 |  | note | Method - V+M
label | 7953b452-f9ef-5ccd-b45e-7b04f2bf4a45 |  | note | Frequency - Once
label | f77dd28b-e4bf-5460-8b37-b3c5c2a4c6c2 |  | note | WP - AE Smith
label | 858fe47b-ecd1-5f27-a54c-ca11640cd88f |  | note | HP - AE Smith / CPB / IR
label | 6d25559f-06a0-5f93-b8b9-14bc85c5598f |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | CPB Signature & separate IR Signature
checkpoint-status |  |  | checkpoint | 3.4 - Hold 15.5 Bar pressure for 4Hours (END WITNESSED)
label | 5a6932cd-cc34-55b9-ae63-d0c6fa584cd0 |  | note | Resp. - SUP
label | 1d77bb1b-5d23-5ee1-adbc-4364eda7139e |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 21fda1e0-8c82-5c9d-bb64-fb3419d85c35 |  | note | • AS/NZS 3500.1:2021
label | b69bf6ca-2c9d-5e22-bc45-31bb6d148c66 |  | note | • Clause 109.2:NZS 4541:2013
label | 4515d015-2861-5dc2-98f1-0fef5fc0ef00 |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | a97e7a9d-20e3-5b65-8a8c-3575e0933d72 |  | note | • All relevant parties to witness pressure of 15.5 Bar
label | 0bc98e45-c365-55ac-af43-9572ad150050 |  | note | Method - V+M
label | 1c5f19fe-3ab6-5007-a644-44460e250c2e |  | note | Frequency - Once
label | 0342ac0c-ab33-52a9-92f5-25247c6aa91f |  | note | WP - AE Smith
label | b2554c32-e799-55c9-883b-a5f8c76a6b9c |  | note | HP - AE Smith / CPB / IR
label | 2ce9c0dd-d369-5ac9-9a59-cf616690cd22 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | CPB Signature & separate IR Signature
checkpoint-status |  |  | checkpoint | 3.5 - Pressure released or reduced for next test
label | 1bf2da26-5cf6-53c4-9210-1f33a26f6bd2 |  | note | Resp. - SUP
label | fc285641-1274-5c29-a950-e960f7cb1b7b |  | note | Referenced Documentation -
label | 74019c76-c6cd-5622-8739-217a186b6f1f |  | note | Conformance Criteria - Supervisor to ensure energy (pressure) is only stored while under test
label | 25030100-65c0-5df3-b3d0-c56584450fd0 |  | note | Method - V+M
label | 0d5b59ae-c96e-5732-b1ef-264b5aeb8189 |  | note | Frequency - Once
label | a375188f-c15c-599b-874d-a1fbd20d7628 |  | note | WP - AE Smith
label | 33c4f843-5836-5652-9a7d-b185bd341ac7 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.6 - Discharge pressure leave system in a safe state
label | cfbd38e1-a6d5-5c09-9b03-5c995091c02c |  | note | Resp. - SUP
label | 32a02075-fd1e-5a00-ad67-be3835a31bba |  | note | Referenced Documentation -
label | 3cb3d771-5ce6-5f66-817a-164caaab3ecb |  | note | Conformance Criteria - Discharge system pressure, ensure area is left in a safe state meeting site requirement
label | b0383aaf-439f-586f-b4a4-2350f5f874aa |  | note | Method - V+M
label | b247e491-0ebe-5eb6-aef3-fa029eab06fb |  | note | Frequency - Once
label | 9d796864-e1e7-54f1-b2b2-673ad9907546 |  | note | WP - AE Smith
label | 7609da75-4cf4-5af5-991c-fa45837b075f |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 5.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 12.1 - Testing Results
label | fe4042b0-f7be-5735-b5b7-6b999705d98b |  | note | Resp. - SE SUP
label | d82c2091-6981-54d3-8bbb-0dfea80dd3c2 |  | note | Referenced Documentation - NZT5007-STE-FSSP-0001
label | 63d835de-4643-5558-b10d-0c8a94c0ce0b |  | note | • AS/NZS 2566.2
label | a85a3935-be34-57a5-911d-11c3c195cade |  | note | • NZS 4541:2013
label | 9c877914-804b-5704-ad16-cb3b65116c9c |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | a98308d9-9b1c-59b0-8b94-98e7fda023ad |  | note | Method - DR
label | f23493c1-183d-53f2-a8e5-5d895a69ff0a |  | note | Frequency - Each lot
label | c923b50f-4249-503f-a199-a61081629192 |  | note | WP - AE Smith
label | 79ae645f-004d-5a5d-a177-348df4f86b17 |  | note | HP - AE Smith / CPB / IR
label | d4915432-cd9b-5881-9a26-6206b0414a27 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | CPB Signature & separate IR Signature
checklist-flat |  |  | checklist | Cleaning Agent Removal |  |  |  |  | Yes | Flushing - Cleaning Agent Removal | f4eddc02-4c47-4bea-95e7-8b4115707beb
checkpoint-status |  |  | checkpoint | All sections' valves are opened.
text | 9d24596d-c174-5e62-86dd-8a2ee3b4ace8 |  | textbox | Make-up valve is opened.
text | 59f128f9-5abe-5561-9880-76e98fa3391b |  | textbox | Date
text | 64b0b2ab-a025-5000-b03c-779d1b8b331a |  | textbox | Main drain valve at the pump is open.
text | 47e13fb1-a3f4-539a-897b-b7e9abd04ced |  | textbox | Drain waterflow (l/s)
text | b6e6a7c5-5172-5359-8926-0ec7e7d830fb |  | textbox | Drain location
text | 04b33ba2-f36d-57b0-a7db-c333bef82cfc |  | textbox | Drain duration (minutes)
text | 68252108-dd47-5168-a62f-233e34cbadfd |  | textbox | Calculated drain water volume (L)
text | fc6b2eb5-e887-5bad-a374-0e8ab1731c78 |  | textbox | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Adequate make-up water available. System's static pressure is not decreasing.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Circulate and replace water until the water runs clear.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Cleaning" and dates.
text | c121bd02-9d8e-54ac-9acc-29aca4990050 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
text | 594c75d5-a671-5bef-9889-0b3c9867d992 |  | textbox | Site measurement
text | b6edefad-a02a-5491-b210-5d0284e1f18d |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | b5388a5e-bcb5-5f76-852f-a9aba9141c21 |  | textbox | Site measurement
text | 927436b8-1f64-58e5-b5b0-073ea6355535 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 2a882e19-3c8d-5cd0-8766-aaa4ecf70638 |  | textbox | Site measurement
text | c5c4d89e-d8b5-5d97-89e7-2eb5052191e4 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 5b2c1c8f-be1e-5e19-8025-301bdf9a50a6 |  | textbox | Site measurement
text | be8b7e70-87d4-54df-9cb5-3ae2f770133c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 79c89943-a9ac-53bf-bfa6-3ebb52ab37d8 |  | textbox | Site measurement
text | 7febc4d8-2aea-5d4c-aa80-48cc482b0f17 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 9a53c6d3-76cd-53db-9134-27ceb50dd012 |  | textbox | Site measurement
text | ee66bf8d-98ec-54fd-9694-45daf5e12758 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | a250b1b4-45fc-5f49-b23d-c035f6e49e8e |  | textbox | Site measurement
text | 3d8a3bc6-99a3-5059-9668-0e13c8b1d6a0 |  | textbox | Lab test results
checklist-flat | ad1d1507-e635-45e4-9e37-1960ebadda75 |  | checklist | Communications In-Ground Conduits & Cable Pits |  |  |  |  | Yes | Communications In-Ground Conduits & Cable Pits | f96e7f6e-4a5c-48b5-b281-8b25f6748986
checkpoint-status | f51c13cc-0cb6-4006-8d08-181d7983cfbf |  | checkpoint | ROM & Consent Approval received by the client and approved?
label | f9be281a-0dc9-52b5-9140-21f22a11f1ac |  | note | CPB HP – Document review – Receipt of approval by client
checkpoint-status | 2af82d78-322c-4005-8252-7040d3990ded |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 87df0539-ab05-5882-aec8-899a331faaeb |  | note | Attach: material inspection checklist
checkpoint-status | 22288346-c310-4f38-aea5-4eb7e43b9b9e |  | checkpoint | Location
label | 4776d9ae-18f8-59c2-baa4-d9fd87b417c9 |  | note | Shall be as shown on the drawings,
label | e11edf69-62df-598b-98f4-26f76ba42fed |  | note | Shall be as instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction.
label | 7b0bafcf-82e6-54a7-9f54-870571bfde86 |  | note | Attach: Trench drawing
holdpoint | cf451687-84b5-4ee3-b035-9c3c32eee055 |  | signoff | CPB HP
checkpoint-status | 0c4c9caa-323c-4ac3-99a4-b996bfe94504 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
label | 1e53434b-b263-5f74-b75c-369dcc9b08da |  | note | Attach: Trench handover document & photos
holdpoint | b3488e11-6452-44a9-9294-26e4f9492d4f |  | signoff | CPB HP
checkpoint-status | 7676f718-65a4-498a-9475-4adffb86d443 |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status | ac1226c7-61f2-4d1c-bb73-97b6c29b947d |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
label | 8b8a0451-51e8-5af7-afe1-109e54ff873d |  | note | Attach: Conduit layout drawing
checkpoint-status | 700c9aff-386c-4c3a-9a83-d04dc80e43f3 |  | checkpoint | Location of conduits shall be shown on the drawings.
label | 75bb5670-b89b-5912-b9d2-073bafe52f7d |  | note | Attach: Photos
checkpoint-status | 2e4e2060-339f-4bb7-8e81-5077424ec5f9 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | d4587ccd-8544-441f-a44d-bac769edd006 |  | checkpoint | Bedding of Conduit and Pull-Pits
label | bb21f10d-7905-546b-9c49-17dd95feebd4 |  | note | Conduits and pits shall be bedded on approved bedding material.
label | 3873bef5-8a7a-5e11-9a84-367ec3a4005a |  | note | Bedding material shall be 50mm above and below communication conduits, and 100mm above and below electrical conduits
checkpoint-status | 74bf0840-86ef-411f-90cc-4e97be0046a1 |  | checkpoint | Cable Pull- Pits
label | 7cd605ad-b6f4-53c2-86e0-9d773f1e6dcd |  | note | Conduit entering and exiting a pit shall conform to the locations and dimensions shown on construction drawings and specifications.
label | 45163121-bd5e-520b-8f2d-ee65d800252b |  | note | Where practicable, conduits shall enter and exit a pit at the same height and orientation.
label | f72b249c-17b5-54f6-b61c-4e3741613a3e |  | note | Sealing around conduits where they enter the pit is to be undertaken on the inside and outside of the pit.
label | fcf1212d-394d-54d5-a6eb-a9a5cf596188 |  | note | Attach: Photos
checkpoint-status | 7fb2ab5f-5920-4f76-a0e1-fa73e887b76a |  | checkpoint | Bell mouths to be installed where possible and correctly colour coded.
checkpoint-status | 3c247c8a-4e73-430f-9d99-0d4375c330f4 |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
label | 7edb37cb-c945-59e0-a0fd-9dcca5ad943e |  | note | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 81d28980-84f2-47b0-9d32-0e5a59c17da8 |  | checkpoint | As-built drawings completed.
holdpoint | 69a14e44-a12b-4138-a62a-1cf46ef48b2f |  | signoff | CPB / AES HP – As Built Drawing
checkpoint-status | c0f74fa1-c7d4-4771-91b7-7ebf47adce41 |  | checkpoint | ITP Sign off Witness Points
label | b233b966-d3bb-55f7-8fa0-a49ea3a3d4e5 |  | note | 2.3 Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
label | 8a47ad0e-22d6-5e2f-a1a2-ca95f9c3b63e |  | note | 3.1 Number of conduit dimensions shall be shown on drawings.
label | 48bbb8ba-f6ae-543c-83cc-736cbeca7b1d |  | note | 3.2 Location of conduits shall be shown on the drawings.
label | 3c61a4fc-65d2-5c7b-be05-878d157b1ded |  | note | 3.3 After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
label | 90cff102-2b9e-5249-92eb-ab9256f488fb |  | note | 3.4 Bedding of Conduit and Pull-Pits
label | 5e5113b7-a319-5c45-9f1c-13fb531fd79d |  | note | 3.5 Cable Pull- Pits
label | 84ea446b-d4fe-5ed9-b4b7-52f610929c23 |  | note | 3.6 Bell mouths to be installed where possible and correctly colour coded.
label | 58a96a19-64ab-53ba-98e5-5b49d3ccb460 |  | note | 3.7 A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
holdpoint | 105cf945-05e2-4ca7-ab6a-ae408c868243 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat |  |  | checklist | Chemical Flushing Checklist |  |  |  |  | Yes | Flushing - Chemical Flushing Checklist | fd4909ee-622c-4a6f-b133-7060fd033fac
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | 9809b7e5-aafb-5795-b749-ae876c1a8925 |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
checkpoint-status |  |  | checkpoint | pH
text | 98836ee4-38f4-5feb-a8d1-56aac68d172f |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | 75daa135-44cc-5d19-ac55-3f59fa2885a7 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | b490499c-7c99-50d5-bc43-4c236aae95df |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
text | 6e70d9f9-709c-5574-9c90-df0a028f8c26 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Pump is operating at 50 Hz.
checkpoint-status |  |  | checkpoint | Required cleaning chemical (L)
text | 4391d779-020c-54a4-ba46-821bbc7ad96a |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Cleaning chemical(s) added.
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 8705088d-3b1c-5b42-a092-7bbf9e7e4e63 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | a10a9507-b875-5e8e-93c2-35b03be09bd2 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 8f35a594-23da-5f09-a818-b35b04eedb54 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | pH
text | 5d2a4c3b-4fe4-581b-b1f9-c958aaa3531a |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | d426c58b-9bae-5462-a943-815c9ceaef10 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 9b166ffb-c1e3-581e-8ee1-f52d32456aa4 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the circulation before draining water.
checkpoint-status |  |  | checkpoint | Is there any neutralisation chemical added as per chemical specialist advise? If yes enter name and quantity
checkpoint-status |  |  | checkpoint | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | If this is last section to be flushed, then continue draining process.