## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-sectioned | AES-NZ1005-STE-ITP-PMT-0028 - Tank farm installation |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0028 - Tank farm installation
checkpoint-group | MATERIAL COMPLIANCE
checkpoint-status | RDM & Consent Approval - CPB Hold Point
label | Resp. - CPB
label | Referenced Documentation - RDM Tracker Consent Tracker
label | Conformance Criteria - RDM approval tracker Consent approval tracker
label | Method - Document Review
label | Frequency - By Building/ Site Wide
label | Hold Point - CPB
label | Records - Receipt of Approval by Client
checkpoint-status | General - CPB Hold Point
label | Resp. - SE
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | • Specifications & QA Documents Approved
label | • Drawings are confirmed
label | • Equipment fit for purpose
label | Method - DR
label | Frequency - Each material
label | Hold Point - CPB
label | Records - Aconex approval Incoming Inspection Checklists Drawing Register
checkpoint-group | Installation
checkpoint-status | HDPE Support system & seismic Loops
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-TNK-DSH-SEI-0001 AES-NZ1005-STE-DSH-SEI-0002
label | Conformance Criteria - Check the piping support system has been installed as per the Modframe design
label | Method - V
label | Frequency - Once
label | Records - Check Sheet
checkpoint-status | HDPE installation and testing - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004
label | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-004 for the installation and testing of HDPE pipework
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - CPB
label | Records - FRT +weld test reports +QCC (refer site wide testing check lists)
checkpoint-status | Confirm DCW flushing and disinfection complete - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0001 NZT5007-STE-HSSP-0001
label | Conformance Criteria - Completed with the flushing and disinfection of the site wide ring main Refer to the Flushing and Disinfection commissioning plan
label | Method - V + DR
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - CPB
label | Records - CMP + Check Sheet
checkpoint-status | Confirm Hydrostatic pressure testing complete - CPB/IR Hold Point
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0024
label | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-0024 for Hydrostatic pressure testing
label | Method - V+M
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet + Photos
checkpoint-status | Electrical Installation Complete - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - AEC-NZ1005-STE-SPC-ELE- 0002 AS/NZS 3000:2007 AES-NZ1005-TNK-SHD-ELE-0002
label | Conformance Criteria - HSSB installed. Mains terminated Feeds run to filter controls Feeds run to pump drive board Feeds run to chlorine dosing units Labelled & Tested
label | Method - V + FTR
label | Frequency - Once
label | WP - Ae Smith
label | Hold Point - CPB
label | Records - Check Sheet + COC
checkpoint-status | Chlorine dosing Install & commissioning (Include PRVs)
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | Conformance Criteria - 1. Access is suitable to service dosing equipment
label | 2. All electrical checks are complete and permanent power is on
label | 3. BMS connection is complete by others
label | 4. Pipe work checks are complete
label | 5. Isolation is provided to enable either system to be maintained seperately without affecting the operation of the other
label | 6. Equipment mountings are complete
label | 7. Pressure reducing valves are installed in the correct flow direction and set to desired pressure
label | 8. Dosing control sensors are installed.
label | 9. Non return valves are installed in the correct flow direction
label | 10. Dosing specalist to commission and provide report
label | 11. BMS monitoring is commissioned
label | 12. Confirm treated water meets the requirements of the NZ drinking water standard.
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet + FTR + LTR + CMP Report
checkpoint-status | Domestic Cold water Pumps & Drives
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | Conformance Criteria - 1. Confirm pumps & drives are as approved submission.
label | 2. Installation is as per shop drawings.
label | 3. Motor drive board installed & wiring to pumps complete.
label | 4. All electrical checks are complete and permanent power is on
label | 5. Pipe work checks are complete
label | 6. Pump mounting and vibration pads and seismic restraints are complete
label | 7. Non return valves are installed in the correct flow direction
label | 8. Isolation is provided to allow maintenance of any individual pump
label | 9. Grundfos to commission and provide report
label | 10. BMS monitoring is commissioned
label | Method - V + FT
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet + FTR + CMP Report
checkpoint-status | Primary and secondary Filtration systems
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001
label | Conformance Criteria - 1. Confirm filters are as approved submission
label | 2. Installation is as per approved drawings
label | 3. Pipe work connection checks are complete and without leaks
label | 4. Mountings are complete
label | 5. Non return valves are installed in the correct flow direction
label | 6. Isolation is provided to allow maintenance of any filter
label | 7. Backflow drains provided
label | 8. Southland Filters to test and commission filters and provide report
label | 9. BMS monitoring is commissioned
label | Method - V + FT
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet + M + FTR + CMP Report
checkpoint-status | Motorised control valves
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - 1. Confirm valves are as approved submission
label | 2. Installation is as per approved drawings
label | 3. All electrical checks are complete and permanent power is on
label | 4. Pipe work connection checks are complete and without leak
label | 5. BMS control is opertional- check motorised valve positions in normal and emergency operating modes
label | 6. Plantroom bypass Button is operational – check motorised valve positions in activated and deactivated modes.
label | 7. Check button is clearly labelled.
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | Potable Water Tank Level Control valves
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - 1. Confirm control valves are as approved submission
label | 2. Installation is as per design
label | 3. Float valves are adjusted to to ensure overflow state does not occur
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | Alarm indication on and tank level montoring on BMS
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - 1. Tank level monitors are installed as specified
label | 2. Tank level monitors are connected to the BMS by others
label | 3. Verify BMS level output
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | Back flow preventors
label | Resp. - SUP
label | Referenced Documentation - AS/NZS 3500.1:2018
label | Conformance Criteria - 1. Confirm backflow preventors are as approved submission
label | 2. Installed as per design
label | 3. Pipe work connections are complete and without leak
label | 4. Check flow direction
label | 5. Check strainers are clear 6. IQP test
label | Method - V + DR + FTR
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet + IQP - FTR
checkpoint-status | Wash bay supply & RPZ
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004 AES-NZ1005-STE-ITP-PMT-027 AS/NZS 3500.1:2018
label | Conformance Criteria - 1. Confirm pipe work has been installed, tested, flushed and disinfected as per items 2.2, 2.3 and 2.4 2. Confirm RPZ Back flow preventor has been installed tested as per item 2.11
label | Method - V + DR
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | “As built” drawings
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - 1. Mark up construction drawings with as constructed changes.
label | Method - V
label | Frequency - Once
label | WP - AE Smith
label | Records - Check sheet
checkpoint-group | Completion Testing
checkpoint-status | Works Completion Test WCT 54 - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 54 (e)(f)
label | Conformance Criteria - The EIS for the New Waikeria Facility have been installed in accordance with the FDD. This includes EIS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the following systems: (e) general power; (f) earthing system;
label | Method - FTR + V + DR
label | Frequency - Once
label | WP - AE Smith / LJE
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet + QA documents + COC
checkpoint-status | Works Completion Test WCT 68 - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 68 (a)
label | Conformance Criteria - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the – · pressure test all cold and domestic hot water pipe lines, · operation of all valves, backflow devices, pressure devices; · BMS connections to building management systems; · tank control systems testing; and · water metering testing. Independant reviewer to: (i) Attend and witness a selection of PDS commissioning at the Independent Reviewer’s discretion (Contractor to invite Independent Reviewer to all); and (ii) Receive and review
label | Method - DR + V
label | Frequency - Each lot
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet QA Documents IQP certificates
checkpoint-status | Works Completion Test WCT 80 Potable Water storage tank and Pump - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 80
label | Conformance Criteria - Demonstrate operation of potable water storage tanks and pumps, providing onsite potable water for a minimum of 72 hours at normal demand in the event that mains water supply to the site is compromised. Activate emergency supply remotely with the BMS Independent Reviewer to (a) Attend and witness verification testing. (b) Receive and review documentary evidence of quantity.
label | Method - V+M+FT
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet QA Documents
checkpoint-status | Works Completion Test WCT 81 Tanker connection point - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 81
label | Conformance Criteria - Verify the tanker connection points to the potable water storage tanks are provided. Independent reviewer to visually verify
label | Method - V+M
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet
checkpoint-status | Works Completion Test WCT 82 Loss of mains. - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 82
label | Conformance Criteria - Simulate loss of mains supply by isolating the incoming mains supply. Verify The potable water pump operates to supply water in the event of loss of water supply from the site system. The test will evidence that the valve from the storage tank opens, the potable water pump starts up on generator power, and the pumps ramps up and down to maintain a pressurised potable water main to the New Waikeria Facility Site. Outlets within the New Waikeria Facility Site will be opened to simulate water consumption on the New Waikeria Facility Site. Independent reviewer to attend and witness
label | Method - V+M+FT
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet
checkpoint-group | COMPLETION RECORDS
checkpoint-status | Testing Results
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | Conformance Criteria - All pipework pressure test reports shall be provided
label | Method - DR
label | Frequency - Each lot
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | Dosing system - CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001 DWSNZ-2005:2018
label | Conformance Criteria - Dosing testing and commissioning report shall be provided. Water testing results shall be provided
label | Method - DR
label | Frequency - Once
label | WP - AE Smith
label | Hold Point - AE Smith / CPB / IR
label | Records - Check Sheet, + FTR +LTR
checkpoint-status | DCW Pressure Pump set
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - DCW Pressure pumpset testing and commissioning results shall be provided
label | Method - DR
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet +FTR
checkpoint-status | Emergency water supply activation - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - Verification of emegency water supply activation
label | Method - DR
label | Frequency - Once
label | WP - AE Smith / HWL
label | Hold Point - CPB
label | Records - Check Sheet
checkpoint-status | Manual Bypass Button
label | Resp. - SUP
label | Referenced Documentation - AEC-NZT5007-TNKHSDG-1006
label | Conformance Criteria - Verification of mains supply by passing treatment system by manual activation of plantroom Bypass button
label | Method - DR
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet
checkpoint-status | Backflow Preventors
label | Resp. - SUP
label | Referenced Documentation - AS/NZS 3500.1:2018
label | Conformance Criteria - Backflow testing
label | Method - FT
label | Frequency - Once
label | WP - AE Smith
label | Records - Check Sheet + IQP Test report / Certificate