## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | e00c0aab-3040-4f15-97df-40fd0d805584 |  | checklist | Document Attachment Checklist (V.081021) |  |  |  |  | Yes | Document Attachment Checklist (V.081021) | 0285e834-4383-49ea-b293-e6f9be5167b0
checkpoint-status | ec5816b2-6764-4923-a006-2e832c348d33 |  | checkpoint | Documents attached for reference - Pass once attached
checklist-sectioned | 9cb25932-4b11-4ace-88b6-6e2066407577 |  | checklist | ITP-Rising Mains + Vacuum Test |  |  |  |  | Yes | ITP-Rising Mains + Vacuum Test | 215df766-833a-43ac-a091-204de26b5817
checkpoint-group | 77800b38-2d7c-4469-bfd5-c654f36abda8 |  | section | Installation
checkpoint-status | 955d65e4-7b38-4db1-b4fa-90b53fb70ba2 |  | checkpoint | Latest version of drawings being used for the work - Drawing & Revision No's noted below or photo attached
checkpoint-status | a69804d9-f5e5-45e6-a121-df7d04d8ee2e |  | checkpoint | Rising Mains Type, select type(s) below
boolean | ae19a5ff-8626-5dc4-8d6a-8a5a91bc0789 |  | tickbox | Sewer Rising Mains(SRM)
boolean | 15378041-6300-50aa-8b93-532bb471a3c7 |  | tickbox | Station Drainage Rising Mains(SDM)
boolean | 8f4bc31a-ca49-5a96-9b8c-fb7906af1bce |  | tickbox | Trade Waste Rising Mains(TRM)
text | 9c38f98f-0569-565c-909a-e54807adadf3 |  | textbox | Pipe Size/s
checkpoint-status | 14ec0b77-e489-4d16-b815-2d8eee4f713f |  | checkpoint | Location of pipework as per IFC drawing & CYP site survey set out
checkpoint-status | 156ef1ed-b237-464d-9685-564abc05ad5c |  | checkpoint | Pipe material used are as per Tunnel and Station Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 Rev E)
boolean | d232948a-878c-5861-843b-faeed84e3970 |  | tickbox | HDPE
boolean | 70746a57-371e-506f-8496-6848888cc7d8 |  | tickbox | Cast Iron
boolean | 985d1fc7-1076-5fec-a92e-03d1cff4ddce |  | tickbox | PE
boolean | affc2f7d-f8a1-5dba-bcc2-558c15d92f5b |  | tickbox | Galvanised
checkpoint-status | 0d2f28a7-ea71-46ff-8c6a-fd041856a186 |  | checkpoint | Setout and alignment as per Drawings
checkpoint-status | f00d5a28-6aea-4b02-8d88-9408158dd280 |  | checkpoint | HOLDPOINT - Verify above steps are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | a98b1fcb-7406-41f9-aa6a-6e4a524cbc5c |  | checkpoint | Invert levels as per drawings
checkpoint-status | d3537ddd-fcc6-4cc8-878a-b0d08e3b7082 |  | checkpoint | Pipework on correct grade as per AS 3500.2 Sec 3.4
checkpoint-status | 3d56ec66-bdad-4c93-8a61-c8d7dd5d7c5b |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Sec 4.9.6.2
label | 846da4df-1b14-5953-86f9-67ca64daa185 |  | note | Vertical clip spacing as per AS 3500.3 Sec 4.9.6.2
checkpoint-status | 18a3bd31-0b95-440a-9324-6c3f6949fe87 |  | checkpoint | Brackets Installed Correctly.
checkpoint-status | d9280ccf-b148-40a3-9cfa-75ee69d36374 |  | checkpoint | Correct drainage venting per AS3500.2 sec 3.9 if applicable
label | 45bb953e-1fdb-595b-b708-2f6edc22ab77 |  | note | Attach signature below
checkpoint-status | b481008d-9a92-4d25-889b-b24493c0bf93 |  | checkpoint | Pipework Labelled- Attach Photos below
checkpoint-status | 7b2bd937-a70d-463f-896e-d85b82758279 |  | checkpoint | Heat Trace installed to trade waste
checkpoint-status | 67f4177f-9e96-4abf-91ed-ba2c8a9553c3 |  | checkpoint | All points connected
checkpoint-status | d5bae2f7-f007-49cf-880e-a72332910281 |  | checkpoint | As-built information recorded
checkpoint-status | 2c82de60-45ec-4594-8383-8ca7b1289c65 |  | checkpoint | No damage to pipeworks or fittings - Attach Photos below
checkpoint-status | 1d1b8605-b8c8-468e-b00f-ed84d46f9955 |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | 9fe5c6a3-920a-4bd4-a1ff-d9a26acdbaba |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 5097d22c-571c-507a-9b04-e619aa796b98 |  | tickbox | CDC - General photos/comments attached below
boolean | a17aee9e-624d-5018-bb6a-4a4409a8ab65 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | bf26696e-c678-5830-8ac6-8e87068b4b4c |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 185dec7d-096a-4508-a54a-944c949dd6c5 |  | section | Vacuum Testing on Rising Mains
checkpoint-status | f98dd9b0-ebf9-421f-a400-14c99df6ca98 |  | checkpoint | Test Details- Pass once entered
text | 0e898a05-5848-5880-8535-db6b18295d95 |  | textbox | Location (Area/Level/Zone)
text | f36174e1-2cc9-5bd8-a46f-2ae1300a840e |  | textbox | Testing Calibration Certificate Uploaded Per Level
text | 59eaee70-376a-57d7-b642-1308b8924732 |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | 855080f7-cad2-4b8d-8026-f1b9c2b11dc5 |  | checkpoint | Final Vacuum Test for Rising Mains
label | dd1533b4-ed92-5696-8c96-e05e7f4fa1cb |  | note | Starting pressure -28kPa
boolean | 69e8aeff-fe3b-5c13-91cd-62dd9938f753 |  | tickbox | CDC - General Photos/comments attached below
boolean | 0139fa18-3ac0-5464-acc2-117094cfa8b1 |  | tickbox | CYP Nominated comments - General comments attached below
checklist-sectioned | 33ee743e-0694-4638-b5ae-451ef057aba0 |  | checklist | ITP-Drainage & Vents + Air Test |  |  |  |  | Yes | ITP-Drainage & Vents + Air Test | 2a442ecf-ae9f-457c-a479-38a3e6064142
checkpoint-group | 4ef49188-c248-436f-922f-9a7218b936e0 |  | section | Installation
checkpoint-status | 5c349f10-fe6c-4f26-bf12-5b2ea4939a78 |  | checkpoint | Latest version of drawings being used for the work - Drawing & Revision No's noted below or photo attached
checkpoint-status | 449a3953-01ea-4dbb-940d-98174942ab66 |  | checkpoint | Drainage Type, select type(s) below
boolean | 0356250c-be8d-5f81-a182-08313552058c |  | tickbox | Sewer Drainage(STP)
boolean | 5417920d-82e2-50d0-b1e0-5d74ad7ed045 |  | tickbox | Station Drainage(SDR)
boolean | 21fbb749-ae02-54ce-936d-4930a3aaf1aa |  | tickbox | Trade Waste Drainage(TDW)
boolean | 9ab167eb-520a-548d-ba11-a90956d2a443 |  | tickbox | Storm Water Drainage (STW)
boolean | 17e5c65c-ef32-5838-826f-adabc39b61c3 |  | tickbox | Sewer Vents (SVP)
boolean | dcffaf39-5805-5e7a-b4ca-f525e056d2b3 |  | tickbox | Station Vents (STV)
boolean | 8de21873-0846-5863-a14d-e68174661112 |  | tickbox | Trade Waste Vents (TWV)
boolean | b6f69337-c6f4-5fe2-8da3-c26bb3e83db3 |  | tickbox | Trade Waste Chamber Vents (TCV)
text | c37357e8-ef37-5a55-8c5a-aa713175d86a |  | textbox | Pipe Size/s
checkpoint-status | b4b2bd5c-a4db-4a27-89b9-490a3913bd23 |  | checkpoint | Location of pipework as per IFC drawing & CYP site survey set out
checkpoint-status | 001ecb39-2b42-402b-b918-5094ae8ca160 |  | checkpoint | Pipe material used are as per Tunnel and Station Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 Rev E)
boolean | 84f11f80-4cb4-5cdf-9174-59aa6b230b5f |  | tickbox | HDPE
boolean | 3c49c2e0-294b-51be-ba68-c21aa1b39e28 |  | tickbox | Cast Iron
boolean | 468bf738-223e-5e84-a715-b672f242e6f8 |  | tickbox | PE
boolean | 066209ce-c816-53b6-9073-88e5c6b526fa |  | tickbox | Galvanised
checkpoint-status | c326c77b-f77b-45ac-a8ea-66c34b639f21 |  | checkpoint | Setout and alignment as per Drawings
checkpoint-status | b89f6402-9428-467f-a3f4-5e5f04042743 |  | checkpoint | HOLDPOINT - Verify above steps are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | d249d4c4-de6e-4f56-b5a6-b1b357ca65be |  | checkpoint | Invert levels as per drawings
checkpoint-status | 05d03d50-9944-49e7-91e8-efd65b215446 |  | checkpoint | Pipework on correct grade as per AS 3500.2 Sec 3.4
checkpoint-status | f7951461-37de-4cba-81bf-c951e2086bff |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Sec 4.9.6.2
label | daea490a-5810-5e49-9559-70c489459ea9 |  | note | Vertical clip spacing as per AS 3500.3 Sec 4.9.6.2
checkpoint-status | 187b69e8-cee4-4d0b-80dd-ab6ee969ddba |  | checkpoint | Brackets Installed Correctly.
checkpoint-status | 41b6498c-09b4-4575-bca1-90ba862fb7f1 |  | checkpoint | Correct drainage venting per AS3500.2 sec 3.9 if applicable
label | 8e450a26-89d7-577a-b4c6-644a369a38a4 |  | note | Attach signature below
checkpoint-status | 1f2adf8a-f729-4e0e-8a1f-d10a2a038a89 |  | checkpoint | Pipework Labelled- Attach Photos below
checkpoint-status | 76ee10f6-601d-4790-81b0-636dc46c9592 |  | checkpoint | Heat Trace installed to trade waste
checkpoint-status | 6f5c45e0-04a1-488f-a6d5-30fc6381ecd0 |  | checkpoint | All points connected
checkpoint-status | 946c5eb0-1af8-410e-8fca-5dca0c916466 |  | checkpoint | As-built information recorded
checkpoint-status | d69150f7-241d-4600-aecd-6f8a0b0d9ebc |  | checkpoint | No damage to pipeworks or fittings - Attach Photos below
checkpoint-status | 6ab03e24-344c-4edd-b930-82fa8dd247cc |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | a814e3f0-17a1-43c6-8bed-8e38d251a773 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | fc89cb75-efba-59ee-91a8-c0e5db917e05 |  | tickbox | CDC - General photos/comments attached below
boolean | c2c977c3-8b0d-5ebc-8a77-5ceaca879933 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | dbb5faaf-c1bf-58a5-8b6f-168e80f5a911 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | c6f6f0ff-d576-4bef-99ae-ef4b9edf4a1f |  | section | Air Testing on Drainage
checkpoint-status | 024be24d-4a36-4487-bdbd-b92210cc37ad |  | checkpoint | Test Details- Pass once entered
text | 4a8f2b0c-30aa-5063-a0a1-8d85eb45a7f2 |  | textbox | Location (Area/Level/Zone)
text | ca37e291-6704-54b0-8935-127cd8c0da03 |  | textbox | Testing Calibration Certificate Uploaded Per Level
text | 64e39abb-5517-5f9d-a505-0ff93d7e674b |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | 8a020634-39c2-4800-81a6-74ead8aa1eca |  | checkpoint | Final Air Test for Drainage
label | fb9d17eb-9ba8-54ec-a11b-cd511a9b1bcd |  | note | Minimum 15 kPa
boolean | a8388e1b-7d74-58b7-bb3a-8de8e5d66b91 |  | tickbox | CDC - General Photos/comments attached below
boolean | 5e3ad965-5a54-5365-afcb-66be439bef44 |  | tickbox | CYP Nominated comments - General comments attached below
checklist-sectioned | 8b212b2e-e90c-47f4-8d55-691e39b50794 |  | checklist | ITP-Gas + Pressure Testing |  |  |  |  | Yes | ITP-Gas + Pressure Testing | 2ddbe895-b9d3-4e83-9307-2803cc04e0d7
checkpoint-group | 36bcd081-88c0-4ced-953f-c9dfcffcb421 |  | section | Installation
checkpoint-status | 983c964d-c917-481a-874d-659fe939afae |  | checkpoint | Latest version of drawings being used for the work - Drawing & Revision No's noted below or photo attached
checkpoint-status | 6deb657f-220c-4b0d-8dde-b324afb1e4b0 |  | checkpoint | Service Type, select type(s) below
boolean | a4441e73-036d-5572-add7-f5958f432d6f |  | tickbox | Natural Gas (NAG)
text | f7fe0842-009a-50e1-a9ce-34a354d4f7b3 |  | textbox | Pipe Size/s
checkpoint-status | 7d5ea115-154f-4b22-8c59-db2ced67bb74 |  | checkpoint | Location of pipework as per IFC drawing & CYP site survey set out
checkpoint-status | a5769e08-cf23-48e1-9961-1e9209538cae |  | checkpoint | Pipe material used are as per Tunnel and Station Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 Rev E)
boolean | 8d47cc2c-d1c3-52a2-a862-9970b36dcab8 |  | tickbox | PE
boolean | cb1d6668-9a75-58ea-8154-27801f3316a6 |  | tickbox | Copper Tube
boolean | 652a775b-648f-5f6b-a2f6-a8295d427c26 |  | tickbox | PE-X
checkpoint-status | ddfce5ab-61d3-440b-811e-0abef992f06e |  | checkpoint | Setout and alignment as per Drawings
checkpoint-status | da7046cf-64df-48fb-9578-b437fcb5d572 |  | checkpoint | HOLDPOINT - Verify above steps are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | 83b069cd-36f2-4e3c-a2f5-52698b1ead72 |  | checkpoint | Inverts and Grades as per Drawings
checkpoint-status | 2d107dd9-0415-4de6-96a2-98fd9d4db1c6 |  | checkpoint | Brackets Installed Correctly.
checkpoint-status | 98317e44-9309-481c-9aa7-2345564a5ca2 |  | checkpoint | Pipework labelled- Attach Photos below
checkpoint-status | 23e18028-f3d8-499b-b0ab-09b6f77d90dc |  | checkpoint | Heat Trace installed to Hot Water as per drawings,if required
checkpoint-status | 414d5089-16ef-460e-8acf-1279ec9e856b |  | checkpoint | All points connected
checkpoint-status | 27651d14-4a8e-4adf-b4b3-ad96fe569ced |  | checkpoint | As-built information recorded
checkpoint-status | ad924f7c-e021-4071-a747-1df212161771 |  | checkpoint | No damage to pipeworks or fittings - Attach Photos below
checkpoint-status | 288dd858-faf4-4f18-b269-5de28793a6ad |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | f743f40c-3af6-488f-a504-12ed1ac6d06d |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 75212970-7cc8-5e4e-bf24-4b917724f6bc |  | tickbox | CDC - General photos/comments attached below
boolean | a6fde9e1-97d7-5bc3-a011-969b5d259d33 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 6b020d1a-ed9f-5fb2-b2e6-e5561bfb8bae |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 69af025b-3013-4f14-a343-abe7a8a774df |  | section | Pressure Test
checkpoint-status | c4a0aa6d-7e94-47bc-9f99-9dff308af80d |  | checkpoint | Test Details- Pass once entered
text | f34be5ca-b64f-5207-bb6d-546e7edb02a2 |  | textbox | Location (Area/Level/Zone)
text | dfec0e4a-5816-5177-ae03-613f502f69f0 |  | textbox | Testing Calibration Certificate Uploaded Per Level
text | 437656d3-1e82-56e7-bad7-40c908158e4a |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | c3ba466d-361b-467a-804b-e899a9827e30 |  | checkpoint | Final Pressure Test
label | 6b0f2aa7-38eb-53f9-a22e-76663d7eefc5 |  | note | Test at 7kPa or 1.5 times the operating pressure whichever is greater. As per AS5601.1 2013
boolean | 5ff98fa9-3b7d-5926-9fbb-32f3df6b8300 |  | tickbox | CDC - General Photos/comments attached below
boolean | 12a33d17-bfe6-510a-aa32-8e633130de5f |  | tickbox | CYP Nominated comments - General comments attached below
checklist-flat | 48d244d7-219c-4d54-8c0f-ff2090712127 |  | checklist | ITP-Fixture Fittings |  |  |  |  | Yes | ITP-Fixture Fittings | 39c9868c-d9c8-4a69-bb4f-2846a6972f27
checkpoint-status | bce6bf6b-e952-46b9-9bbf-634843111cad |  | checkpoint | Service & Fitting types (list)
text | 137789ab-1156-5ad1-91d9-c1820d10a940 |  | textbox | Fitting list
checkpoint-status | eba099cf-97a1-4cdf-bcab-676308362876 |  | checkpoint | Correct items installed as per approved specifications
checkpoint-status | f65510ef-d0a2-46b4-bcc8-594e10838551 |  | checkpoint | No apparent damage- free of cracks,chips, crazing or other defects - Attach Photo below
checkpoint-status | 300d0102-868b-4765-8d5f-0c87f8974546 |  | checkpoint | Sealant is neat. Correct type, colour and volume
checkpoint-status | 97322f52-6050-459e-a3ba-c7fbd9b22220 |  | checkpoint | Fittings are installed straight, Carry visual inspection
checkpoint-status | ef435d00-02e9-4643-a3a0-07159005cc1b |  | checkpoint | Access panels are installed as per approved product installation drawings
checkpoint-status | b04cf709-6868-4573-8459-b7fe1ca6cfed |  | checkpoint | WC's fixed with levelling brackets after floor installation, seat lid secure if applicable
checkpoint-status | 55a713b0-56eb-42f1-a04e-958d49182e92 |  | checkpoint | Check each item for operation-hot and cold water if applicable.
checkpoint-status | 66264329-de5b-432a-b4de-894fd7f3f243 |  | checkpoint | All points connected
checkpoint-status | 6e322488-1f5e-4af0-97b9-e32be88f48e1 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 1fb1d64b-af78-5d7b-9b7f-ca5f1d045d82 |  | tickbox | CDC - General photos/comments attached below
boolean | b38b41ff-44fe-51cf-b4ba-9ec4bd62e4d7 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 120b5dcd-1ef0-5a02-8d5e-122bc112db5a |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checklist-flat | edd14db6-2725-48a3-bc65-fc62d1d911d1 |  | checklist | Commissioning (V.061221) |  |  |  |  | Yes | Commissioning (V.061221) | 525e7340-bf62-4ca9-af78-ec5563c12daf
checkpoint-status | 65f0a668-4bad-4aeb-a8ae-20f7ae811f31 |  | checkpoint | Check products for imperfections
checkpoint-status | e973e895-5e52-4110-bb59-fab6deb84924 |  | checkpoint | Fixtures location & ixings all correct (as per drawings & samples)
checkpoint-status | 13307686-3cf6-48ed-a098-f3177765dd19 |  | checkpoint | Clean out all strainers / aerators
checkpoint-status | 67fd507c-6a69-464e-9d59-6a6536e0a395 |  | checkpoint | Check for no cross connections / leaks / access to isolation valves
checkpoint-status | d4397630-b2e0-4526-89bd-5251c14be162 |  | checkpoint | Floor wastes (clear of debris & draining correctly)
checkpoint-status | 8863b44b-54a4-4339-8126-ced64152f5cd |  | checkpoint | Quality of silicone seals to fixtures acceptable
checkpoint-status | a5cbb75c-6539-4d39-87cd-9e1059383e1f |  | checkpoint | Hot water tempering valve set to 50c (+/- 5c) & DDA thermostatic mixing valve set to 42 degrees.
checkpoint-status | e3a75b0b-7ce6-4074-bd9d-430d05f71c62 |  | checkpoint | Water pressure acceptable 350Kpa to 500 Kpa
checkpoint-status | dfbd7a0c-52c8-4e9b-ab00-55bdc7e7d78d |  | checkpoint | Hydraulic Work(s) completed to specification/drawings & Area left clean/tidy
label | f742363a-ebc0-57a8-a848-3ad2a31e205b |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 39cbcaa3-6d12-5b3a-a7fe-8841f76ddf64 |  | note | Click to Attach Signature(s) below
button | b9191a12-48d2-5b30-91f7-8dc651fde593 |  | button | Signature by Builders Site Coordinator | Yes, No
button | 353f317a-3fb9-58ea-9874-f01620d9b4b6 |  | button | CDC Plumbing Signature Sign-Off added below | Yes, No
checklist-flat | 5855af73-d402-4cfb-8c7e-0c2a7ed7be2d |  | checklist | Hydrostatic Pressure Test |  |  |  |  | Yes | Hydrostatic Pressure Test | 5e851ed5-93bb-4f6e-beb8-3c389d916bc4
checkpoint-status | d8705e9f-0ec8-41d9-9b1c-1b6ae787f49e |  | checkpoint | Test Details - Pass once entered
text | a46e979c-e11d-59eb-914e-80e4acde035d |  | textbox | Location (Area/Level/Zone)
text | 69ff2014-bc1e-5c14-bc44-b16862bc7e55 |  | textbox | Testing Calibration Tested Date
text | adef5b79-2375-5d7b-8f6b-e7a7642d6efa |  | textbox | Testing Calibration Due Date
text | 142d44ff-8ea5-53c7-ab8e-42187c4c8406 |  | textbox | Service
text | d7972519-8ed7-54c3-b099-82af51845a1c |  | textbox | Testing Apparatus Type
text | 173e4fe4-8e00-5244-8066-ddc6eeed76ba |  | textbox | Testing Apparatus Number
checkpoint-status | 6a74b58b-def9-4eb8-8921-dd6d695641d2 |  | checkpoint | Preliminary Sectional Air Test to 15kPa
checkpoint-status | 85bea043-e15d-41d6-92d6-a1a575182554 |  | checkpoint | Final Hydrostatic Test
text | 40f8085c-a71b-5225-91b2-fc88c931ad02 |  | textbox | Test reading kPa
checklist-flat | 85b7e71a-94f8-4e33-b793-9477a89640ae |  | checklist | Cast-Ins/penetrations CYP Checklist Number CHK/MMTS/00810 |  |  |  |  | Yes | Cast-Ins/penetrations CYP Checklist Number CHK/MMTS/00810 | 6033783b-623e-4ad5-91db-940ab5dab3d2
checkpoint-status | ce2d8350-e2fc-49f7-ae56-e093a0627b5c |  | checkpoint | Are the latest Version of the drawings being used for the work. Ref: 7.3.1 & 7.3.2 section on Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001)
text | 1f99e359-787a-5ad8-9667-67f4b7ebea48 |  | textbox | Drawing number
text | 820c4ab6-bc6f-5242-a26a-e1e82cdfe41a |  | textbox | Revision
checkpoint-status | fd35507e-37c2-4457-9ba0-fde8a9cb3550 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out Ref: 8.1.5 & 8.3.3 on Hydraulic Services Specification
select | ef4d35ad-274d-5c30-9155-32ad9b0484c6 |  | dropdown | Drain / Penetration type | Permanent,Provisional
checkpoint-status | 955b0a2d-03dc-41f6-b2d0-e291654436ed |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
select | 1c620945-18e3-554e-a198-d39c2dbc2c8a |  | dropdown | Pipework material used. Ref : 7.9.1 section on Hydraulic Services Specification | HDPE,Cast Iron,Poly
checkpoint-status | d01a8959-aa08-4f1a-86fa-32fef0299804 |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
label | ad31a986-604e-5a0d-986a-9eed6468a70a |  | note | Visualised by Nominated CYP Authority Only (CYP NA2- Proficiency Level 2)
boolean | 263de90d-0287-57d9-a474-82d76525678e |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | 4a03cd75-9cd2-4d28-aef1-2ee6f336082f |  | signoff | HOLDPOINT - CYP to Verify steps 1 to 6 are compliant with applicable supporting documentation
checkpoint-status | e6262f74-1a76-4119-b451-8b9da900ff92 |  | checkpoint | Invert levels as per drawings Ref: AS3500.2.2015 Table 3.4.1 and 8.3.8.4 in Hydraulics Services Specification
checkpoint-status | 8984b3fd-3d94-4bea-b5be-46a94cdea69c |  | checkpoint | No damage to pipework or fittings. Ref: Attached Photos below
checkpoint-status | 5bebdcd4-cfc1-4ab3-808c-d16518579eb2 |  | checkpoint | Correct drainage venting per Ref: AS 3500.2 2018 sec 3.9
checkpoint-status | 203f8533-1da8-41bc-881e-feb134eed4c9 |  | checkpoint | Correct fire protection / fire collars as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | 4a43b444-df4c-4dab-9fd0-6c2c580e351d |  | checkpoint | Type & Brand of collar used as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | eb78479f-a08a-4595-8e4d-96e6125c82fa |  | checkpoint | All points are connected
checkpoint-status | 9be6ebd9-7bf4-475a-8c83-08ad9ea794b5 |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1 and 8.3.8.4 on Hydraulics Services Specification
checkpoint-status | 2eae51e5-9492-42b4-93a8-9727c2efc7ed |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued Ref: As Per manufacturers requirement
checkpoint-status | 708c007c-de4e-4ec8-a48e-62cde55057eb |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued) Ref: As Per manufacturers requirement
checkpoint-status | 08c6d24a-b945-4561-9139-4c879238b033 |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | 51aad7c4-b9e3-4420-8562-e36e24182e79 |  | checkpoint | Pressurised pipework to 15 Kpa according to AS3500.2 Sec 15 and Ref: 8.1.9, 20.3.6 & 20.3.8 on Hydraulics Services Specification
label | f05efb5d-04fa-5771-a5fb-b5205d3413f6 |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | e3f3cfd5-1774-4d6b-bae4-235d07b579a6 |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
boolean | 712f6c4c-8ff4-5c9e-9920-07a71210501b |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
label | ac8d3e43-6b35-5c21-a1a2-2f567239c251 |  | note | Visualised by Nominated CYP Authority Only
holdpoint | 03dc6b09-c3d8-48ca-aac8-48398d196910 |  | signoff | HOLDPOINT- CYP Nominated Authority sign off test
checkpoint-status | 9319fbf2-1e27-4ea6-afda-f030981d6849 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | b934a841-c564-4512-9328-b9a053ee7db7 |  | checkpoint | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 416782e8-285c-4de7-8036-1cf5364a7eaa |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 7c0ccfd2-98b7-5508-aaab-a50d10ce491d |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | a44c7e41-534b-40a2-a605-ca0303b71be2 |  | checkpoint | Pipework to remain full of water during pour. Ref: As Per manufacturers requirement
checkpoint-status | f0ad4df0-00dd-4fc5-a900-e6fab24a0ea9 |  | checkpoint | Has pipework been picked up for completed works (As-built)
checkpoint-status | 68f6d73a-e3de-4f2d-955e-ff7b846a17ab |  | checkpoint | Signoff - CDC to sign before passing this checkpoint
boolean | 48a12645-36fd-51dc-b7e4-7cabe1ee3a55 |  | tickbox | CDC - General photos/comments attached below
label | 13628fe2-4917-57da-80e0-3c6591ebe213 |  | note | SIGN-OFF :Name & Signature attatched below
holdpoint | 6748bb34-ee07-448a-b350-a9c312d86499 |  | signoff | FINAL HOLDPOINT- CDC authority to signoff
checkpoint-status | fb183ed2-5d10-4940-bbc6-d0611d75f9a1 |  | checkpoint | Signoff - CYP to sign before passing this checkpoint
boolean | e1d34617-52b8-5ed5-aa9e-c12fe01fb3c1 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 200c9f84-1e14-53cd-9c4a-67377817ae8a |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | 0c8c85cc-2b6a-41ae-8ff8-cdb0b1cf8019 |  | signoff | FINAL HOLDPOINT- CYP nominated authority to signoff
checklist-sectioned | c33578e1-d6a6-4f39-a8bb-6c11a071514e |  | checklist | Cast-in/Peno + Hydro Test (COMBINED) V.010322 |  |  |  |  | Yes | Cast-in/Peno + Hydro Test (COMBINED) V.010322 | 6baa6efa-7797-4eae-b622-5e5d9721b382
checkpoint-group | bf205879-6b47-4212-ac6b-f6fcd4ca83a1 |  | section | Cast-Ins/penetrations CYP Checklist Number CHK/MMTS/00810
checkpoint-status | cdf0b03d-6405-4b0d-a3de-420ff946d9af |  | checkpoint | Are the latest Version of the drawings being used for the work. Ref: 7.3.1 & 7.3.2 section on Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001)
text | e4bcdf11-e8da-556b-af0f-3e57aa8ebba0 |  | textbox | Drawing number
text | 914e58f6-b28b-540e-914b-05108376386a |  | textbox | Revision
checkpoint-status | e316f6d8-4741-4dc5-aedc-3af66cfbce82 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out Ref: 8.1.5 & 8.3.3 on Hydraulic Services Specification
select | 3dceeaf2-925a-5123-b739-9a212ae93ea9 |  | dropdown | Drain / Penetration type | Permanent,Provisional
checkpoint-status | 1deea372-7691-4148-8467-d0fc9054e1cc |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
select | d731832d-dcd9-5e5b-8255-455bb71e323b |  | dropdown | Pipework material used. Ref : 7.9.1 section on Hydraulic Services Specification | HDPE,Cast Iron,Poly
checkpoint-status | 2a8d43dc-94eb-4fee-a9fb-ba2f56a74168 |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
label | 0f9b1e62-f4de-5faa-8b7b-e8a5374ebd0a |  | note | Visualised by Nominated CYP Authority Only (CYP NA2- Proficiency Level 2)
boolean | 9bd6e42c-6e35-5313-a533-4fd7ad70c3cf |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | 8715d0c9-ee46-400e-8119-ab37b210ae96 |  | signoff | HOLDPOINT - CYP to Verify steps 1 to 6 are compliant with applicable supporting documentation
checkpoint-status | e5a2677d-9ba2-49ba-bc4b-73bbd468a2e3 |  | checkpoint | Invert levels as per drawings Ref: AS3500.2.2015 Table 3.4.1 and 8.3.8.4 in Hydraulics Services Specification
checkpoint-status | 2e8707e3-ca25-4fc8-9a94-180a57dec478 |  | checkpoint | No damage to pipework or fittings. Ref: Attached Photos below
checkpoint-status | e8153c1a-9d38-454b-bc67-d983d74f0c22 |  | checkpoint | Correct drainage venting per Ref: AS 3500.2 2018 sec 3.9
checkpoint-status | 39d10b4f-0b86-4e0a-a45a-38564b947504 |  | checkpoint | Correct fire protection / fire collars as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | ea093143-31ab-476a-9ed5-20e8bef818f4 |  | checkpoint | Type & Brand of collar used as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | 4b4c1259-aeaf-4070-9e15-d86c9efce54a |  | checkpoint | All points are connected
checkpoint-status | 8166e3f8-d795-438d-96e2-f3fe965c97ec |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1 and 8.3.8.4 on Hydraulics Services Specification.
checkpoint-status | 119b94c5-d326-4e7c-ac14-ae6e6132095e |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued Ref: As Per manufacturers requirement
checkpoint-status | acb58366-2c38-4941-902a-a72a5c77b8c0 |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued) Ref: As Per manufacturers requirement.
checkpoint-status | 64402f96-b510-4e68-a243-32653316b4c0 |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | 4928254e-bc65-4bf6-8d64-106cdae46b6b |  | checkpoint | Pressurised pipework to 15 Kpa according to AS3500.2 Sec 15 and Ref: 8.1.9, 20.3.6 & 20.3.8 on Hydraulics Services Specification
label | f4a63497-40d2-5057-962d-fc775052f997 |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | 54b04138-5b83-447a-ab84-1b3ca6f46918 |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
boolean | d11698b4-e5ab-5634-b9b4-1b168c14b34b |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
label | 65cfaa18-4853-5490-81ab-6ff5aaf2a921 |  | note | Visualised by Nominated CYP Authority Only
holdpoint | fbfde8d4-9e31-4533-9e8f-7f40f8f53a86 |  | signoff | HOLDPOINT- CYP Nominated Authority sign off test
checkpoint-status | 9e560b4e-8953-4e65-8487-051f642fb235 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | acfd6c1f-a2da-41a3-aaab-d40409ccafa2 |  | checkpoint | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 3c0d5db3-6028-4888-9cb7-0b781750b051 |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 1c7d236d-55c9-5f1d-b0d5-0d3bc8624876 |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | 465d0c9a-ff80-4c48-a1e9-9730773c8c7b |  | checkpoint | Pipework to remain full of water during pour. Ref: As Per manufacturers requirement
checkpoint-status | f1d6b0e3-bd81-4e05-b71a-0276259688be |  | checkpoint | Has pipework been picked up for completed works (As-built)
checkpoint-status | 2c9ea592-bffb-4b8a-9753-74f194268ce2 |  | checkpoint | HOLDPOINT BELOW - CDC to sign before passing checkpoint
boolean | eada05fe-7f39-5e16-8c98-96bfa4332216 |  | tickbox | CDC - General photos/comments attached below
label | 39f0a56e-016e-5a86-9eb2-565935dbd9fa |  | note | SIGN-OFF :Name & Signature attatched below.
holdpoint | db1a2574-2e7b-4413-9794-e691911cc74a |  | signoff | FINAL HOLDPOINT- CDC authority to signoff
checkpoint-status | 579bec89-2e82-4623-a44c-0943e4bf14e6 |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
boolean | b3432292-f5bf-5bc9-8d34-6357163c6fc2 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | b34ec8bb-7cca-5fd3-a5b5-afdb40fcea7a |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | 37bcac37-7e57-49ef-89a8-56ac0235dcd8 |  | signoff | FINAL HOLDPOINT- CYP nominated authority to signoff
checkpoint-group | 84f569ba-52f8-4655-857d-4d1e60dfbb19 |  | section | Hydrostatic Pressure Test
checkpoint-status | 4dcb4bed-6549-44a8-95f6-6facab9a69d4 |  | checkpoint | Test Details - Pass once entered
text | 011538dd-589a-57ec-aeff-3357fcc95dea |  | textbox | Location (Area/Level/Zone)
label | 4cb61ab9-269a-51f6-9630-f58573b9b48c |  | note | Testing Calibration Certificate Uploaded Per Level
text | 3ade032a-5584-5b5f-a4c7-1fac7530ab3a |  | textbox | Service
text | 823445c3-94e4-5b16-9359-77c187d16f1a |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | 10f4042a-fbdb-43a1-8486-f59c2fd89d90 |  | checkpoint | Final Hydrostatic/Pressure Test
label | 4921e220-ded9-5a1f-a755-d3baa256f8ec |  | note | Pressurised pipework to 15 Kpa according to AS3500.2 Sec 15 and Ref: 8.1.9, 20.3.6 & 20.3.8 on Hydraulics Services Specification
boolean | 447dfa50-e468-5090-aeb8-eccfd2f7b513 |  | tickbox | CDC - General photos/comments attached below
boolean | 8e6fbc04-22cd-5ed2-8da3-a283db8045c7 |  | tickbox | CYP Nominated comments - General comments attached below
checklist-flat | 92b70383-39bc-46b7-9531-b0d9c62cb27a |  | checklist | Cast-Ins/penetrations ITC-01 |  |  |  |  | Yes | Cast-Ins/penetrations ITC-01 | 7e694d0b-bd94-4b90-a876-aef9eaea541c
checkpoint-status | c14e32dd-927a-4ff8-95d4-c0118cecf97a |  | checkpoint | Are the latest Version of the drawings being used for the work
text | 77660ccb-3310-52e0-873c-7cf74f1ebbed |  | textbox | Drawing number/s are noted on ITP
checkpoint-status | 8750c011-bc94-4595-80b1-dcf8028868cd |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out
button | f063fa9f-1f46-542c-abc5-06fdf6ce585b |  | button | Drain / Penetration type | Permanent, Provisional
checkpoint-status | 6da67979-8175-4e5a-a8eb-8d63fb296347 |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
button | 663280e6-dfca-5b6d-9d12-7d07b1a67ebb |  | button | Pipework material used | HDPE, Cast Iron, Poly
checkpoint-status | 829ee81a-6793-462a-88a0-fdd6ff2c0969 |  | checkpoint | HOLDPOINT - Verify steps 1 to 6 are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | c31380b3-bd4b-4fa1-8415-a0fb608467bb |  | checkpoint | Invert levels as per drawings
checkpoint-status | ef11a26c-690f-4fad-9d4e-0b42726a746c |  | checkpoint | No damage to pipework or fittings - Attach Photos below
checkpoint-status | d7517eaa-b99b-44b2-839a-90ecf29e1d63 |  | checkpoint | Correct drainage venting per AS 3500.2 2018 sec 3.9
checkpoint-status | 193bde97-8ca9-44e5-a6b5-4d6f38198d06 |  | checkpoint | Correct fire protection / fire collars as per C3.15 of the BCA AS4072.1
checkpoint-status | 6fee1ea4-164a-4872-9e4f-9defc641a596 |  | checkpoint | Type & Brand of collar used
checkpoint-status | 993083f7-25c7-428e-9551-84b86d90e357 |  | checkpoint | All points are connected
checkpoint-status | 1d140431-792a-493e-8989-be107c34fe11 |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1
checkpoint-status | 74ab99f2-a324-4caa-bd83-f64f87562c22 |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued
checkpoint-status | 068a70a4-d5b8-4673-ae21-8190e75fcbe8 |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued)
checkpoint-status | 0d716b83-d0c7-41d2-b7b8-07aa35d9fec0 |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | f85e712f-4d88-4dd6-9cbf-3a8339b84010 |  | checkpoint | Pressurised pipework to 15 Kpa
label | 4a716b16-0c66-577a-8d4e-8f2180d811e4 |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | d326f4f7-fec8-4d7a-a2fb-dc5b8d8eebcc |  | checkpoint | Hold Point - CYP Nominated Authority sign off test
label | 093e059c-2e6f-54a7-9a0e-ae23f9da51b1 |  | note | Attach Signature(s) below
checkpoint-status | 15cb0048-69dd-4d8b-810d-9199b941f723 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
label | dc86250d-2506-5373-94c1-fbadc788f9ee |  | note | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 001ef846-7caa-4a7f-95fc-9b1913702e5a |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 2713b8ee-e626-5714-aae0-770898ebbaf7 |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | 8bba5e88-63f4-40f7-941b-25d95ad3e55e |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | d8d27684-a47d-4459-a680-80849397730a |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 9a9e1906-72e7-53a1-86b2-38ebf55a5daf |  | tickbox | CDC - General photos/comments attached below
boolean | 1bf5ae57-8297-5d04-bd2b-919d4853178e |  | tickbox | CYP Nominated comments - General comments attached below
boolean | f8ca00c6-b1e5-5ff5-8766-a4a8dfa94b9f |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checklist-sectioned | 0c7a9c4e-ffa2-4c10-845f-81d71f8cf2cb |  | checklist | ITP-Drainage + Flush Test |  |  |  |  | Yes | SYS - ITP-Drainage + Flush Test | 9c47c72a-4864-40c0-af01-448c5e4de62f
checkpoint-group | 311007c5-1dda-4494-bb59-c8b0fdd8c057 |  | section | Installation
checkpoint-status | 83b81e17-2557-4790-a50a-8bb09670f41d |  | checkpoint | Latest version of drawings being used for the work - Drawing & Revision No's noted below or photo attached
checkpoint-status | f4785893-b4f6-4367-8f09-e46642ec0c0f |  | checkpoint | Drainage Type, select type(s) below
boolean | 0356250c-be8d-5f81-a182-08313552058c |  | tickbox | Sewer Drainage(STP)
boolean | 5417920d-82e2-50d0-b1e0-5d74ad7ed045 |  | tickbox | Station Drainage(SDR)
boolean | 21fbb749-ae02-54ce-936d-4930a3aaf1aa |  | tickbox | Trade Waste Drainage(TDW)
boolean | 9ab167eb-520a-548d-ba11-a90956d2a443 |  | tickbox | Storm Water Drainage (STW)
boolean | 17e5c65c-ef32-5838-826f-adabc39b61c3 |  | tickbox | Sewer Vents (SVP)
boolean | dcffaf39-5805-5e7a-b4ca-f525e056d2b3 |  | tickbox | Station Vents (STV)
boolean | 8de21873-0846-5863-a14d-e68174661112 |  | tickbox | Trade Waste Vents (TWV)
boolean | b6f69337-c6f4-5fe2-8da3-c26bb3e83db3 |  | tickbox | Trade Waste Chamber Vents (TCV)
text | c37357e8-ef37-5a55-8c5a-aa713175d86a |  | textbox | Pipe Size/s
checkpoint-status | be6539a8-3a65-46f1-a729-f72818c8cea5 |  | checkpoint | Location of pipework as per IFC drawing & CYP site survey set out
checkpoint-status | fe16f8d9-8aa8-4fb4-91ea-9085096147d1 |  | checkpoint | Pipe material used are as per Tunnel and Station Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 Rev E)
boolean | 84f11f80-4cb4-5cdf-9174-59aa6b230b5f |  | tickbox | HDPE
boolean | 3c49c2e0-294b-51be-ba68-c21aa1b39e28 |  | tickbox | Cast Iron
boolean | 468bf738-223e-5e84-a715-b672f242e6f8 |  | tickbox | PE
boolean | 066209ce-c816-53b6-9073-88e5c6b526fa |  | tickbox | Galvanised
checkpoint-status | 1742a30c-851c-4365-8c63-addf173c3bd0 |  | checkpoint | Setout and alignment as per Drawings
checkpoint-status | e478f135-ee71-495a-a2c6-d931c29f65bd |  | checkpoint | HOLDPOINT - Verify above steps are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | c19abfce-c468-4c84-bc0b-e740d602d8f9 |  | checkpoint | Invert levels as per drawings
checkpoint-status | ad3fa78d-6b0c-41d2-ac6e-2d364cf32de1 |  | checkpoint | Pipework on correct grade as per AS 3500.2 Sec 3.4
checkpoint-status | 2e940f88-2218-45a6-b22d-d70b2c1ce5fe |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Sec 4.9.6.2
label | daea490a-5810-5e49-9559-70c489459ea9 |  | note | Vertical clip spacing as per AS 3500.3 Sec 4.9.6.2
checkpoint-status | 9f87f731-2c24-4280-a129-544def1b4577 |  | checkpoint | Brackets Installed Correctly.
checkpoint-status | 1e800449-8abd-45ca-95c2-ffe33cf800be |  | checkpoint | Correct drainage venting per AS3500.2 sec 3.9 if applicable
label | 8e450a26-89d7-577a-b4c6-644a369a38a4 |  | note | Attach signature below
checkpoint-status | 9cd0ecec-c36f-4314-9b74-46450fbc92d8 |  | checkpoint | Pipework Labelled- Attach Photos below
checkpoint-status | 59c871a3-2b90-497b-bb59-edae7d5b1707 |  | checkpoint | Heat Trace installed to trade waste
checkpoint-status | 7227ffbe-1ea9-41d8-afda-453f9aa99e2f |  | checkpoint | All points connected
checkpoint-status | 22901361-66aa-477f-9464-341c45e9453c |  | checkpoint | As-built information recorded
checkpoint-status | b9b18c46-f507-493d-a751-8de980912ff6 |  | checkpoint | No damage to pipeworks or fittings - Attach Photos below
checkpoint-status | c801c114-9c04-4dbf-9910-ea5a43f54f08 |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | a35e6d44-a9aa-41a8-9d8c-df244f32a002 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | fc89cb75-efba-59ee-91a8-c0e5db917e05 |  | tickbox | CDC - General photos/comments attached below
boolean | c2c977c3-8b0d-5ebc-8a77-5ceaca879933 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | dbb5faaf-c1bf-58a5-8b6f-168e80f5a911 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checklist-sectioned | 2538cd7d-f15b-4c37-9b29-e6a9aae9a64d |  | checklist | (Enter Pour # or Cast-In details) Test 2 |  |  |  |  | Yes | SYS - (Enter Pour # or Cast-In details) Test 2 | a890fd36-8262-4adc-8fea-ea08696c624d
checkpoint-group | 797cd6c8-dab2-46a1-8c13-2d0fc48b7eb5 |  | section | Cast-Ins/penetrations ITC-01
checkpoint-status | b940f0e5-4032-432f-b41f-ca8645ade337 |  | checkpoint | Are the latest Version of the drawings being used for the work
text | bd495977-b42b-43db-a471-20a4d12298d2 |  | textbox | Drawing number/s are noted on ITP
checkpoint-status | 6f9feb6c-8049-4caf-9099-fd8983f78e07 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out
button | e052772c-dab7-4664-9c2e-37df47641f2f |  | button | Drain / Penetration type | Permanent, Provisional
checkpoint-status | 3bd5540e-a26f-4045-9f7f-0ac01e3bbdee |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
button | d7ebff4b-36fb-4377-aa5f-ac777bc6f815 |  | button | Pipework material used | HDPE, Cast Iron, Poly
checkpoint-status | fc47d9cd-7a32-499d-a72b-0f1d4857f14f |  | checkpoint | HOLDPOINT - Verify steps 1 to 6 are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | 9fd64e36-cc96-4917-81ee-05e55359e981 |  | checkpoint | Invert levels as per drawings
checkpoint-status | ad72fef5-fbb8-451a-9946-52c26717c96b |  | checkpoint | No damage to pipework or fittings - Attach Photos below
checkpoint-status | 00417d7a-f2df-420c-9912-64778d763a2c |  | checkpoint | Correct drainage venting per AS 3500.2 2018 sec 3.9
checkpoint-status | 9c3f8c1a-f50c-41f5-8c44-c0230b682dea |  | checkpoint | Correct fire protection / fire collars as per C3.15 of the BCA AS4072.1
checkpoint-status | 37f060e2-f3db-496f-8c7c-a773459e2ff2 |  | checkpoint | Type & Brand of collar used
checkpoint-status | 81d5d4f4-bbd7-4071-b642-34759b120bff |  | checkpoint | All points are connected
checkpoint-status | 0d4d3da0-b5ea-48c9-8da1-4a1eb32aac95 |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1
checkpoint-status | 75dc175c-415f-4af6-94da-8ccabb4efc9d |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued
checkpoint-status | 5d548cab-71e5-46ce-a912-c40144ca9867 |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued)
checkpoint-status | 8643ad30-ce06-4a5b-a19f-9a9444d3eefc |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | a98af15b-01dc-45d2-b83a-6662abebcc49 |  | checkpoint | Pressurised pipework to 15 Kpa
label | b6f959c1-7547-459c-adc2-7cbcf730c9f9 |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | 62e7975a-b619-42ae-a48c-bc7bf3c52ca5 |  | checkpoint | Hold Point - CYP Nominated Authority sign off test
label | 50e1e89c-dd6c-4c5f-b68d-c55ae7867463 |  | note | Attach Signature(s) below
checkpoint-status | b58dea9c-eba9-487a-b757-1be23ff2e5ba |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
label | 80006d58-e45b-40e0-bbca-e37a7ca1321f |  | note | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | f7899660-5f61-4019-ada8-a2be840860ce |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 49c7b626-80d5-44a2-982a-97fa2f8387bd |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | e2c2dbf7-cd94-4c86-8f08-52fc80e6031c |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | 69cfebf6-9664-4956-a942-d2bd0bf0041c |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 3a7f991f-00f0-438c-a004-c83c32b00d53 |  | tickbox | CDC - General photos/comments attached below
boolean | 1c3c87ad-787f-40f3-b09b-29acb5f9bb39 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | bb76f190-037e-406b-81c7-ac70fc8d7877 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 07b9e73b-aed5-4ce2-a79c-952ff1c2ac3b |  | section | Hydrostatic Pressure Test
checkpoint-status | 1a763822-02a3-4ad6-8418-3b0a6957cdbb |  | checkpoint | Test Details - Pass once entered
text | 3e86feff-40bc-4519-b00f-9df76281bee5 |  | textbox | Location (Area/Level/Zone)
text | b3f2eb7d-6e95-49c6-9d2e-743880ce87ff |  | textbox | Testing Calibration Tested Date
text | 929591cb-291b-4a97-b50d-2cf5e252a1c9 |  | textbox | Testing Calibration Due Date
text | 2a8fba82-cfc2-4bc5-844e-6977b0db6ac7 |  | textbox | Service
text | 2557366c-eb22-457c-ba38-f93dc47b1930 |  | textbox | Testing Apparatus Type
text | 6afbadf8-4e4d-40cf-b546-58a3553d76f5 |  | textbox | Testing Apparatus Number
checkpoint-status | b9994f12-2b2b-458f-8bcf-7072db25366a |  | checkpoint | Preliminary Sectional Air Test to 15kPa
checkpoint-status | 52b0c2c6-52b5-439b-9622-5243da0a08dc |  | checkpoint | Final Hydrostatic Test
text | 0e452ed7-5d9c-418a-8a6c-d10b7dd21924 |  | textbox | Test reading kPa
checklist-flat | 7a271a6d-ef9d-408f-a9d5-b543bc6c0838 |  | checklist | Document Attachment Checklist V.010322 |  |  |  |  | Yes | Document Attachment Checklist V.010322 | ac5e4c27-2a68-4d8a-b5ca-7bf874643a33
checkpoint-status | eef7d320-71d9-45b7-808a-cd8e0ee9eee3 |  | checkpoint | Documents attached for reference - Pass once attached
text | 415b3ef6-fc70-587c-a4b3-ef1b627bb9b7 |  | textbox | Drawing No. and Revision noted below
checklist-sectioned | c7cf85da-3683-4b97-a27c-cb36eca23a88 |  | checklist | Peno's 1 (Vertical elements) |  |  |  |  | Yes | SYS - Peno's 1 (Vertical elements) | af6319a1-8412-4740-a687-460f6372c1f7
checkpoint-group | 9f060188-fce3-4d25-9cfc-08e7416202a9 |  | section | Cast-Ins/penetrations ITC-01
checkpoint-status | c9dc2559-fcb8-4047-872d-71252a27f56e |  | checkpoint | Are the latest Version of the drawings being used for the work
text | bd495977-b42b-43db-a471-20a4d12298d2 |  | textbox | Drawing number/s are noted on ITP
checkpoint-status | 5cb734f5-7bd1-4895-9044-b0e576f88981 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out
button | e052772c-dab7-4664-9c2e-37df47641f2f |  | button | Drain / Penetration type | Permanent, Provisional
checkpoint-status | 4772b439-1a85-4383-988c-f84e49763b1a |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
button | d7ebff4b-36fb-4377-aa5f-ac777bc6f815 |  | button | Pipework material used | HDPE, Cast Iron, Poly
checkpoint-status | 46cd0fae-bdc6-493b-b77e-767b71545f9a |  | checkpoint | HOLDPOINT - Verify steps 1 to 6 are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | 8337adfc-9c60-4733-81c1-ae3e225a83fd |  | checkpoint | Invert levels as per drawings
checkpoint-status | ba89a466-3237-4519-9144-ec48017ccf05 |  | checkpoint | No damage to pipework or fittings - Attach Photos below
checkpoint-status | d1f82002-9468-4c66-b0de-db7c4a1b0a64 |  | checkpoint | Correct drainage venting per AS 3500.2 2018 sec 3.9
checkpoint-status | 617edd7d-9663-41ea-8bad-d89fb3633db0 |  | checkpoint | Correct fire protection / fire collars as per C3.15 of the BCA AS4072.1
checkpoint-status | 51437271-2642-4e5a-9a7a-83db06cb274e |  | checkpoint | Type & Brand of collar used
checkpoint-status | 401870d4-e3af-43ee-af0b-b651b07ea1c7 |  | checkpoint | All points are connected
checkpoint-status | 501d50a0-1836-4494-8d35-512c8ddabe4c |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1
checkpoint-status | df3a36ae-c3f3-40ee-9217-fd3f288d3c92 |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued
checkpoint-status | 469af371-2bdd-4528-af2a-eaa69301d294 |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued)
checkpoint-status | 3cdca11b-f7cc-40aa-a07c-1b6679c3db7d |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | c573ff75-31f7-4209-b9d2-677a3cc2fb45 |  | checkpoint | Pressurised pipework to 15 Kpa
label | b6f959c1-7547-459c-adc2-7cbcf730c9f9 |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | 595a33ee-9efc-48a6-bf73-0dc484a72536 |  | checkpoint | Hold Point - CYP Nominated Authority sign off test
label | 50e1e89c-dd6c-4c5f-b68d-c55ae7867463 |  | note | Attach Signature(s) below
checkpoint-status | 4f1192b0-4058-4dc8-9267-b7f8ccc8f0f8 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
label | 80006d58-e45b-40e0-bbca-e37a7ca1321f |  | note | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | a0c3bdb8-20b0-4a5d-924a-ec9c375ac4ce |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 49c7b626-80d5-44a2-982a-97fa2f8387bd |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | b1f6dd8b-a2a7-48d4-b83a-638d6e3fd97c |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | 39147955-f51d-4e5a-ac9e-426df483aba1 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 3a7f991f-00f0-438c-a004-c83c32b00d53 |  | tickbox | CDC - General photos/comments attached below
boolean | 1c3c87ad-787f-40f3-b09b-29acb5f9bb39 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | bb76f190-037e-406b-81c7-ac70fc8d7877 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 48925a9c-fc0f-4e9a-b3dd-53776514c475 |  | section | Hydrostatic Pressure Test
checkpoint-status | 1bc46289-b50a-40b3-919c-d1433eb2b520 |  | checkpoint | Test Details - Pass once entered
text | 3e86feff-40bc-4519-b00f-9df76281bee5 |  | textbox | Location (Area/Level/Zone)
label | 0d2ad449-24c8-41af-bf24-ab11f6b14669 |  | note | Testing Calibration Certificate Uploaded Per Level
text | 2a8fba82-cfc2-4bc5-844e-6977b0db6ac7 |  | textbox | Service
text | 2557366c-eb22-457c-ba38-f93dc47b1930 |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | 9080e4c6-cb6e-42a4-abc8-d888eb556455 |  | checkpoint | Final Hydrostatic/Pressure Test
label | b1ad7940-5dba-4442-b79c-881399bea393 |  | note | Minimum 15kPa
checklist-flat | dcd04125-d173-4218-a7d2-13518426f703 |  | checklist | Cast-Ins |  |  |  |  | Yes | SYS - Cast-Ins | bc9d3516-54ce-475d-a783-a972a0966fe5
checkpoint-status | a8e60c91-324d-4fce-80c9-ed29915b67b6 |  | checkpoint | Are the latest Version of the drawings being used for the work
text | 7525c773-c968-5120-844a-b660130cb797 |  | textbox | Drawing number/s are noted on ITP
checkpoint-status | 711bce2b-3c05-4893-ab8d-7ea5cd91bcff |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out
button | bd32dc49-1cc7-50c2-b675-387a6e659f77 |  | button | Drain / Penetration type | Permanent, Provisional
checkpoint-status | c644379e-ccc0-4817-b6eb-2b100f7ab93b |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
button | 796b243d-0a9c-52cc-b90e-15ef4ee60b23 |  | button | Pipework material used | HDPE, Cast Iron, Poly
checkpoint-status | 5f1afbc7-b6c2-4b9f-90cf-674453436e19 |  | checkpoint | HOLDPOINT - Verify steps 1 to 6 are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | 4639fc79-0729-43c0-9024-edd769d3390e |  | checkpoint | Invert levels as per drawings
checkpoint-status | 66af7ab9-8f97-4d30-a961-b1cd45c1bb25 |  | checkpoint | No damage to pipework or fittings - Attach Photos below
checkpoint-status | c0ea1634-3ecb-4e5b-9bc5-ebe4351a7d30 |  | checkpoint | Correct drainage venting per AS 3500.2 2018 sec 3.9
checkpoint-status | 24c1ab47-7e08-4b59-b63c-3395489467fb |  | checkpoint | Correct fire protection / fire collars as per C3.15 of the BCA AS4072.1
checkpoint-status | 8d203c01-506f-40cc-a359-e190f94bc08c |  | checkpoint | Type & Brand of collar used
checkpoint-status | f3f41270-13aa-40ce-a0e4-55a8ac28ae41 |  | checkpoint | All points are connected
checkpoint-status | 44730f2d-2696-477d-962d-a67b4791fe95 |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1
checkpoint-status | 60c262cb-a76f-451c-af59-4886d7cc9ad3 |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued
checkpoint-status | 2bdeb7e7-db72-4dc0-88eb-1feebdafccbe |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued)
checkpoint-status | 4488186d-ad46-4ab6-8bb0-922462c7fe3a |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | cb0675e9-d239-4de4-b7b2-1b1fb54e1f0b |  | checkpoint | Pressurised pipework to 15 Kpa
label | df2f4394-3549-5945-9c47-c020efaecb9f |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | 578b7bd9-f586-4a28-9388-0dbaae67b36c |  | checkpoint | Hold Point - CYP Nominated Authority sign off test
label | 7243a5fc-8ef2-5cc1-90fe-41463aadeb1e |  | note | Attach Signature(s) below
checkpoint-status | 250cfdd5-f2e3-4636-81da-6d43d62f4909 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
label | 0fe595b7-c099-5de3-87c7-0bd99dc48932 |  | note | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 223efb48-3198-4808-a55f-5477ac135133 |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | ebe25767-37c4-5a90-9eb9-0ca5390a90e8 |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | ce7fc30d-5a7d-4327-87ef-58827ef53c10 |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | 4324ac1b-6870-4b72-8924-6d66430183b5 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 4b7431b5-a86a-5dfd-9b14-e6aa01605044 |  | tickbox | CDC - General photos/comments attached below
boolean | 9837415f-f89f-582a-a661-95400e3bb072 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 932334c1-60b8-52a1-9b78-5554e53140a0 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checklist-flat | 58170520-cecd-4e66-87f1-c7be0df013c9 |  | checklist | Hydrostatic Pressure Test |  |  |  |  | Yes | SYS - Hydrostatic Pressure Test | bce9f3ad-28d0-4612-a290-dea085afc806
checkpoint-status | 7d022e13-f3d4-49b6-9803-3c2cf715599d |  | checkpoint | Test Details - Pass once entered
text | 4eb1f699-54ea-5054-a99a-17da72f703b2 |  | textbox | Location (Area/Level/Zone)
text | 74df036d-8a76-5f06-bf4a-efac245143fc |  | textbox | Testing Calibration Tested Date
text | 46c63206-2f69-510b-87fd-85377628b6e3 |  | textbox | Testing Calibration Due Date
text | 08ceb692-00ef-54a5-b0cb-5df2a755ded6 |  | textbox | Service
text | 848c0b3a-ab17-5b35-976a-62f6711625a1 |  | textbox | Testing Apparatus Type
text | 258d59d6-9cd6-5ab1-b045-c4f2c3809863 |  | textbox | Testing Apparatus Number
checkpoint-status | aa9eb1f8-afea-45a3-8e06-013f23e04577 |  | checkpoint | Preliminary Sectional Air Test to 15kPa
checkpoint-status | 7c9dab1c-9bcf-483e-a0ec-429a8f8c103b |  | checkpoint | Final Hydrostatic Test
text | 75f275b5-c7f7-524c-94ba-6d3ef796b414 |  | textbox | Test reading kPa
checklist-sectioned | 8006d446-d2cc-41c9-8061-cda0ad6feced |  | checklist | Cast-in/Peno + Hydro Test (COMBINED) |  |  |  |  | Yes | Cast-in/Peno + Hydro Test (COMBINED) | d3169e1f-89ee-47a8-b81b-42a91dee678c
checkpoint-group | 4d5d5478-75c8-4cfc-b9fe-c9ea1156c577 |  | section | Cast-Ins/penetrations
checkpoint-status | 28e4da2a-ce62-4c84-a082-15b9361e10fc |  | checkpoint | Are the latest Version of the drawings being used for the work
text | 01e0ca6b-4a77-567d-af99-8822269a40ea |  | textbox | Drawing number/s are noted on ITP
checkpoint-status | c0e9686e-ccaa-4de6-a27d-1f7acf27f6f3 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out
button | b0f85438-6d9f-5a4e-80a7-63556358ac4d |  | button | Drain / Penetration type | Permanent, Provisional
checkpoint-status | c4cb0eed-3472-47a5-8d49-b76db0e97bd7 |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
button | 5a8a843e-3f4b-5e84-94f2-df3515ee116b |  | button | Pipework material used | HDPE, Cast Iron, Poly
checkpoint-status | 0486ed48-213f-4636-9da1-17ec6b5a4b5f |  | checkpoint | HOLDPOINT - Verify steps 1 to 6 are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | ad09c860-1a4a-4a04-aa84-9cb4485a0660 |  | checkpoint | Invert levels as per drawings
checkpoint-status | 4dea3f06-95ad-47fd-b966-1a6e1fa9fa90 |  | checkpoint | No damage to pipework or fittings - Attach Photos below
checkpoint-status | b228db10-6374-480f-8b54-100691469df5 |  | checkpoint | Correct drainage venting per AS 3500.2 2018 sec 3.9
checkpoint-status | 64781aac-c4c7-4c3b-9313-2e4a5f7c8e64 |  | checkpoint | Correct fire protection / fire collars as per C3.15 of the BCA AS4072.1
checkpoint-status | 3fb0b292-3222-4fa8-a81f-d3ffabda4839 |  | checkpoint | Type & Brand of collar used
checkpoint-status | c5f2fd6b-3e59-4b9f-bca2-09add813e93f |  | checkpoint | All points are connected
checkpoint-status | 0886211a-2e85-4fb8-b86b-eda0c95f28bf |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1
checkpoint-status | be140ccd-99cd-4620-a9d1-ac29f890069f |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued
checkpoint-status | 95f87774-01f0-48bd-bf82-cc072bad38be |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued)
checkpoint-status | 1ecfcd81-b179-4b6b-aed2-089fad3ad5b0 |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | 2a940fa7-883b-4bc4-819a-d090df0eb261 |  | checkpoint | Pressurised pipework to 15 Kpa
label | a3ab1876-52db-5cad-bfca-5a15264f696d |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | b98dbcee-e980-4b59-a4ec-f2d55c4933ba |  | checkpoint | Hold Point - CYP Nominated Authority sign off test
label | ace3be10-e793-5353-8538-d424ece6051f |  | note | Attach Signature(s) below
checkpoint-status | eeacb3ea-27f5-43ff-86f2-d2a7095967e3 |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
label | 1274fe35-47f5-5dc5-9908-6ef0c3ef3abc |  | note | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 2ac670a4-db2b-49e6-a2e1-1327741d6d70 |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 8a815ca0-f047-5df3-956b-cb5db0373eb6 |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | 93010a42-1279-47b9-834a-059deae31c0d |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | 975a3685-f619-4606-9e6f-da88c64a57fa |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 65d3cd1d-1b93-5b40-b315-86753fc89bb5 |  | tickbox | CDC - General photos/comments attached below
boolean | 1583c299-93c0-5d6a-bd2f-866aa735e164 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | b7f0cd16-1180-544d-8e5b-6f12fd1bbfcd |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 822d2413-c152-4deb-a90b-9481b05cf249 |  | section | Hydrostatic Pressure Test
checkpoint-status | c1f0d3ef-b1ee-4bcf-b134-1011baf54c1b |  | checkpoint | Test Details - Pass once entered
text | 41ccc5cc-5f71-56b5-b5bb-b4b623b255dd |  | textbox | Location (Area/Level/Zone)
label | e88a9186-d10b-54db-b88c-284ab462d223 |  | note | Testing Calibration Certificate Uploaded Per Level
text | 1e028284-2933-5c8f-bdad-0ca5864d30c0 |  | textbox | Service
text | dd45a018-3af3-5235-a4a8-7c69a47e0228 |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | 1a744a6c-e15d-40dd-9dc1-fe194cb8e27f |  | checkpoint | Final Hydrostatic/Pressure Test
label | 1fbc79aa-a7c3-5a3e-94fe-2e20e75949bc |  | note | Minimum 15kPa
boolean | 3195b146-b147-5553-8a8d-58802c80cfcd |  | tickbox | CDC - General photos/comments attached below
boolean | 2556e642-875b-58b1-a858-437725e560a8 |  | tickbox | CYP Nominated comments - General comments attached below
checklist-flat | 033695ed-cc1d-48fb-93a7-f2a5f0d777c0 |  | checklist | Hydrostatic Pressure Test V.010322 |  |  |  |  | Yes | Hydrostatic Pressure Test V.010322 | e452fcd1-bc7e-4e71-878e-bda3373d2d2c
checkpoint-status | 3d8273f4-3372-4a1c-a248-d9c98f30e42c |  | checkpoint | Test Details - Pass once entered
text | 2b2824c1-3a5a-589d-a351-41cb21ad6bc3 |  | textbox | Location (Area/Level/Zone)
text | 37ac218e-b812-5f4d-9050-bffd0eff6e67 |  | textbox | Testing Calibration Tested Date
text | 62cbd57f-46f0-5bf0-a299-7fb180649b3a |  | textbox | Testing Calibration Due Date
text | 9697cfdf-6725-5c3f-b6cd-f9be79e20251 |  | textbox | Service
text | 73530e3c-8e5a-5d33-9533-db2fde80e61a |  | textbox | Testing Apparatus Type
text | 5f588f2c-45fd-543d-b8c2-f1fc4f1b0e8e |  | textbox | Testing Apparatus Number
checkpoint-status | 4c0e514c-e5db-4beb-939c-98e4ad2979e2 |  | checkpoint | Preliminary Sectional Air Test to 15kPa
checkpoint-status | 27aba6a0-43d8-40aa-b25b-1e722021370f |  | checkpoint | Final Hydrostatic Test
text | 9acbc071-3cae-5b3c-8bcf-0706e073159e |  | textbox | Test reading kPa
checklist-sectioned | 43e96614-5150-4570-b81a-d35d71604cbe |  | checklist | ITP- Water + Testing |  |  |  |  | Yes | ITP- Water + Testing | e7b9bc60-3254-4fdc-83d0-2701e1f5ff8c
checkpoint-group | 82993c29-745e-4080-a0bf-0f6c46645d2e |  | section | Installation
checkpoint-status | 119ac793-3e8d-47fe-b39d-e45e2028c7b5 |  | checkpoint | Latest version of drawings being used for the work - Drawing & Revision No's noted below or photo attached
checkpoint-status | 0702f6df-a4de-40bc-93b5-68a08b8c8ceb |  | checkpoint | Service Type, select type(s) below
boolean | f0af82b6-eec1-5ac3-ba2a-dd45c83e9831 |  | tickbox | Domestic Cold Water(DCW)
boolean | 2fdef0dc-5ab5-5b84-81da-7b3058bca87c |  | tickbox | Domestic Hot Water(DHW)
boolean | e3bfb0b3-2fde-55f1-bad9-f657e640456d |  | tickbox | Domestic Tempered Water(DTW)
boolean | 1bf35996-b3e7-53f4-8692-4754cb4881f0 |  | tickbox | Treated Recycled Water(TRW)
boolean | 5e68e83f-4595-5f39-9aff-e8177b1fed64 |  | tickbox | Fire Test Water(FTW)
boolean | 1dba4032-9453-55f5-927f-df9260c28fb7 |  | tickbox | Priming Pipe(PRP)
text | cfefe9fe-2a8a-581d-bbf7-78d97e689dc5 |  | textbox | Pipe Size/s
checkpoint-status | c037aacf-e997-40a9-bcf5-3be16ff368e3 |  | checkpoint | Location of pipework as per IFC drawing & CYP site survey set out
checkpoint-status | 5fe21f08-f36c-402c-b760-ac7b92be787e |  | checkpoint | Pipe material used are as per Tunnel and Station Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 Rev E)
boolean | 7e017b84-cbf5-5cdd-a1c2-640057b6d15d |  | tickbox | PE
boolean | 98b1e10a-5103-5b61-af73-8ab20032f9c7 |  | tickbox | HDPE
boolean | e0048b1d-3a28-5db2-b1bd-30ed94616ed9 |  | tickbox | Copper tube
boolean | 7d3e3a86-7921-5def-bf15-62bcfbdfa7dc |  | tickbox | PE-X
boolean | 07f98cb6-9cc5-5fd9-91b9-623e0adf5ede |  | tickbox | Other
checkpoint-status | cbeff464-c798-4299-a7c4-16487b012501 |  | checkpoint | Setout and alignment as per Drawings
checkpoint-status | 5cfe1e80-5a07-4044-8b08-31ac29fb8d1a |  | checkpoint | HOLDPOINT - Verify above steps are compliant with applicable supporting documentation. Visualised by Nominated CYP Authority
checkpoint-status | 3ba3d62d-5bb5-4cce-9f55-0c85658dbb7d |  | checkpoint | Inverts and Grades as per Drawings
checkpoint-status | 1f7e71cf-c013-454d-8c35-589adacdbe52 |  | checkpoint | Brackets Installed Correctly.
checkpoint-status | 5bfc2be7-761c-4d10-817c-e6889973e15c |  | checkpoint | Pipework labelled- Attach Photos below
checkpoint-status | eb3e7fb7-ed78-4c43-bc8c-b716e55b6380 |  | checkpoint | Heat Trace installed to Hot Water as per drawings,if required
checkpoint-status | d6ae8aa3-6f3b-4499-9a5f-9b58b77f4e56 |  | checkpoint | All points connected
checkpoint-status | 45d5f024-8a30-4203-8a44-bc9518b72b54 |  | checkpoint | As-built information recorded
checkpoint-status | 05a81aee-a0d9-4463-afcc-c15d7f45bf1b |  | checkpoint | No damage to pipeworks or fittings - Attach Photos below
checkpoint-status | c63ffdf6-b2a2-4430-bbfe-7f6d772386eb |  | checkpoint | Has excess pipework been picked up for completed works
checkpoint-status | ab857f6e-d584-4a0a-a3a8-0c097d6b1ef5 |  | checkpoint | FINAL - Pipework completed to specification/drawings - Area left clean & tidy
boolean | 79f221b9-0e86-57bb-b4ca-5275881ffd7c |  | tickbox | CDC - General photos/comments attached below
boolean | 91b0099b-be34-5a38-b006-41bc8bb74c00 |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 729e2f61-10a8-58ee-b11f-7c4239c718d6 |  | tickbox | SIGN-OFF - CDC & CYP Nominated Signature(s) attached below
checkpoint-group | 96fd2b9c-60d1-43c3-a5ae-3f35dcf4afc8 |  | section | Hydrostatic Test
checkpoint-status | f81b8245-93b9-43ed-bd84-054a78a57d60 |  | checkpoint | Test Details- Pass once entered
text | 08364548-d2f3-5a4c-b058-4b6881028482 |  | textbox | Location (Area/Level/Zone)
text | ac94436c-ddfd-597a-b138-850618050ae1 |  | textbox | Testing Calibration Certificate Uploaded Per Level
text | fce8ce19-8142-55ab-b8f5-8d3e6ba45011 |  | textbox | Testing Apparatus Type & Number (Input or Attach photo below)
checkpoint-status | d441d404-7d10-43d0-90fa-9cb2b9344c4f |  | checkpoint | Final Hydrostatic Test
label | 4da5b9aa-e492-59af-85c6-96d3658f8594 |  | note | Test at 1500kPa for no less than 30 min as per AS3500.1 2015
boolean | 6f823f93-ccb5-5531-a93a-9f8553181228 |  | tickbox | CDC - General Photos/comments attached below
boolean | 97325e33-02af-50f5-b9b7-ccfd02fcbb0e |  | tickbox | CYP Nominated comments - General comments attached below
checklist-flat | 61401729-94e2-4a2e-958c-9e917e17f87d |  | checklist | Drawing Upload - Checklist (V.101221) |  |  |  |  | Yes | Drawing Upload - Checklist (V.101221) | edd90b0b-8bb5-4084-b20c-2eddb3c268e4
checkpoint-status | c1c80c9a-4cca-4c71-a4b1-d8883461429e |  | checkpoint | Drawings/comments/signatures - attached below
checklist-flat | db2d5a5f-0113-479f-9d48-cece40c33072 |  | checklist | Cast-Ins/penetrations CYP Checklist Number CHK/MMTS/00810 |  |  |  |  | Yes | Cast-Ins/penetrations CYP Checklist Number CHK/MMTS/00810 | fde493f8-5cc7-4606-a958-218034cf5fee
checkpoint-status | 4233aea7-03bc-40bc-9e27-e991c38a6ce1 |  | checkpoint | Are the latest Version of the drawings being used for the work. Ref: 7.3.1 & 7.3.2 section on Hydraulic Services Specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001)
text | 66d11df4-9e47-5d1b-a575-b89d04767089 |  | textbox | Drawing number
text | 63481272-7b98-5ba7-ac6a-eb7a375df68c |  | textbox | Revision
checkpoint-status | 76485c48-95de-48e3-88c0-1d66b7aa96c8 |  | checkpoint | Location of pipework is as per IFC drawing & CYP site survey set out Ref: 8.1.5 & 8.3.3 on Hydraulic Services Specification
select | 64fc4749-082a-58ac-b169-8748fc0ec58e |  | dropdown | Drain / Penetration type | Permanent,Provisional
checkpoint-status | 6489dad1-fe8b-4fbd-9e26-36b0b1da39fb |  | checkpoint | Pipe materials used are as per Tunnel and stations hydraulic services specification (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
select | 0d59fcec-62a4-50bf-b159-87ee7b8476cf |  | dropdown | Pipework material used. Ref : 7.9.1 section on Hydraulic Services Specification | HDPE,Cast Iron,Poly
checkpoint-status | 42c427f2-d1e1-4470-9fb7-bc44e61b4e4d |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
label | c979a251-9561-5e42-90c1-252794a6f36e |  | note | Visualised by Nominated CYP Authority Only (CYP NA2- Proficiency Level 2)
boolean | 8865a3a5-9551-50fb-a0af-4093c4218d67 |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | dc1184a1-4974-4112-8a94-3f7fdb43772b |  | signoff | HOLDPOINT - CYP to Verify steps 1 to 6 are compliant with applicable supporting documentation
checkpoint-status | 546c65a6-4651-4d28-beea-7af379df9a37 |  | checkpoint | Invert levels as per drawings Ref: AS3500.2.2015 Table 3.4.1 and 8.3.8.4 in Hydraulics Services Specification
checkpoint-status | c63ebd2a-f8ec-41d8-8a8d-756e384d233a |  | checkpoint | No damage to pipework or fittings. Ref: Attached Photos below
checkpoint-status | 705ba79e-1227-46ca-9784-0ef3e9002dad |  | checkpoint | Correct drainage venting per Ref: AS 3500.2 2018 sec 3.9
checkpoint-status | f99c2fb0-12a3-4317-92df-9aed5bcba316 |  | checkpoint | Correct fire protection / fire collars as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | ddfbca83-a336-44ab-afcf-fcd20a0d5995 |  | checkpoint | Type & Brand of collar used as per Ref: C3.15 of the BCA AS4072.1
checkpoint-status | 6c9fee23-b9e9-441d-8fda-5586f9e48359 |  | checkpoint | All points are connected
checkpoint-status | d7e84abd-33e7-4a72-b865-217abfa65248 |  | checkpoint | Pipework on correct grade as per AS 3500.2 2015 Table 3.4.1 and 8.3.8.4 on Hydraulics Services Specification
checkpoint-status | 51e32634-8b64-4659-97a8-c2297d9618da |  | checkpoint | Pipes are clean & Clear of debris - Welded / Glued Ref: As Per manufacturers requirement
checkpoint-status | dce7665d-add3-44d9-9ad4-419fb062bd0b |  | checkpoint | Joint method defect free (Compression band) (Electro fusion) (Glued) Ref: As Per manufacturers requirement
checkpoint-status | 391c9559-5f09-484b-bdd4-3ef56b335b6e |  | checkpoint | Has the pipework been witness marked and signed upon positive visual inspection of chosen method of jointing
checkpoint-status | d64bdaef-520f-4b9f-9b34-b109915d817f |  | checkpoint | Pressurised pipework to 15 Kpa according to AS3500.2 Sec 15 and Ref: 8.1.9, 20.3.6 & 20.3.8 on Hydraulics Services Specification
label | 37445c50-795a-58dd-aca3-8d6a1123bc0b |  | note | Settle time for test is 3 min then an additional test time of 5 min Maximum pressure drop is +/- 3 Kpa over a 5 min period
checkpoint-status | f63a3aed-880c-4a13-b26e-0a4539f5249c |  | checkpoint | HOLDPOINT BELOW - CYP to sign before passing checkpoint
boolean | 6b3b5e8c-e3e1-580c-a382-e023b0d113f5 |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
label | a66d6ab1-e112-5d03-b6a2-49f98ce60243 |  | note | Visualised by Nominated CYP Authority Only
holdpoint | 39b6b22d-3b1e-4c1d-905f-eb2f89d51274 |  | signoff | HOLDPOINT- CYP Nominated Authority sign off test
checkpoint-status | f3d89d1b-e82e-4eb1-8da6-3ddcf6f9faca |  | checkpoint | Pipe clipping on grade as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 39da6d49-b5e1-49cd-9319-bf6d95e26dd9 |  | checkpoint | Vertical clip spacing as per AS 3500.3 Clause 4.9.6.2
checkpoint-status | 05e0c6be-7d09-4fe2-8f08-fd24e0fbd0c1 |  | checkpoint | Pipe lagged in accordance with tunnel and stations hydraulic services specification
label | 23ef99b5-d277-586e-b382-6d83606cc1c8 |  | note | Specifications (TAS-CYP-SDU-ZWD-SPC-BSH-SDU-B0001 REV-B)
checkpoint-status | e226b1d2-bd4e-4101-bc38-c50661ffe660 |  | checkpoint | Pipework to remain full of water during pour. Ref: As Per manufacturers requirement
checkpoint-status | 01d8e77f-c9a4-4b89-8a36-47fdb9e797ec |  | checkpoint | Has pipework been picked up for completed works (As-built)
checkpoint-status | 87129215-d3ff-41fa-a7bf-196e0366e905 |  | checkpoint | Signoff - CDC to sign before passing this checkpoint
boolean | 24a1b564-ea98-59ef-b8c4-1e3bcbc282bc |  | tickbox | CDC - General photos/comments attached below
label | e846bfe5-d461-59f3-88a6-cf8a1454fc01 |  | note | SIGN-OFF :Name & Signature attatched below
holdpoint | 3204ce1c-81f5-42a5-8272-df5b3d403aa5 |  | signoff | FINAL HOLDPOINT- CDC authority to signoff
checkpoint-status | 801aa421-3bb7-42ba-9b4a-8182d42d2040 |  | checkpoint | Signoff - CYP to sign before passing this checkpoint
boolean | 59221730-e193-5021-8066-fa6267f7a5fe |  | tickbox | CYP Nominated comments - General comments attached below
boolean | 4b82b593-7fc9-5645-90f4-43aa44081ed0 |  | tickbox | SIGN-OFF - CYP Nominated Name & Signature(s) attached below
holdpoint | cccf09e1-e477-4aa4-9ec5-56cf37be804e |  | signoff | FINAL HOLDPOINT- CYP nominated authority to signoff