## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Traffic Signals | itp |  |  |  | Yes | ITP - Traffic Signals | 07795f08-0b93-4954-81f0-16c8e0a0e5c8
section | Setout, Materials and Preparation
checkpoint | 900.1 - Method Statement Development / Job Safety & Environmental Analysis
label | Detail of Activity - Prepare shared services trench construction methodology and Job Safety & Environmental Analysis suitable for site (eg access, working areas, proximity to slopes, traffic and other site hazards, construction stages proposed)
label | H
label | Minimum Test Frequency - NA
label | Inspection / Test method - NA
label | Acceptance Criteria - Method Statement and JSEA Completed and signed by relevant authority.
label | Record documents - MS & JSEA
label | Responsibility - Contractor
label | Comments - Method Statement and Job Safety & Environmental Analysis to be provided to Engineer for review prior to commencing excavation on site.
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.2 - Drawings and Specifications
label | Detail of Activity - Check drawings are for construction and latest revision. Check Specification is for construction and latest revision
label | H
label | Minimum Test Frequency - NA
label | Inspection / Test method - NA
label | Acceptance Criteria - Drawings and Specification are the latest revision.
label | Record documents - IFC Drawings and Specification
label | Responsibility - Contractor
label | Comments - Up to date drawings and specification to be reviewed before construction.
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.3 - Power Connection
label | Detail of Activity - Ensure power supply is organised and connection is in place
label | H
label | Minimum Test Frequency - once per set of traffic lights
label | Inspection / Test method - NA
label | Acceptance Criteria - Complete NC1 form and ensure ducting for power is in place.
label | Record documents - NC1 Form
label | Responsibility - WSP / Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.4 - Comms Connection
label | Detail of Activity - Ensure comms connection is organised and ducting is in place
label | H
label | Minimum Test Frequency - once per set of traffic lights
label | Inspection / Test method - NA
label | Acceptance Criteria - Liase with service provider and organise connection (UCG) Universal communications group.
label | Responsibility - Contractor
label | Comments - Order connection from Chorus
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.5 - Survey Set Out
label | Detail of Activity - GPS Setout of the shared services trench location as per the construction drawings.
label | W
label | Minimum Test Frequency - All shared trenches.
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - N/A
label | Record documents - Contractor's site diary and/or photos
label | Responsibility - Contractor
label | Comments - Setout location prior to commencing works.
checkpoint | 900.6 - Sediment Controls are in place for the particular section
label | Detail of Activity - Check ESCP and ensure any controls needed are in place before excavation.
label | M
label | Minimum Test Frequency - once per section
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Erosion and Sediment controls are in place prior to starting works.
label | Record documents - Contractor's site diary and/or photos
label | Responsibility - Contractor
section | Construction and Finshing
checkpoint | 900.7 - Element Locations / Positioning / Types
label | Detail of Activity - Walk over with TTOC, WSP, TSL & Downer representatives to agree positions of intersection elements
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - TTOC, WSP, TSL acceptance.
label | Record documents - Written confirmation
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.8 - CIS Production
label | Detail of Activity - Draft CIS to be produced, independently reviewed and approved.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Document Review
label | Acceptance Criteria - Review completed and development approved.
label | Record documents - InEight Documents
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.9 - Software Testing
label | Detail of Activity - Software to be independently tested using traffic signal emulator software (SFT Testing)
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Document Review
label | Acceptance Criteria - Approval for release received.
label | Record documents - SFT Test Result Summary Sheet
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.10 - Software Testing
label | Detail of Activity - SFT files provided to create PROM, bench testing to be completed by TSL
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Document Review
label | Acceptance Criteria - Pass result for bench test on "Appendix H - Controller Bench Testing Form".
label | Record documents - Appendix H NZTA P43
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.11 - Pole - Installation
label | Detail of Activity - Ensure poles are plumbed vertical
label | W
label | Minimum Test Frequency - Each pole
label | Inspection / Test method - Location/Position Acceptance
label | Acceptance Criteria - Plumbed vertical
label | • Tolerance: +/- 10mm per 5.0m length
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.12 - Pole - Identification / Finishing
label | Detail of Activity - Pole Number Verification
label | W
label | Minimum Test Frequency - Each pole
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Ensure poles are numbered correctly and match the CIS sheets (pole numbers match program and diagram numbers).
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.13 - Pole - Footings
label | Detail of Activity - Footing Type
label | W
label | Minimum Test Frequency - Each pole
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - TSL engineer confirmation that poles are founded securely and have adequatley sized footings for the site conditions.
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.14 - Pole - Footings
label | Detail of Activity - Soil Bearing Strength
label | H
label | Minimum Test Frequency - One per pole cluster area (i.e. north-eastern corner, median etc.)
label | Inspection / Test method - Scala Penetrometer
label | Acceptance Criteria - Average 3 blows / 100mm over 500mm or per comments
label | Record documents - Scala Testing
label | Responsibility - Contractor
label | Comments - Scala results to meet or exceed per below:
label | 0mm - 100mm - ≥ 3 blows per 100mm, 100mm - 200mm - ≥ 2 blows per 100mm, 200mm - 300mm - ≥ 2 blows per 100mm, 300mm - 400mm - ≥ 1 blow per 100mm, 400mm - 500mm - ≥ 1 blow per 100mm
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.15 - Pole - Footings
label | Detail of Activity - Concrete Foundation Dimensions
label | W
label | Minimum Test Frequency - Each footing not within concrete or asphalt.
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Where a pole is not surrounded by concrete, the pole must have 500mm2 of concrete surrounding it with a depth of 150mm (20MPa as below).
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.16 - Pole - Footings
label | Detail of Activity - Footing Concrete Strength
label | M
label | Minimum Test Frequency - Each footing requiring concrete
label | Inspection / Test method - Visual Inspection/Concrete Dockets
label | Acceptance Criteria - Confirmation footing concrete strength (where required - i.e. delivery dockets) is min 20MPa at 28days, or as specified in foudation design.
label | Record documents - QC Sheets/concrete dockets
label | Responsibility - Contractor
checkpoint | 900.17 - Cabling
label | Detail of Activity - Continuous Lengths
label | M
label | Minimum Test Frequency - All lengths
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Cabling to be continuous lengths from controller to the pole, and from pole to pole (i.e. no joints between poles).
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.18 - Cabling
label | Detail of Activity - Looper Feeder Cable Slack
label | M
label | Minimum Test Frequency - All lengths
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Following cable slacks to be provided:
label | – 1.8m (minimum) at controller base
label | – 0.5m (minimum) inside KSJB
label | Record documents - QC Sheets
label | Responsibility - Contractor
checkpoint | 900.19 - Cable Termination Chart
label | Detail of Activity - Provide cable termination chart in controller cabinet.
label | H
label | Minimum Test Frequency - Each controller cabinet
label | Inspection / Test method - Inspection
label | Acceptance Criteria - Cable termination chart provided.
label | Record documents - QC Sheets
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.20 - Earth / Earth Loop Impedance Testing
label | Detail of Activity - Complete earth loop impedance testing per 3.15.2 of NZTA P43.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection as specified in 3.15.2 of NZTA P43
label | Inspection / Test method - Inspection
label | Acceptance Criteria - Submit results in a report.
label | Record documents - QC Sheets
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.21 - Loop Testing
label | Detail of Activity - 500V test from the isolated conductors down to earth.
label | H
label | Minimum Test Frequency - All loops
label | Inspection / Test method - Electrical Testing
label | Acceptance Criteria - Result ≥ 10 megaohms.
label | • Q ≥ 15 when measured in the kerbside junction box (KJB).
label | • Submit results signed by technician who conducted the testing and in a report.
label | Record documents - QC Sheets
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.22 - Loop Feeder Cable Testing
label | Detail of Activity - 500V test from isolated conductors down to earth.
label | H
label | Minimum Test Frequency - All feeder cables
label | Inspection / Test method - Electrical Testing
label | Acceptance Criteria - Result ≥ 10 megaohms.
label | • Resistance of feeder cable ≤ 10 megaohms when measured at the controller. Submit results signed by technician who conducted the testing and in a report.
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.23 - Log Book
label | Detail of Activity - Log book detailing any attendance at site, reason for attending and brief description of work carried out.
label | H
label | Minimum Test Frequency - Once per controller box
label | Inspection / Test method - Visual Inspection
label | Acceptance Criteria - Log book provided/completed as required.
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.24 - Site Acceptance Testing
label | Detail of Activity - Completion and sign off of TTOC-07 Site Acceptance Test (SAT) documentation.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Inspection / Audit
label | Acceptance Criteria - All requirements satisfied and TTOC Traffic Signals Engineer signed acceptance of SAT document.
label | Record documents - TTOC-07 SAT
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.25 - Electrical certificate of compliance and record of inspection
label | Detail of Activity - Complete COC and ROI.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Inspection / Audit
label | Acceptance Criteria - Submit COC and ROI.
label | Record documents - COC & ROI
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.26 - Commissioning
label | Detail of Activity - Submit completed and signed Appendix H forms 5 working days prior to commissioning.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Document Submission
label | Acceptance Criteria - Submit Appendix H forms to TTOC.
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.27 - Commissioning
label | Detail of Activity - Notify TTOC with 48hrs notice before commissioning lights.
label | H
label | Minimum Test Frequency - Once per set of traffic lights/intersection
label | Inspection / Test method - Inspection
label | Acceptance Criteria - TTOC Acceptance.
label | Record documents - Written confirmation
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
section | Close Out
checkpoint | 900.28 - Collate above documentation
label | Detail of Activity - Document review
label | H
label | Minimum Test Frequency - Each ITP
label | Inspection / Test method - Review
label | Acceptance Criteria - All above documentation is shown as attached to this work pack.
label | Record documents - Review
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.29 - Controller cabinet documents
label | Detail of Activity - Controller Cabinet Information
label | H
label | Minimum Test Frequency - At time of commissioning
label | Inspection / Test method - Review
label | Acceptance Criteria - Laminated copies of below placed in document pocket inside controller cabinet, within two weeks of commissioning:
label | – As-built plans
label | – Completed cable termination chart
label | – Controller Information Sheet (CIS)
label | – Log-book
label | Record documents - Review
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 900.30 - As-built drawings
label | Detail of Activity - Survey
label | H
label | Minimum Test Frequency - At completion of construction
label | Inspection / Test method - Asbuilts to be submitted at the completion of construction, information to be captured regularly.
label | Acceptance Criteria - Asbuilts reviewed and submitted showing final location of all poles, access chambers, KJB, loops, lantern displays and cabinets. Completion and sign off of TTOC-08 Site Asset Collection Sheet/Appendix K of NZTA P43 documentation.
label | Record documents - In Eight record
label | Responsibility - Contractor
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Client Final Inspection - Contractor
label | The signature below verifies that this ITP has been completed in accordance with NZTA Specifications and verifies lot compliance.
text | Contractor's Rep Name:
holdpoint | Add Signature
checkpoint | Client Final Inspection - BBO Engineer
label | The signature below verifies that this ITP has been completed in accordance with NZTA Specifications and verifies lot compliance.
text | BBO Engineers Rep Name:
holdpoint | Add Signature