## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | ITP 02 - Speedpanel |  |  |  |  | Yes | ITP 02 - Speedpanel | 35b00907-9c8c-41eb-b678-fb6ab6497366
checkpoint-status |  |  | checkpoint | Drawing Reference - Latest IFC drawing referenced
checkpoint-status |  |  | checkpoint | Current revision (Photo of title block with drawing No. and revision)
checkpoint-status |  |  | checkpoint | Area clean and accessible to start work
checkpoint-status |  |  | checkpoint | Confirm panel thickness used - 78mm
checkpoint-status |  |  | checkpoint | Setout of wall location verified
checkpoint-status |  |  | checkpoint | Apply approved fire rated sealant (Hilti 606) between c-track and structure to entire perimeter (Photo)
checkpoint-status |  |  | checkpoint | Fix c-track to structure using Hiliti Huss anchors at 500mm centres (Photo)
checkpoint-status |  |  | checkpoint | Apply approved fire rated sealant (Hilti 606) to internal corner ot the c-track (one side) to entire perimeter (Photo)
checkpoint-status |  |  | checkpoint | Verify maximum 20mm gap between speedpanel and top c-track (Photo)
checkpoint-status |  |  | checkpoint | Panel fixing - Perimeter 500mm centres / Horizontal 250mm centres / Vertical 1000mm centres
checkpoint-status |  |  | checkpoint | If pressurised riser, all joins have been sealed - panel end & perimeter
checkpoint-status |  |  | checkpoint | Install head track protection fixed with 30mm screws at 125mm centres (Photo of completed wall)
checklist-flat |  |  | checklist | ITP 01 - Rigid Board |  |  |  |  | Yes | ITP 01 - Rigid Board | dc4819ee-03e6-4471-9be0-85c62a44e37c
checkpoint-status |  |  | checkpoint | 1 - Set out Rigid Board
label | 39c00b11-1723-599c-888c-9eef81bd40a1 |  | note | ACCEPTANCE CRITERIA: Thermal Insulation Plan Latest Revision (Photo of Title block with drawing No. and revision)
label | 7ca0bb0c-99f0-55d7-bb7c-326d80563a85 |  | note | ○ Area is clean and accessible to start work
label | e2a37b14-a33a-581b-b534-ae7ff2a1e178 |  | note | ○ Setout of Rigid Board
label | 2257f509-ce0e-5d25-b85f-6c789bc0ceba |  | note | FREQUENCY: Each location
label | 9a767177-fd5e-53e7-a125-986c03ceb470 |  | note | VERIFICATION RECORDS/COMMENTS: Visual, Checklist
label | 54ac57ae-c611-5fc8-9ec6-4f0751db4062 |  | note | INSPECTION BY: S (Subcontractor), S (Multiplex)
checkpoint-status |  |  | checkpoint | 2 - Install Rigid Board
label | ae221eac-84bf-5531-a88e-49d60de6641d |  | note | ACCEPTANCE CRITERIA: Confirm the thickness / R-value of the board (State the panel thickness and R-value)
label | 564986b0-3e6d-555c-8750-14b72f6343c4 |  | note | ○ Min 35mm head diameter fasteners
label | c05401d3-8295-5576-82f5-2c11dc9e106e |  | note | ○ 11nos of Fasteners required for a full board size (1.20m x 2.40m) with 3no of the fasteners along the middle
label | 1f922d0c-ff88-5dd2-9f1b-694281b548e9 |  | note | ○ The fasteners are evenly distributed over the whole board
label | d078e8a5-7f2a-5b79-9d36-b293590fdaaa |  | note | ○ Fasteners along each length - no less than 50mm or no more than 150mm from edge of the board
label | 2865115d-c25a-52ce-99e3-4f788e42dd3f |  | note | FREQUENCY: Each location
label | c12ff955-f523-5e7a-8aaa-751b763e0de5 |  | note | VERIFICATION RECORDS/COMMENTS: Visual, Checklist
label | a7ca7a5b-aed3-5243-8d57-40d01ebcef71 |  | note | INSPECTION BY: S (Subcontractor), S (Multiplex)
checkpoint-status |  |  | checkpoint | 3 - Tape & Seal
label | 970c76da-b7cd-51cd-9f30-460036d85351 |  | note | ACCEPTANCE CRITERIA: Tape placed over the center of the joint of both board
label | bbfca93b-2628-5193-b462-b34e30c80954 |  | note | ○ All joints are taped
label | e938dcfe-154a-588a-bd97-9acc7a0b6d78 |  | note | ○ Exposed board edge cover with foil tape lapped 48mm onto underside of the board
label | 05b89720-8f96-50dd-b1d0-35d2b24a4bda |  | note | FREQUENCY: Each location
label | 55fde089-d57c-59d1-a8ea-ffb266eaa8cd |  | note | VERIFICATION RECORDS/COMMENTS: Visual, Checklist
label | e868d389-a8c1-536d-91da-c2eaa340fe77 |  | note | INSPECTION BY: S (Subcontractor), S (Multiplex)
checkpoint-status |  |  | checkpoint | 4 - Clean up
label | 7b18ab29-f401-5c3c-bbcc-102158da39d1 |  | note | ACCEPTANCE CRITERIA: Waste all cleaned. Tools and materials placed well.
label | bf838c4d-9f95-51c1-ba77-89d0b9a07989 |  | note | FREQUENCY: Each location
label | f9c4b777-0297-5621-945e-e241c19824a9 |  | note | VERIFICATION RECORDS/COMMENTS: Visual, Checklist
label | 3128fb09-cf31-5c96-9032-8ae01dae47eb |  | note | INSPECTION BY: R (Multiplex)
checkpoint-status |  |  | checkpoint | 5 - Materials Receipt Inspection
label | 37c05b37-a294-5618-9e06-fcfab01fcf36 |  | note | ACCEPTANCE CRITERIA: Refer to ITP No: 5 Incoming Goods
checkpoint-no-status |  |  | checkpoint | Final Inspection
text | e8afe93f-de38-508f-807c-175b7365652f |  | textbox | Comments:
text | 426c346a-f313-5edb-8d03-5381191a0b5b |  | textbox | Date of Inspection:
text | e643c12f-53f1-5581-80be-5d64d6f074fa |  | textbox | Carried out by: