## PROJECT STRUCTURE
Folder Structure |  |  |  | Checklists
FLAT BUSH SCHOOL | TAMAKI HEALTH | PROJECT: OPTIMAL 97 GRAFTON
INTERIOR FITOUT
|  | LEVELS | BASEMENT | 1ST FIX
2ND FIX
|  |  | GROUND FLOOR | 1ST FIX
2ND FIX
|  |  | LEVEL 1 | 1ST FIX
2ND FIX
|  |  | LEVEL 2 | 1ST FIX
2ND FIX
|  |  | STAIRWELL | 1ST FIX
2ND FIX
COMMISSIONING
|  |  | BASEMENT DB | COMMISSIONING - DISTRIBUTION BOARD
|  |  | GROUND FLOOR DB | COMMISSIONING - DISTRIBUTION BOARD
|  |  | LEVEL 1 DB | COMMISSIONING - DISTRIBUTION BOARD
|  |  | LEVEL 2 DB | COMMISSIONING - DISTRIBUTION BOARD

## CHECKPOINTS
CHECKLIST | 1ST FIX
CHECKPOINT | CABLING INSTALLED AS PER LGHTING AND POWER LOCATIONS REFLECTED
CHECKPOINT | DATA CABLES INSTALLED, CABLE LABELLED AND CONFIRMED AS PER DATA LAYOUT
CHECKPOINT | DATA CABLES RAN BACK TO COMMS CABINET.
CHECKPOINT | CORRECT SIZE POWER/LIGHTING CABLE INSTALLED AS PER CABLE CALC TO LOADS AND VOLTAGE DROP
CHECKPOINT | NOGS MARKED AND INSTALLED FOR FLUSH BOXES AND SURFACE MOUNTED LIGHTS
CHECKPOINT | FLUSH BOXES MOUNTED AS PER ARCHITECTURAL ELEVATION
CHECKPOINT | FLUSH BOXES FOR ISOLATORS INSTALLED ABOVE BENCH OR AT ACCESSIABLE LOCATION TO APPLIANCE
CHECKPOINT | FEED AND SWITCH WIRES INSTALLED AND CONFIMRED FOR LIGHTING
CHECKPOINT | LIGHTING LOOPS INSTALLED AS PER LIGHTING LAYOUT
CHECKPOINT | EMERGENCY CIRCUITS AND LOOPS CHECKED AND COMPLETED.
CHECKPOINT | BOND CABLE TO CEILING GRID/SINKS AND STRUCTURE IS RAN AND CONFIRMED
CHECKPOINT | DEDICATED POWER CIRCUITS TO ROOM AND MEDICAL SERVICE PANEL
CHECKPOINT | BPA ROOM POWER OUTLETS ARE RCD PROTECTED FROM RCD POINT WITHIN ROOM
CHECKPOINT | BPA ROOMS MEET AS/NZS 3003:2018 PATIENT AREA STANDARD
CHECKLIST | 2ND FIX
CHECKPOINT | LIGHT SWITCHES INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | POWER OUTLETS INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | DATA OUTLETS INSTALLED, LEVELLED, LABELLED AND TESTED.
CHECKPOINT | HALLWAY OUTETS DEEMED CLEANERS OUTLETS INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | SURFACE SOCKETS FITTED OFF FOR PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS
CHECKPOINT | SURFACE SOCKETS ARE LABELLED TO ALLOCATED CIRCUITS CORRECTLY
CHECKPOINT | PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS ARE INSTALLED IN CORRECT LOCATIONS.
CHECKPOINT | EMERGENCY LIGHTS INSTALLED, LABELLED, LIVE AND WORKING CORRECTLY.
CHECKPOINT | CEILING GRID/SINKS/ BUILDING STRUCTURE IS BONDED AND TEST RESULTS < 0.5 OHMS TO DB
CHECKPOINT | 10mA RCD RESET POINT IN ROOM INSTALLED, LEVELLED, LABELLED AND CORRECTLY WORKING
CHECKPOINT | RCD PROTECTED AMBER POWER OUTLETS INSTALLED, LEVELLED, LABELLED CORRECTLY AND LIVE
CHECKPOINT | BPA ROOMS MEET AS/NZS 3003:2018 PATIENT AREA STANDARD
CHECKPOINT | BPA SIGN INSTALLED IN A VISIABLE LOCATION.
CHECKPOINT | BPA ROOM INSPECTED AND SIGNED OFF
CHECKLIST | COMMISSIONING - DISTRIBUTION BOARD
CHECKPOINT | SWITCHBOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DB SCHEDULE COMPLETED, INSTALLED INTO DB AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD CHECK SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EARTHING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | TIMECLOCK TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | BOARD FREE FROM DEBRI, NO MARKS, ALL ACCESSORIES INSTALLED
CHECKPOINT | LABELLING COMPLETED ON ALL FIELD OUTLETS, SWITCHES AND ISOLATORS ETC
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX