## Master List Templates
Id | Type | Name | Values | Prompting Name
561008bb-58d2-48f6-bd38-674610c2eb61 | checklist | Add Concrete Pour Record |  | Load No.
c5ccbbbb-305b-4d59-b2a8-a2529972fe8d | section | Details
e5b2b6c7-fb17-4b0c-875a-19f20460fc2c | checkpoint | Details
d0f39a05-355d-5237-ac26-3dacbad4a401 | textbox | Docket No
04145c0b-7fe4-53ed-9c42-24e161783c74 | textbox | Time Batched
2780b034-47cf-57e6-a289-34f1395ee555 | textbox | Arrived on site
68785430-9a4f-5de5-8eac-8f7ec1be1638 | textbox | Dispatch Commenced
42b65e86-ca78-5907-9eee-970e854e40e8 | textbox | Completed
0df7555b-8dfa-524a-b82c-7068f6c709ba | textbox | Concrete Volume: Vol
82c05a1b-cd01-5cfe-97fa-cad0dedf9eb2 | textbox | Concrete Volume: Cum. Vol
0e983d07-bcf9-5fce-a248-9a3448207bcc | textbox | Initial Slump (mm)
5a5d397c-f34f-59e2-944d-16b1dff57f54 | textbox | Concrete Temp (Degrees C)
62a2c26b-df38-55d3-a8d9-de9bec659c55 | textbox | Water added on Site: Qty (L)
c6437bc2-1f8b-58ca-bb01-c1b7643f1b44 | textbox | Water added on Site: Final Slump (mm)
9ec7919a-4aeb-5134-a0b4-ddf5187c2102 | textbox | Ambient Temperature (Degrees C)
29cbd7d3-c9f2-55cc-a516-04f4e1479193 | textbox | No./ Days of Cylinder Taken
17cf5b4e-2f18-553a-bfe0-2aeafe338588 | textbox | Remarks
e543d322-1e56-4dee-9bee-22c531e2e5eb | checklist | BESS & PCS footing Touch Up paint FIC |  | BESS & PCS footing Touch Up paint FIC -
ca169310-0c6a-44da-a727-abe60baadb23 | section | 2. SPECIFICATION
619de76c-b689-4ca3-ad1c-deea0bcb5c2d | checkpoint-no-value | Coat: 1
6c6db31d-14df-539f-8e96-f3a6fc409968 | note | Product: Surface preparation – Bristle blast the damaged areas to achieve a profile of 50-75um and feather the surrounding sound galv up to 50mm
2cd66ec6-8adf-56b0-a42a-0b57cca6054e | note | Colour: n/a
8f90bb7f-e289-5a56-b950-0b72bacff666 | note | DFT (μm , Min-Max): n/a
0858697d-072f-4549-933d-f56200916244 | checkpoint-no-value | Coat: 2
4077767f-3b59-5802-ae5e-f73bbaffe5cf | note | Product: Apply the Interzinc 52 @ 75um
29fb953c-cda4-5c8f-b105-92283a82b157 | note | Colour: Grey
61fdeb5a-77bb-5ddf-9002-f2fcc0c0f2b3 | note | DFT (μm , Min-Max): 75 (total)
36e6cbae-c7d4-4c41-acbe-f27b0b1d4f09 | checkpoint-no-value | Coat: 3
efe47bd9-0026-5216-ab35-2691ab7c48a1 | note | Product: Apply the Interplus 1180 @ 200um (if applying by brush or roller this can be done in multiple coats)
b332ae9e-e8fe-52fb-a69c-5f02d074325f | note | Colour: Grey
8c951751-1ec8-5c95-aace-252ff2df9dc3 | note | DFT (μm , Min-Max): 200 (100 for each coat)
82c357ef-5146-4655-89b3-9ce692467f13 | section | 3. SURFACE PREPARATION
00feacf4-336c-4022-b2ef-5d9214ad08cf | checkpoint | Does visual standard of surface preparation comply with specified requirements?
c07012ea-0cb4-4e0b-9fe7-ff4fdff09109 | section | 4. COATING APPLICATION
ddac2add-0f4a-4f3d-b65b-9986d4d696d7 | checkpoint | COAT 1
7ed4e5e2-bd29-5cd7-910a-5012f7256369 | number | Coat No.:
edbaf6ee-a1d4-5511-ae1b-723897806c99 | date | Application Date:
c0c9ef6c-1035-550b-8ace-c3ca845b0d79 | textbox | Batch No.:
ba6f0833-081b-53f9-aa7e-9eb4198db5fb | textbox | % RH
1c3b955c-9a1e-5bbb-8759-ecaa146923e9 | textbox | Ambient Temp (ºC)
810d7bac-4d5d-50f8-a6cc-ec23301459df | note | Steel Temp (ºC): >10, Comply to ASTM D3276
6e776c7e-e892-5e7d-9149-b8aa7314d65d | textbox | Dew Point (ºC)
c4475b1e-ed48-5bc6-a68f-3da0f11f4f82 | textbox | Wet Film Thickness (μm)
bc1b9cd3-5a3c-405a-9f7a-4761a6b33d93 | checkpoint | COAT 2
3548cf55-89f3-5a47-b573-adf90054db92 | number | Coat No.:
da81f821-fdb9-5609-a410-a53a343de00d | date | Application Date:
0b87eddd-3ebd-5a5f-bdb0-bcedda9a6c63 | textbox | Batch No.:
e56d52fe-0eec-5d0a-a956-bb9ba123f630 | textbox | % RH
b041e7d5-109c-5aac-82f2-6185867aac58 | textbox | Ambient Temp (ºC)
b3dd12d0-4fa9-5868-a1b4-ce9f95c52ae5 | note | Steel Temp (ºC): >10, Comply to ASTM D3276
e8ac521d-ad05-504f-9349-1dc5ce09a0bf | textbox | Dew Point (ºC)
6a2e08d8-7ce9-575a-a3e6-1db739434332 | textbox | Wet Film Thickness (μm)
47446d3a-3789-483b-889b-15a5692fc2db | checkpoint | COAT 3
30af7ed6-6fe8-5f82-ab53-1cd3f9946956 | number | Coat No.:
9bf3a641-909e-5b2c-a914-64dc40db1053 | date | Application Date:
400f2126-8561-5bdb-a936-5c4fa83ddc7b | textbox | Batch No.:
7fa778db-894e-593f-b5f2-b31bf029ca3d | textbox | % RH
b4fdd1f4-4391-52f8-98cf-610b6168316e | textbox | Ambient Temp (ºC)
0c9c8af9-04af-5872-a937-9867b044745c | note | Steel Temp (ºC): >10, Comply to ASTM D3276
ecde2c07-7205-5e61-9323-ca81883ce4c2 | textbox | Dew Point (ºC)
32b99e8e-75a3-5e3b-ac17-aa49f755cfda | textbox | Wet Film Thickness (μm)
3facdf04-cd28-4182-86aa-fac2a2123128 | section | 5. FIC - SPECIFIC CHECK ITEMS
5cbf89f6-64de-48af-9faa-9e350d91fc9a | checkpoint | Ambient conditions (steel temp, air temp, % RH, dew point) complies?
823a7f87-f536-4973-be56-03b18e6c07d6 | checkpoint | Application method complies to manufacturer’s recommendations?
9bdba00f-d198-44b4-b5fc-1e8d772be078 | checkpoint | Recoat intervals complies to manufacturer’s recommendations?
519c7d4d-59cd-4a14-9796-17de699508b1 | checkpoint | Colour complies to specifications?
f586b266-9f24-425b-b3aa-20a3e0095409 | checkpoint | Dry film thickness/Wet film thickness complies to specifications?
b993e230-8e0b-486f-8893-22d0c5a9369e | checkpoint | Final appearance (runs, overspray, uniformity, etc.) acceptable?
ac6b1679-0c43-4513-a8b0-15f2766a83bb | section | Document Sign-off
bd7cc974-cfd3-4979-adfe-3b73343b329a | checkpoint | Prepared by:
3ff9c617-c21e-51d0-8b28-b3c4f76c7ffd | textbox | ROBAR - Name:
89dbf16c-be5a-51fe-b547-7e541e5d987e | textbox | ROBAR - Position:
c75e9128-1cad-596d-a58a-d302430b2659 | date | Date:
00c6dafe-20b4-4683-bce5-033aa6d7e41e | signoff | Add Signature
e6cf256a-8749-409c-96e6-08884942cf3f | checklist | General QA Checklist |  | General QA Checklist
af8bde2f-abf6-4229-b3f5-8ba8aef22176 | section | Details
753a5922-ac4f-4ace-a07f-db7ee4542692 | checkpoint-no-value | QA - Title & Date
64b537b7-5f9e-49de-a91b-4a89fcb44d30 | checkpoint | QA - Drawings or markups uploaded
7d83c687-eec4-4276-9700-2cee430d92f9 | checkpoint | QA - Survey or asbuilt uploaded
d4984f70-ff9c-4b10-bb7f-72d6c90f6a6f | checkpoint | QA - Supporting photograph(s) uploaded
d57baf63-3f69-41b7-970e-099c473fa974 | checklist | Lot Checks | itp | Lot
81b6d5a2-04e6-488a-8389-23b47616dcb6 | section | Section 1: Preliminaries & Permits
21e42e79-ebf9-4a61-bc6e-048f3f84a20c | checkpoint | 1.1 - Collect and verify information (Site boundary, utilities, survey map, design drawings)
517ea329-99f7-5146-a7f8-c92daa9c1fe0 | note | Responsibility - SE/PE
160f9ef5-41ed-5eb1-9098-5ffc605ae160 | note | Specification Reference - WBS-SS-CI-SPC-0006
da211c9a-0793-5138-90e1-433cb41258ce | note | Conformance Criteria Summary - Results included in work pack
0c9bd694-eea8-5e54-9736-c6c9342b7cc5 | note | Method - R
cb926d55-afe2-5620-b8b4-795b2928b97b | note | Frequency - PW
dbc1dcde-d837-5ea4-8960-bddb77539d76 | note | Hold/Witness Point Requirements: ROBAR - V
70e19a14-9c94-5f9a-bf8d-a0e6426c1360 | note | Hold/Witness Point Requirements: SEPD - NA
63312388-8d5d-588c-9d80-43f9dd25d2e3 | note | Hold/Witness Point Requirements: Client - NA
c2f3c05c-8489-52f0-abfa-3f1e7ee5f9f9 | note | Records or Checklist Document Number - IFC Drawings
26a56964-cefd-49e6-b86a-99b899ebad17 | checkpoint | 1.2 - Permit approval (GDA/GDP)
181fbc36-0c87-5125-b776-d46f1fbfa249 | note | Responsibility - SE/PE
c384d9c2-95c8-5619-b80c-433fa963586a | note | Specification Reference - WBS-SS-CI-SPC-0006
e9046fd9-fb2f-5fb1-8b58-1bdaef79dc34 | note | Conformance Criteria Summary - Approved excavation permit (GDP) prior to commencing works
f8891bf4-4e40-5294-b700-8663dfe2511a | note | Method - R
41ec940f-bc63-5b16-b09e-0d84f531f61a | note | Frequency - PW
a2aedd50-b396-596a-a9ac-290a678e8c8c | note | Hold/Witness Point Requirements: ROBAR - HP
9d26b4f7-a0ee-5a74-a299-e8728060e637 | note | Hold/Witness Point Requirements: SEPD - HP
0a8dac73-f512-5156-a30d-00390494ecbf | note | Hold/Witness Point Requirements: Client - NA
4252bcd5-9765-5a62-a33d-cb2164e31524 | note | Records or Checklist Document Number - RR-SEPD-CI-SOW-002-01
fe2d3215-616d-4c4e-8e97-b61e1c747704 | signoff | HOLD POINT
f585a2e6-bcdb-49de-8e67-3579fa5c7292 | checkpoint | 1.3 - Site set-out
fcf9d8df-3bfb-542d-a651-831cb0047dea | note | Responsibility - SE/PE
a6305e80-7e9e-5a3a-9ff4-4b4f43cef341 | note | Specification Reference - WBS-SS-CI-SPC-0006
1a27382a-4567-5502-97c7-4873db123967 | note | Conformance Criteria Summary - Verify levels, site boundaries, and physical bounds per IFC drawings
b6211579-1202-5758-9fb2-640df1d3ba25 | note | Method - R
24792a94-b2ec-5b35-a948-317f5de8910c | note | Frequency - PW
6c036614-438c-537b-99d9-36590fc17cc3 | note | Hold/Witness Point Requirements: ROBAR - V
a5c59ab1-7895-50af-888f-04d4c46f8308 | note | Hold/Witness Point Requirements: SEPD - NA
93bd7cd7-748e-5f1d-ae32-f456e3f71105 | note | Hold/Witness Point Requirements: Client - NA
890f900e-2c7a-53be-8b81-7a06c7251042 | note | Records or Checklist Document Number - IFC Drawings
6d96e2a7-7e12-46c4-a019-688797ea0931 | checkpoint | 1.4 - Sediment control plan
28bbf8d2-77d0-5211-b5b2-4150183eb337 | note | Responsibility - SE/PE
1d7b93cd-0cb1-566c-a564-bb783a564ce1 | note | Specification Reference - WBS-SS-PM-PLN-0024, WAE230103-03-003 TM Rev0
a4ceab7b-56da-5874-a76f-fa1b5e25a2f1 | note | Conformance Criteria Summary - Sediment control measures in place
f98306a0-a1ae-50fa-95e8-ea3a1e482f7a | note | Method - R
2c5ae9cc-914b-53b8-aca4-fd45b66ae0a2 | note | Frequency - PW
ae5c7e9f-bbab-5feb-a8fe-71dfb6362fc8 | note | Hold/Witness Point Requirements: ROBAR - V
6c2668fe-9d3b-58eb-810f-8d0c33fd7c3e | note | Hold/Witness Point Requirements: SEPD - NA
9afa84a2-9df3-51d1-945d-5eef20e778cf | note | Hold/Witness Point Requirements: Client - NA
87ceb740-8b04-52ea-aa2a-83b8557331e3 | note | Records or Checklist Document Number - SEPD environment-al plan
e9282161-19a1-4690-8aa7-5d5c56e3f968 | checkpoint | 1.5 - Dust control plan
20865913-c2ae-5dfd-9f53-78bf3d512b2b | note | Responsibility - SE/PE
a4927cc6-c434-5362-b50e-b13e420335cb | note | Specification Reference - PP3 section 1.5 and section 4.1
9ceddbeb-632d-5911-a67c-3e32534a5a1f | note | Conformance Criteria Summary - Dust control measures in place
bbde52a1-8a7b-59ef-a258-8114ba8c0b39 | note | Method - R
a7de38da-0f7d-52f0-a199-6e7c6808f344 | note | Frequency - PW
c0e41ad6-dfa6-5df5-b283-0f114b063588 | note | Hold/Witness Point Requirements: ROBAR - V
357a855e-6abe-5eea-bb99-b32b5fc10db0 | note | Hold/Witness Point Requirements: SEPD - NA
05ca8daf-1690-5278-bca9-2fdfbcbe65de | note | Hold/Witness Point Requirements: Client - NA
cc44d686-d3d2-5ea1-a9c3-277159fa9198 | note | Records or Checklist Document Number - SEPD environment-al plan
0d8e3b65-3346-41c8-a87c-796d04c01156 | section | Section 2: Materials
1db4105c-99ea-4a99-b1ee-904d78f7cc5b | checkpoint | 2.1 - Import fill material inspection
acca818f-5d20-511f-8bdc-5c1fdf2de180 | note | Responsibility - SE/PE
6f98fe80-e26d-5d04-8b3a-47634020ba74 | note | Specification Reference - WBS-SS-CI-SPC-0006
b00ba6d2-bcc4-590d-8ee0-c1536e513118 | note | Conformance Criteria Summary - Material certificate and test report for particle size distribution, moisture content, MMDD
3e0e2000-cbee-5993-9d3f-47671e7a6802 | note | Method - R
0aeebea1-19c5-5aa6-8d22-2eb2069cf25a | note | Frequency - PW
2c79cc86-928a-5356-86c0-dbb90fb0ace7 | note | Hold/Witness Point Requirements: ROBAR - V
130008e6-2abc-526d-9a1d-12fface921bd | note | Hold/Witness Point Requirements: SEPD - V
d42ce498-e38a-53af-9c84-2146152fbabd | note | Hold/Witness Point Requirements: Client - NA
0ade8a38-9005-5a74-a7dc-f62d0af88d76 | note | Records or Checklist Document Number - Material certificates
cdc19136-59a5-4850-bf29-c4292435e444 | checkpoint | 2.2 - Verify suitable foundation material (compaction >95% MMDD)
0234c66c-cb17-50dd-a85b-d0d0c3076efb | note | Responsibility - SE/PE
ba23a6d0-f415-57d6-b045-221af3f0d771 | note | Specification Reference - WBS-SS-CI-SPC-0006
63afde34-2d4d-5be8-b7e7-bccf6f820e24 | note | Conformance Criteria Summary - Geotechnical test results showing compliance
9e7c624e-62f3-5bf6-8d9a-3ebc53a1705d | note | Method - R
8e4eadfc-7931-5bc8-89a3-e685b1c5b4ba | note | Frequency - PW
24a8f820-75e3-5985-b757-ca9ef7bdc93f | note | Hold/Witness Point Requirements: ROBAR - HP
ea1c18e0-fa29-5d62-ad79-584ac1e10913 | note | Hold/Witness Point Requirements: SEPD - HP
6813823b-d5e6-5a82-82a5-39a3e00e6218 | note | Hold/Witness Point Requirements: Client - NA
95b2f260-9f23-53a9-a968-19c6956f254b | note | Records or Checklist Document Number - Test results
63d8d3a9-05df-4fb2-9c2e-459760a59c6a | signoff | HOLD POINT
989f26da-fed7-4ea1-b745-6c967162e14c | checklist | Project Photos |  | Project Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2f595e7f-92f4-4834-a1eb-63e97455c8d0 | checkpoint | Upload site photos
326668f9-3d34-495a-b04f-15a1bb0c11f5 | checklist | RR-SEPD-BESS-FIC-001-01 - Earthworks | itp | RR-SEPD-BESS-FIC-001-01 - Earthworks -
87b5eb07-576f-4c2f-b86c-7a82e5812db1 | section | Part 1 – Preliminaries (photos where applicable)
744ef392-bb3f-45c1-8004-612dea734f3d | checkpoint | Review of approved construction drawings and specifications
6f0e6ad6-89f4-5e73-b949-489845d4a418 | note | All drawings and specifications approved and up to date
44cad7ca-783f-5332-b20e-8fb7678881b5 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
8b1d093f-7f56-4ff9-ba46-fdd1e5392c13 | checkpoint | Verification of permits
b7be4f80-1cc7-5bfe-982c-076df4399b70 | note | All relevant permits (GDA/GDP) in place
f33d6102-4868-5d03-bf84-a6ecdfacff7b | note | Specifications/Drawings Reference - GDA/GDP
ff9a08fe-3b3b-4332-9cff-6062ace46577 | checkpoint | Site access and safety preparation
3c444e26-6cc0-5e64-8b8b-ac923e4164bb | note | Site access cleared and made safe
c4f04b07-133b-5075-80a9-e4757167b708 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
8277fff3-b62a-4f92-95da-7c42305b1066 | checkpoint | Safety inductions and toolbox talks
cd737a2d-b8d3-556b-8c5d-b6f33a4923d9 | note | All personnel inducted; safety briefings completed
22fc95ef-c494-5f03-b0d6-a372fcfec36b | note | Specifications/Drawings Reference - Induction record
02e91297-3dfc-41e7-94ae-514b8d678b45 | checkpoint | Environmental controls in place
be7d955d-9f62-5532-b906-09b977ad2a9a | note | Dust, noise, and sediment barriers installed and functioning
44e955b1-9fef-5c42-adf4-b772786f8e59 | note | Specifications/Drawings Reference - SEPD environmental requirements
26ed3d4c-d985-4e94-86c5-f4afec09407d | section | Part 2 – Set-out and excavation (photos where applicable)
77408a55-0ccc-4fb5-9301-3bcc34e1d8b2 | checkpoint | Site set-out verification
1c3438b4-b05e-5510-a48b-e43f82e19b29 | note | Set-out verified and matches IFC drawings
710ee0c9-d13c-5606-9538-84940b38a330 | note | Specifications/Drawings Reference - Site IFC Drawings
8adc9b2c-c704-4d62-9d4f-a051b8e35859 | checkpoint | Excavation to design levels
62d4ce23-a61c-53cc-96ea-3113f13e1694 | note | Excavation within tolerance of design levels
d5da907d-904a-5616-8322-e16f2d09cbd1 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
a02eb524-821f-45ca-9277-6754dadbecfe | checkpoint | Stockpiling of excavated material
8372dd4f-35e1-5a0d-af45-fa68e7a719e4 | note | Material stockpiled properly, no contamination
8793284a-7ea8-5db6-9c5c-973ea6ea9e47 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Galt construction sediment control plan
b1d9772c-5c27-4364-a1de-04db1123220d | checkpoint | Subgrade inspection
a9cc5602-680a-5e10-993b-78fd0310a105 | note | Subgrade verified, compacted and stable
b99cb831-aae1-5ca5-b38f-22c05739f05e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Geotechnical report
f50ed6fe-d6f9-4421-b777-b857ad1a4838 | checkpoint | Principal Inspection
9fc4e47e-4748-5f37-94d6-95c75727eb1e | note | Principal’s Project Requirement to have principal release the HOLD POINT for backfilling foundations
704c35a8-2cfa-5b6e-a95c-61319819d8ae | note | Specifications/Drawings Reference - Principal Project Requirements
70f1b27e-7798-4ebd-a45f-58c25fc18a24 | checkpoint | Subgrade compaction testing
87a6505d-6051-56ae-a528-899e6b86c816 | note | CBR and compaction results meet project criteria
33cb3965-0f15-5ec9-b24e-92491629b524 | note | Specifications/Drawings Reference - AS 1289 Geotechnical report WBS-SS-CI-SPC-0006
6a4da468-598e-4c1b-92f7-dd56a304062e | checkpoint | Proof rolling of subgrade
01dfea3b-80f2-52c5-b469-2bd84ec22c51 | note | Subgrade proof-rolled to confirm stability and detect soft spots
a3e95d4e-989b-5ea5-8445-960651db6634 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
edbe548a-c49b-4c74-a48d-0b42c874a7cc | section | Part 3 – Fill material and compaction (photos where applicable)
de39163c-0e46-47ac-9021-6824015056f6 | checkpoint | Imported fill material testing
d056ee87-e0d7-52ab-8376-f0df8008d018 | note | Material complies with particle size, moisture content, MMDD, Die back certificate
7a12e6ce-5912-5e38-9e06-2b86062d74d5 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 Test material results
58d1fed3-2301-45a0-9b43-ba4062d031ae | checkpoint | Fill placement in 250-300mm lifts
f88395e3-aa3b-5abc-ba20-702209ea54e7 | note | Layers placed in maximum 300mm (loose) thickness
ea04e54e-4d2f-5a65-a07b-bb7d7c27d486 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006
69bc23fa-6a29-426e-b40b-d24785ea0999 | checkpoint | Compaction testing
d906db38-7477-5f60-9966-9be6761281b5 | note | Compaction >95% MMDD
c0514e17-a8c8-5df0-ab82-40e57c9534d9 | note | Specifications/Drawings Reference - AS 1289 Compaction test results WBS-SS-CI-SPC-0006
22d067fd-7c55-4d53-8b5e-6525e03828ff | section | Part 4 – Environmental and erosion controls (photos where applicable)
752ff6ee-5433-4990-bcf6-17786d554c7b | checkpoint | Dust control measures
e9565d8a-a0ec-549b-a11e-4ad82386c985 | note | Dust suppression methods in place and effective
9dba82b7-6003-556e-ab28-0204d526d2e2 | note | Specifications/Drawings Reference - SEPD Environmental Plan
05f8d015-431c-4995-ba8f-0c6cf8037b89 | checkpoint | Erosion and sediment control measures
a86a2dcc-f6df-541e-963f-6a3e7f0caa3d | note | Sediment barriers, silt fences, and basins installed and maintained
14e05556-4771-5116-a836-3346afc44285 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0006 WAE230103-03 003 TM Rev1 CESCMP
e0cd18a2-22a7-4d77-bb43-59239dcc0ce5 | checkpoint | Site drainage
3487a660-65a1-569b-847f-3e14c942ef04 | note | Temporary drainage in place to control stormwater and prevent site flooding
5ef1b87e-9c12-52fa-8dfe-3ef5d250b76b | note | Specifications/Drawings Reference - Drainage Plan Site Inspection Galt construction sediment control plan
018e0979-e3db-4708-877d-1840c866d3cc | section | Part 5 – Final inspections and acceptance (photos where applicable)
db3333a1-736f-4e20-8b47-826e944d804b | checkpoint | Final surface inspection
6e89f35f-2449-5df3-9c8d-b6b0d59582b8 | note | Surface is stable, free from defects, and meets design criteria
276cae38-a1b9-5fb4-a27b-2cfea0f65948 | note | Specifications/Drawings Reference - Site inspection Proof roll
e64612cf-8790-48c0-8603-ae5a3254d227 | checkpoint | As-built survey verification
c716100f-eaf5-5774-8cdd-2257c0cd75c7 | note | As-built levels and layout match design
c654e383-7297-5e6c-adeb-a1814a3f91ae | note | Specifications/Drawings Reference - As-Built Drawings Survey Report
1a5b28da-e51d-4fd8-94ff-70f9f62679b8 | section | Document Sign-off
ab136bcf-2721-448a-9da3-e20f41ec1e49 | checkpoint | Prepared by
ca84f374-4c64-5cd2-8481-5c07a55acae7 | textbox | ROBAR - Name:
1f8edddb-3353-5014-a2df-41e5a4dc66f6 | textbox | ROBAR - Position:
98308999-ecfe-50f4-a33a-33e5ad8ef017 | date | Date:
4f3d84aa-f3a2-4d0e-97a9-ec7a15828610 | signoff | Add Signature
e67c9062-1257-4597-a150-b59aa3a48eeb | checklist | RR-SEPD-BESS-FIC-002-01 - Concrete Works | itp | RR-SEPD-BESS-FIC-002-01 - Concrete Works
97531fa1-8e70-4bd0-8938-256a1a8cc941 | section | Part 1 - Preliminaries (photos where applicable)
73aa77b7-ade6-4e60-95e4-feb19198e094 | checkpoint | Review of approved construction drawings and specifications
2727464c-98cc-52f5-bd08-c825a8eb7f5b | note | All drawings and specifications approved and up to date
6c3b19e1-669e-50bb-ad55-49e74dd6a647 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-007
bd92b514-1851-4e33-885d-8f0e59bf8da6 | checkpoint | Steel mill certificates
0035b5b4-49c6-5b22-94fa-d4555eaf5cf4 | note | Steel schedules and Mill Certificates verified and uploaded
56730e48-422a-49c6-bb35-41db7ae9e94b | checkpoint | Lot map
eebfaf4a-a500-5207-8f01-68c3d7cae2a8 | note | Lot map markup created and uploaded
aa02a855-c7ea-46c3-95e7-4c76126a1f78 | checkpoint | Verification of permits
630db3d5-dd49-5458-a025-e14883cd047c | note | All relevant permits (GDA/GDP) in place
b4fd9c06-30be-5375-a77e-bad44be3be44 | note | Specifications/Drawings Reference - GDA/GDP
c338dedf-87be-4619-826e-26a206fc78f5 | checkpoint | Site access and safety preparation
4a761837-32ce-556b-ad7c-439091c41a6a | note | Site access cleared and made safe
75010945-96b4-5b54-bf3f-4241701a7c6d | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-007
9933934f-36cc-46de-bb6a-94682db37262 | checkpoint | Safety inductions and toolbox talks
02e4e6ee-0ae3-5c94-9805-f2229aaa78a6 | note | All personnel inducted; safety briefings completed
6f518f86-a7c2-5033-8969-13731569e5cd | note | Specifications/Drawings Reference - Induction record
16c590e8-06a0-4bdb-a72b-083f89a8bc20 | checkpoint | Environmental controls in place
012e6832-9e77-5746-b991-d0497ee1a416 | note | Dust, noise, and sediment barriers installed and functioning
b3985007-3aec-5724-ba64-64b03b1b000a | note | Specifications/Drawings Reference - SEPD environmental requirements
77f6771b-1790-4751-baa0-2d42f058f126 | section | Part 2 - Survey (photos where applicable)
55783876-995f-4bfa-94d4-cab35fc59a95 | checkpoint | Setout location
42d47ccc-a50b-5258-817f-64a8c9e43a26 | note | Slab set-out conforms to approved design coordinates
8a0135f0-3821-5f65-8bbb-df8a8874981b | note | Specifications/Drawings Reference - Site Layout Drawings, Survey Plan
05cee545-64ae-4e81-a5e8-0baa31b7b910 | checkpoint | Level and alignment check
8994addf-d6da-508d-bc80-56967f8fd89b | note | Levels and alignment of formwork and slab position verified
53f4d84c-78d1-5879-8875-26595cf7534b | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007, Survey Report
3084a2d7-1b9c-4761-95d7-0d0f6cfcf090 | checkpoint | As-built survey after formwork and reinforcement
89fb7859-d945-5b31-9ddd-c9d477c6f59a | note | Survey to confirm reinforcement cover and formwork position
789f32f0-4a48-57df-b1b5-089f0262f720 | note | Specifications/Drawings Reference - As-Built Drawings, Survey Report
8b7fa29c-a2b2-432c-b35b-d8cbc8e864b6 | section | Part 3 - Pre-pour inspection (photos where applicable)
1540ac7f-4c40-4bf8-86df-703f79d81ee1 | checkpoint | Review of approved concrete mix design
23accabf-e0b8-5161-a901-bdfc28ccac6b | note | Mix design approved P3220100
93e1ddc7-8d37-5b85-9377-db2e7c7337c9 | note | Specifications/Drawings Reference - AS 1379, WBS-SS-CI-SPC-0007
504b36f6-3b9c-4f50-a8ea-ed28e3177ba1 | checkpoint | Formwork installation
383566d7-5a8a-5186-8680-91f12310d0f5 | note | Formwork aligned, clean, and secure; dimensions correct
245380c0-45a5-51aa-851d-cc6ad13807bf | note | Specifications/Drawings Reference - AS 3610, WBS-SS-CI-SPC-0007
899553bb-a214-409f-b57c-ebd801c69a39 | checkpoint | Reinforcement placement
c0fc234f-77bf-541a-a50a-03204290ae08 | note | Reinforcement size, placement, spacing and cover as per drawings
8421dc20-23ad-54fd-9d1a-eb86fca8655e | note | Specifications/Drawings Reference - AS 4671, WBS-SS-CI-SPC-0007
2e912fe3-37fb-49be-8098-c602abaae4f6 | checkpoint | Reinforcement ties
be900450-a4d0-5225-b1b2-a02ceebb3c31 | note | Reinforcement securely tied in place, no loose bars
7c88349e-e273-5f2d-846e-d3dc8be5004b | note | Specifications/Drawings Reference - AS 4671
914b0012-8d33-48c3-8237-71c22d52c17e | checkpoint | Installation of dowels
693821b5-ab72-5ba8-b67e-f0da7685ba4d | note | Correct placement of all embedded items, dowels aligned
2a97dfc1-b45e-5f9a-bc30-8863396f4408 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
ef203b77-30b7-43d4-98e1-ace5e791117b | checkpoint | Waterproofing membrane
36646b24-737d-542a-a59f-216b0f9b7bd2 | note | Membrane installed per design; overlaps secured
8c4e0d71-d1ad-5b0a-a545-bc7796cbfe04 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
99e52d5d-1127-44c3-aac5-2c3287cbe59b | checkpoint | Crack control joints
4f7ce754-8667-5c8e-81e3-31b7cfb9eb2d | note | Joints placed and cut as per drawings and specifications
350e0c0c-8a4a-5baf-88c1-01f880b11d7e | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
bc60da28-8d12-478e-9eb1-a2c3468af046 | checkpoint | Construction joints
56a338b5-8ce8-59a0-a992-e561f99ed015 | note | Joints placed and prepared as per drawings and specifications
33abacb5-290f-59ae-918e-38d60ee05914 | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
8d19c651-accd-453d-8471-d215aa428c58 | checkpoint | Site safety inspection prior to pour
a5f25890-d039-57cd-a6a8-625a9e55f08f | note | Site clear, access routes checked, and emergency plans in place
a448061b-6824-5546-b1ef-1ba4b2aa8286 | note | Specifications/Drawings Reference - Safety Plan, WBS-SS-CI-SPC-0007
4a6337f1-e2da-4b3b-9a81-e091db2d9663 | section | Part 4 - Concrete pouring and compaction (photos where applicable)
12945ad2-b1fb-49a2-a2a3-2349ee5c7948 | checkpoint | Concrete delivery
2dc6cf20-7815-5e92-bc90-6356bb688f5a | note | Delivery in line with approved mix design
f3447ec1-084d-5a1f-9a08-7cdb8e6a16b2 | note | Specifications/Drawings Reference - AS 1379, Delivery dockets
5b784a47-f8d5-4b22-ab3e-11d2d540e881 | checkpoint | Slump test
72907292-bd41-57c5-907b-d750430fc888 | note | Slump within specified range (e.g., 100mm +/- 20mm)
97fd5123-dc31-5ed6-ab17-bc1a96987679 | note | Specifications/Drawings Reference - AS 1012, Slump Test Results
5db39adb-cf85-450e-874d-6f5ba8798ef0 | checkpoint | Concrete placement
906c62fa-6906-5e91-9625-abdb2dc45244 | note | Concrete placed within formwork without segregation or delays
fd07646b-d9c8-50b5-844e-b3c924f99ea4 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
c13faa7b-37f7-4278-b17e-43a94144694f | checkpoint | Compaction of concrete
05744d26-5d79-5b13-aaa5-7029fca0db2f | note | Concrete compacted using vibrators, no visible voids or honeycombing
c4102f86-bb81-5af6-b1b7-03318728a4d0 | note | Specifications/Drawings Reference - AS 3600, WBS-SS-CI-SPC-0007
cbef00f4-13e4-43a0-ab06-b06e7d94d2c9 | checkpoint | Cylinder sampling for compressive strength
4f9dcdd9-8608-56aa-9779-91aa503e0ed3 | note | Cylinder samples taken for 7, 14, 28-day tests
aa458440-88fb-5d19-9ccd-c373f588ec38 | note | Specifications/Drawings Reference - AS 1012, Sample Register
9c89d006-353b-4b03-a9d0-0e349082f97c | checkpoint | Concrete temperature monitoring (if required)
9c9b7cc3-8649-5432-bac4-7c1fc2068dc0 | note | Temperature recorded during pouring
5034577c-75fd-5b9a-a01f-7c7f43b924ac | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007, Pour record
cb0248b8-7935-4f72-acac-a4d9e30956fb | section | Part 5 - Post-pour inspection (photos where applicable)
8dd79ea6-2d6a-4930-b126-ebcb1dfb8bdd | checkpoint | Surface finish
c172d179-0ee6-59a9-8a30-235b99c7e65d | note | Class 5
0080eae1-8d54-53c0-ba2b-c064e1289a42 | note | Specifications/Drawings Reference - AS 3610, WBS-SS-CI-SPC-0007
9816562d-bf04-4d7b-af87-20601698a89d | checkpoint | Curing method
6996bae3-cb29-5afe-91bf-477db268632d | note | Curing compound or wet curing applied as per requirements
e32033a8-61db-5a30-aa7c-724100adeb72 | note | Specifications/Drawings Reference - AS 3799, WBS-SS-CI-SPC-0007
0829052d-8d7b-401c-b45a-01ca813e7a60 | checkpoint | Formwork stripping
d3d2f44c-7992-533a-a573-c87c42db00d7 | note | Formwork removed after concrete reaches required strength
5f253170-ccf2-50b0-bda7-2929d5b38e98 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
2cb242af-f7e3-4121-85ca-36cdc298531e | checkpoint | Compressive strength testing
1967ef0e-d91b-5dd5-8173-974911f28732 | note | Compressive strength results meet >32 MPa at 28 days
42cb11ef-f217-5211-9f30-a97697c517e4 | note | Specifications/Drawings Reference - AS 1012, Test Results
4bd5be95-2a03-43ac-8b6f-f8c0a59b2f81 | checkpoint | Inspection of surface cracks and defects
69dddd49-846a-50eb-8d2a-ca0bc0f444dc | note | No major cracks or surface defects observed
529a90d9-ef9b-559d-b145-a44e84803cc6 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-0007
ef76c153-fbfe-4447-a327-59fdc66f2e11 | section | Part 5 - Final survey and as-built verification (photos where applicable)
5c8efa4d-70e9-4f6f-b93e-f44891faef76 | checkpoint | As-built survey verification
24980e66-de23-5e8f-9c58-b63f8522cb1d | note | As-built levels and layout match design
8bd0d860-ec64-59f6-8faf-1036219282e7 | note | Specifications/Drawings Reference - As-Built Drawings, Survey Report
881716bc-df4c-4021-ba8f-f34abfe9e3d5 | checkpoint | Final inspection sign-off
7e4c8a72-14b9-5c4d-960d-8a39407f9811 | note | Final approval of the slab surface, dimensions, and finish
76f72e52-62c6-5b50-9c2c-9425fb134d23 | note | Specifications/Drawings Reference - FIC sign-off
e593606c-8846-4fa9-840b-e18534959f34 | section | Document Sign-off
68d9bb92-f5ab-4ab0-98ef-37e5eafe834d | checkpoint | Prepared by:
7e60fb1e-903b-5255-8a80-ed5bad72b807 | textbox | ROBAR - Name:
982ea418-d3d5-524e-a961-ee00d070466b | textbox | ROBAR - Position:
8201cdc3-2dc2-5660-9afc-c14933d03ce7 | date | Date:
e9e1d579-f4fa-4c8e-9be2-12dc92d550ae | signoff | Add Signature
ed1b3f07-1209-4ac9-9199-408ef2ac27f6 | checklist | RR-SEPD-BESS-FIC-003-00 - Electrical trenching | itp | RR-SEPD-BESS-FIC-003-00 - Electrical trenching -
9be8e05e-8d2f-4364-a902-a3eb539ffa93 | section | Part 1 – Preliminaries (photos where applicable)
3de113b1-49d3-43b8-8bdc-61c087dd6844 | checkpoint | Review of approved construction drawings and specifications
ddb17d71-ec74-5f88-a31a-597b83bc3477 | note | All drawings and specifications approved and up to date
6bd43aff-cfd2-5cf5-923b-2b4cfbef73b1 | note | WBS-SS-CI-SPC-006
98b6d8f2-4143-44d0-bb4d-0372fc69f7e7 | checkpoint | Verification of permits
bf87e8ba-92c0-529b-a3df-9aadaeb22fdb | note | All relevant permits (GDA/GDP) in place
584850db-e213-57da-b610-97cf34bd3e86 | note | GDA/GDP
45a660f7-c974-4d2a-b762-4629a474d9c6 | checkpoint | Site access and safety preparation
464c6b53-3ffa-531a-ac36-e2a70aa874ed | note | Site access cleared and made safe
332167b5-6f93-52c3-b3a2-9f532787626e | note | WBS-SS-CI-SPC-006
36157673-e14b-4e47-a472-d4c3b06d8008 | checkpoint | Safety inductions and toolbox talks
afc235e2-da58-529b-9771-50f062e7ce3b | note | All personnel inducted; safety briefings completed
73cb2989-f1c1-57ae-8705-26c3a5ff10cf | note | Induction record
38d5b86b-b0a1-4e92-bd36-7e02084e7183 | checkpoint | Environmental controls in place
0811f436-c29b-5fa7-a851-1fea426dcd1e | note | Dust, noise, and sediment barriers installed and functioning
c1123f52-9e66-5fad-b3cd-eee1e3d34728 | note | SEPD environmental requirements
6f63129f-fac4-4562-b120-ae0dca8dacb7 | checkpoint | Utility identification
65d23780-7a9e-5e62-96b4-5b1fc42d7e96 | note | All utilities marked as per drawings
bd729b3c-f19e-5502-b1c1-5e3106929eac | note | Project as-built drawings
c171574d-8bdf-4117-a1fa-539536c74184 | section | Part 2 – Set-out and excavation (photos where applicable)
baeeaef0-4683-42d7-9bb6-6c0b34365166 | checkpoint | Site set-out verification
dd5f90f4-df5c-5065-bd2b-7eb23e3cc619 | note | Set-out verified and matches IFC drawings
9acb22e3-8066-59dd-ad65-00de3ca817c1 | note | Site IFC Drawings
cc63f691-1278-496e-8af0-cb7ac7dca685 | checkpoint | Accurate dimensions
58670990-9377-5248-a544-ccaeae6978c2 | note | Width, depth, and alignment match design drawings
0962aea8-d744-58a4-ba6a-c36fff9a6815 | note | WBS-SS-EL-DRG-3005
6561375e-de0c-42d7-b240-70cc3b81877e | section | Part 3 – Excavation (photos where applicable)
065a93d7-fbb1-4869-b25a-cd587c3eb7fc | checkpoint | Dimensions maintained
79fe999c-cefd-524b-90b0-0e1eafe4084c | note | Depth and width meet design specifications
0a338676-9a67-5d9c-96fd-3ca6a9cf1015 | note | WBS-SS-CI-SPC-006, WBS-SS-EL-DRG-3005
08474ac2-512c-4997-99c6-919db9b4c7f0 | checkpoint | Stockpiling of excavated material
c348d6e8-7652-5f51-a7c5-5229763b11a8 | note | Material stockpiled properly, no contamination
03e8c56a-25c9-5d38-9769-a18d41c9dea3 | note | WBS-SS-CI-SPC-006
77f10001-66e2-49c7-8463-8b94d5b1bca9 | checkpoint | Stability of trench
8bd40298-3997-513d-8ac6-6e017bcde13e | note | No loose soil or collapses; protective measures in place if trench is over 1.5m
44b63f59-ab62-5dbf-a154-f81680ed39bf | note | WBS-SS-CI-SPC-006
c4992538-e022-4d36-b1f9-fd223af7de59 | checkpoint | Subbase inspection
bb2538c5-3e0a-5063-baa5-e8d493e33829 | note | Subgrade verified, compacted and stable
69b537f2-db89-531d-82eb-33fb834b1273 | note | Geotechnical report
8dd4b1cc-e163-4999-b1f7-af4915c5b8fe | checkpoint | Subbase compaction testing
5d34349b-2bd7-5d14-93f7-a3302f249b6d | note | Compaction results meet project criteria. 1 test every 40 linear meters and 1 every two layers.
69c44ffe-7489-57a3-b338-c5666176a96f | note | AS 1289 geotechnical report
8c2dfa5e-d01b-4d54-891b-9dafc367147e | section | Part 4 – Fill material and compaction (photos where applicable)
fc43104b-eb16-4089-a9fa-ffcb18901bce | checkpoint | Backfill material
afd15ec5-1440-5a9a-bff0-78670dbffee8 | note | Approved material used for backfill
eb9eca80-422e-5fa9-b5b2-a8048ba66fb0 | note | WBS-SS-CI-SPC-0006
615225df-6641-412b-afd1-64121ed34929 | checkpoint | Imported fill material testing
9b3a5580-58a6-57d1-a769-e4ccc2d769d7 | note | Material complies with particle size, moisture content, MMDD
af27ff75-237f-5492-bee6-18f00bc85815 | note | WBS-SS-CI-SPC-0006, Test material results
8115da33-e4f7-4fa0-9405-484f2ddb30fc | checkpoint | Fill placement in 150mm layers
a869181d-85d4-5226-8f38-0b2d040189d0 | note | Layers placed in maximum 200mm (loose) thickness
55cdad9b-aea3-56b5-9dc9-6a229fa89058 | note | WBS-SS-CI-SPC-0006
e970c9a1-5a54-46a7-a26e-f80d2a18bd82 | checkpoint | Compaction testing
b7288d7e-11d0-5ebb-ac50-9e26f678cff3 | note | Compaction >92% MMDD for general fill
e58b3b26-f56e-5f79-89a2-4d4badfe5c3f | note | AS 1289 Compaction test results
a1b9a602-28c0-4560-9416-b15c583d8162 | checkpoint | Level and grading check
e2bc6ff0-d0e9-5815-ba3a-b97e10b8a03e | note | Levels and grading match design tolerances (+/-20mm)
ae5d545b-d989-5824-a2cd-86763f105919 | note | WBS-SS-CI-SPC-0006, Survey Report
bd252a46-fd06-4a8c-97be-75b0f017786b | section | Document Sign-off
e34b23a1-9a16-455d-ace1-de77c990ec42 | checkpoint | Prepared by:
ff920a5d-566c-5898-9a0a-8a71a1a3c414 | textbox | ROBAR - Name:
6fcadfd2-dd87-5302-93a2-ff95e240ba4d | textbox | ROBAR - Position:
a81403fb-6a58-5292-b6b4-dd38a419727e | date | Date:
049bca66-6776-4bf2-a566-65dafcb53e18 | signoff | Add Signature
22ef4b64-570c-4f04-8ab8-77e2a18321b7 | checklist | RR-SEPD-BESS-FIC-004-01 - Proof roll | itp | ROBAR FIC ¦ (insert material) ¦ Proof roll Layer xx - RL xx.xxx
d1f978cf-bf8a-41fa-b95e-7a6bfd5fc925 | section | Part 1 – Proof roll (photos where applicable)
e9ad6f2f-ba11-4a5c-b9fc-5fc78869d5bc | checkpoint | 1.1 - Smooth Drum Roller – 12t
ac59aba5-2e75-50a6-9209-6d20680ecb62 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
aaacc864-e29e-4e90-8060-52201efa1d48 | checkpoint | 1.2 - Plate compactor – 0.75t
15888de4-f925-5440-872a-3f93219a8d62 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
ddda332a-7f42-401f-b435-eeb363a81efd | checkpoint | 1.3 - Single pass with smooth drum roller to cover the area for the proof roll. If any doubts remain after a single pass, any subsequent passes, yet no greater than four, further compaction works shall be carried out till SEPD supervisor and PE are satisfied that there are no visual subgrade defects.
38316a20-1dcd-528b-b3ce-c5aada29701e | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
870a11af-e1d6-462f-9c97-5d81d3d5990b | checkpoint | 1.4 - The speed of the pass shall be constant and sufficient and no greater than walking speed.
3c31a49c-f68e-553c-9c69-714c74c8c562 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
dd2bc782-5158-446a-ab08-abd29316511b | checkpoint | 1.5 - No proof rolling to be conducted within 2m of footings, foundations or retaining walls. Subject to a visual assessment and the principal’s approval, any compaction within this proximity of civil infrastructure shall be only achieved using hand compaction methods.
a6a44f92-8b19-581c-8171-32002b17b4f4 | note | Specifications/Drawings Reference - WBS-SS-CI-SPC-006
889d9253-351f-4e5a-9227-ab14dc8fe01b | section | Part 2 – Comments
87dcc43d-c749-4468-a07d-b40228c5d4f7 | checkpoint-no-value | Comments:
afcac34c-0667-4528-9417-fcd26e73899e | section | Document Sign-off
3042148d-1bd7-4489-9246-82899ad354e3 | checkpoint | Prepared by:
d2c2cf7d-d312-5bc6-a7d4-4823c5e1dbfb | textbox | ROBAR - Name:
94b34830-f4c7-5edd-aec3-e80fdf92bfc7 | textbox | ROBAR - Position:
cbdabcd8-6241-5219-b6de-61e69b3e695c | date | Date:
6964c87b-a9d5-40c0-b334-7ec92f5e1b34 | signoff | Add Signature
743b05c7-880a-4a04-861e-f12cbce2c9fc | checklist | RR-SEPD-BESS-FIC-005-01 - Drainage installation |  | RR-SEPD-BESS-FIC-005-01 - Drainage installation -
b90f311e-b0b2-48c9-a174-7f56d4271296 | section | Part 1 – Preliminaries (photos where applicable)
391a5ae1-943d-46af-b010-3140891f2ed6 | checkpoint | Review of approved construction drawings and specifications
f6342505-b25a-51ab-b27a-1de7a80e5994 | note | All drawings and specifications approved and up to date
695d8195-71a4-56d3-a8cb-1f759bcb9c54 | note | WBS-SS-CI-SPC-006
9ed20f6f-3c37-46a7-808d-0472c512ebca | checkpoint | Verification of permits
7f317b9d-2f3a-52fc-9cf4-4f15c3d34bf7 | note | All relevant permits (GDA/GDP) in place
16f9fb0e-965a-516b-a065-1d1ce54cc878 | note | GDA/GDP
db4b78dc-9188-4741-aadb-9ad9496e388b | checkpoint | Site access and safety preparation
5de02b12-6f00-58e6-8f3b-0c9d8c31442c | note | Site access cleared and made safe
3cae6661-0b8f-5857-8494-1680a6e53564 | note | WBS-SS-CI-SPC-006
9e4a987e-a2d8-4ccc-a3c1-145c04c1b7fe | checkpoint | Safety inductions and toolbox talks
5dd35bb7-3ff8-535e-af25-3598d5b7fa5e | note | All personnel inducted; safety briefings completed
2ad7e96a-24b0-5191-9492-2b12e864103b | note | Induction record
81bd5a06-6ded-49f0-8a44-ef1825b6ec98 | checkpoint | Environmental controls in place
f2c11c05-abb5-540a-9e4e-f355cf02fef2 | note | Dust, noise, and sediment barriers installed and functioning
13f28080-b447-54cf-bf7e-2d35fd7394a7 | note | SEPD environmental requirements
5044381a-9051-40ba-a2e2-7a72eb348166 | section | Part 2 – Excavation and trenching (photos where applicable)
f410bf1a-48f8-455b-96ab-2b7ff007e019 | checkpoint | Subgrade proof roll & compaction
2b3a37d6-709a-5180-98c6-8687c1b7f56e | note | Subgrade proof rolled and natural ground conformant (ie. no excessive ground deformation)
98f19113-6fbf-5d62-b81f-8343ca5201d1 | note | Compaction testing performed on subgrade. 1x test per 2 layers per 40 linear meters
d33a063a-7ee3-44c9-8bcd-c53950b5707d | checkpoint | Trench depth and width comply with design
f52d88ae-acd2-59fe-97dc-6749c833a45f | note | Set-out verified and matches IFC drawings
5d0206a4-3452-5b9b-a987-4a191b091c5c | note | Site IFC Drawings AS/NZS 3500
5d2aede9-3681-4177-8c6a-3b207377ea0b | checkpoint | Stable trench walls (benching, battering)
a661bbfb-56a2-583e-a2cb-b884fae5777b | note | Trenches deeper than 1.5m require benching, or battering unless certified by a geotechnical engineer.
cec9a328-06bb-5a24-8f57-c0adf54c3105 | note | WBS-SS-CI-SPC-006 AS 4744
caa23a59-8519-41ff-b58d-56296a5ccb3f | checkpoint | Pipes visually inspected for cracks and defects before installation
9609f655-530c-562b-aab0-3d80fb657f22 | note | Material certs from manufacturer and visual inspection
58b2f5b8-543c-5d70-9ecd-2bc37a0be3ee | note | Material to align with design drawings and load rating
2511f9eb-1e45-50f6-9884-947e883ecae2 | note | Manufacturer certifications
dcd0c819-38f4-4c54-bdb6-7790cce47add | checkpoint | No water accumulation in trenches
31e701c8-65f9-5f5a-b557-151b0554e492 | note | No standing water or excessive moisture inside the trench.
7d480db5-1694-58d1-9546-3846876c07aa | note | AS/NZS 3500
e0e68ab7-f0c1-4dab-9c36-7ad63d99fc2c | checkpoint | Access and egress (ladders, steps) provided for trenches deeper than 1.2m
d56a7f73-f97f-5078-8820-8946d887ee56 | note | Access and egress for each trench.
e8182d35-f054-596e-81ed-e79975a936b6 | note | WHS
8386bb75-7c82-431a-8e57-08b313e54864 | section | Part 3 – Bedding & Pipe Installation (photos where applicable)
60144199-262e-4cc2-a756-05bfa2e2f0b9 | checkpoint | Correct bedding material used (sand, gravel, etc.)
db99c7a9-652f-5cf0-9724-9af661dcd16b | note | Material complies with particle size, moisture content, MMDD
73d654ad-3ee3-591f-b432-c9101fffb41c | note | WBS-SS-CI-SPC-0006 Test material results
09782c34-11a5-4a9e-9e30-e783ae5407b5 | checkpoint | Bedding placement
a55f0016-0f60-5c32-adbf-53e56552bb8e | note | 100mm thick bedding sand placed and screeded to correct heights for pipe placement
61b03917-0ab7-55e9-8119-b7474f1de30f | note | WBS-SS-CI-SPC-0006
7f81e170-de7d-496a-abcb-5e66a56c33f3 | checkpoint | Correct pipe jointing method used (rubber ring, solvent weld, etc.)
1993c0ae-d414-5d6f-a2e5-d0504f8110ff | note | Joints must be fully engaged and sealed per manufacturer specifications
49830ab0-bc4b-5ac0-8e35-f9d14d371522 | note | Manufacturer specifications
82105611-93f0-48cb-8628-a5b798a2d7b4 | section | Part 4 – Backfilling and compaction (photos where applicable)
df2d5a01-6c28-4128-93f3-7d19e08ab465 | checkpoint | Initial backfill material placed evenly around pipes
d70bc48c-a702-5e5c-bf53-2e02ba2c425d | note | Backfill material placed evenly around haunches of pipes
4dbeb5fc-f40a-4394-b24f-963e180a57d9 | checkpoint | Backfilling in controlled layers (300mm lifts)
9219e637-8b0f-5421-93bf-caedc92aa540 | note | Backfill in uniform layers of maximum 300mm thickness
775486c5-cd86-528b-bed2-da0e645ab378 | note | WBS-SS-CI-SPC-0006 Drainage drawings
810b5590-0369-428d-9c60-76cd0ac443f6 | checkpoint | Backfill shall be placed to a depth of 150mm minimum above collars of pipes or conduits
f757b803-b992-5121-a100-f97b9364a627 | note | Minimum 150mm above collars of pipes
72d22a89-b39d-5a01-aae2-f2c2bdc529bc | note | WBS-SS-CI-SPC-0006
e290f1b0-b3bd-4062-b47e-4acf56a1ec98 | section | Part 5 – Survey & Testing as-builts
dce702b6-b3e5-4f2c-b399-e65644bb5a8b | checkpoint | As-built survey verification
00bb7589-acd8-5f07-a259-13bd786f2ef5 | note | As-built levels and layout match design
c3d74251-e086-5734-92df-a724048e9f92 | note | As-Built Drawings Survey Report
70f914de-1b91-4acb-8d0d-ee173fe28755 | checkpoint | Backfill compaction
887692b2-6c9b-5dba-817e-ef973499736c | note | Backfill layers compacted to minimum 93% MMDD
2b47ce3b-923b-53fd-8aa6-0e93f1e68a22 | note | 1x test per 2 layers per 40 linear meters.
a277040a-eef4-5abd-9172-da9d7e9e410a | note | Site inspection
acc738da-39a7-423a-aa7a-cf3298c9f1cc | section | Document Sign-off
3b0f4903-6b18-4b88-8b0b-1a4c5b8b5285 | checkpoint | Prepared by
b90d460f-ca53-5606-a7a5-57af37cb9112 | textbox | ROBAR - Name:
7f8b4e4e-e1a2-5adf-8b90-a479a7d76c0c | textbox | ROBAR - Position:
44602056-170a-5ab0-bb34-4112d72e1870 | date | Date:
6d65e662-c6c8-4040-8e2d-0040e700a3f6 | signoff | Add Signature
ca094cde-8d88-408b-bd6f-723a9d951b5e | checklist | RR-SEPD-BESS-FIC-006-00 - Sheet Piling | itp | RR-SEPD-BESS-FIC-006-00 - Sheet Piling -
0c892eb4-92f7-4859-8a4c-36c4043b907b | section | Part 1 – Preliminaries (photos where applicable)
bf0b02e2-c9c2-4b0b-a5a0-d46837f1705b | checkpoint | Review of approved construction drawings and specifications
c015ba4d-c58d-55f6-9c8b-956214be49a9 | note | All drawings and specifications approved and up to date
fe553a7a-d9b6-5f7e-bdbb-8d118d1e50a0 | note | WBS-SS-CI-SPC-007
ae4b86a7-32f0-47e4-83eb-bb283a392006 | checkpoint | Verification of permits
29e7804c-9827-5dc7-bd0d-f6cccac5187d | note | All relevant permits (GDA/GDP) in place
aaca575f-9662-5cbd-bea8-1f0e1a4b45c5 | note | GDA/GDP
f2ce04fd-3b1f-455c-b03e-4b17b8bc9119 | checkpoint | Site access and safety preparation
450be298-91c5-5b48-90d3-ed474dc67c93 | note | Site access cleared and made safe
9ecaefd9-03b4-5b0a-9f57-18122ad14bd2 | note | WBS-SS-CI-SPC-007
7832ddc5-922f-42d7-81e5-d760b88e4055 | checkpoint | Safety inductions and toolbox talks
3bf2eb32-9111-532c-9bd7-f8cf55d45df8 | note | All personnel inducted; safety briefings completed
83383fda-aa8c-59fd-b3f8-75f71350706b | note | Induction record
1d811ae3-ea23-4923-86e2-ae319dd3cd51 | checkpoint | Environmental controls in place
e365aec5-f130-5db3-8efd-4717e9134251 | note | Vibration monitors installed and functioning
4a2930da-edd7-5bfb-9c30-f3dbd8fcec82 | note | SEPD environmental requirements
90b80c17-33db-4e91-8cdb-db2ff1e6d805 | section | Part 2 – Survey (photos where applicable)
e78872f1-f77b-4969-a546-f1cc617b77c4 | checkpoint | Set-out of sheet wall location
a1ac9604-ade2-5048-a14d-39856ccd4613 | note | Sheet wall set-out conforms to approved design coordinates
4ea79102-21df-5c1c-bc7e-d10c7df26363 | note | Site Layout Drawings, Survey Plan
10333155-ee94-42de-888f-682c2c816aef | checkpoint | Level and alignment check
153847ca-0a8e-5603-9be5-9fcff9e3c543 | note | Levels and alignment of survey points and position verified
00bf3282-b87b-5e4e-9ed1-d11ad1f37288 | note | WBS-SS-CI-SPC-0007, Survey Report
f7970df0-3746-4c2e-ab7e-ac2f5883076f | checkpoint | As-built survey after sheet pile install
fbf6eb11-12a3-5424-a897-c4630bc9fcfb | note | Survey to confirm sheet wall position
483c04b7-0c64-5b5a-8960-fdd7ebff2680 | note | As-Built Drawings, Survey Report
2e3dd651-0c2a-4a8e-9c2e-cd9d121ff14a | section | Part 3 – Installation process (photos where applicable)
f513c7ec-cbde-4859-aff5-f10376cfc39e | checkpoint | Pile alignment
a4f4f1d5-6487-5837-a543-a7db11f9fc54 | note | Ensure proper interlocking and vertically during driving
d0626514-60aa-5b85-bd07-c029c38f7d24 | note | AS 2159 Project specifications
74347d55-301c-4a72-ab75-2fc970f032ae | checkpoint | Driving Logs
f382153e-cdf1-5f07-a289-fe7fd0fd3955 | note | Record depth, energy, and any obstructions encountered
622fa76b-8ec1-572a-b988-c22e09aa44a9 | note | AS 2159, WBS-SS-CI-SPC-0007
23471b89-1b5e-46b8-86f9-a92572146129 | checkpoint | Vibration Monitoring
b2ff9144-b53c-501e-b738-67adde0d8c9e | note | Ensure limits comply with environmental requirements
466e29cf-63cd-579a-8d97-378ca5d6c393 | note | AS 4671, WBS-SS-CI-SPC-0007
d4762e0a-f3dd-49a0-9ef9-1433f84824d9 | section | Part 4 – Quality control (photos where applicable)
309374fb-abec-4d2a-9390-d93bfdcd5f0f | checkpoint | Verticality Check
7e5fa055-6816-569a-9da7-c6716434d915 | note | Confirm deviation tolerance
8f7b1d25-7c23-5217-a6b1-96e77dffb616 | note | Safety Plan WBS-SS-CI-SPC-0007
4c791a4d-db26-4764-9475-1f60967c4e02 | checkpoint | Interlock Inspection
9719412a-4d30-54b9-b8c0-d945994177d1 | note | Verify no gaps or misalignment
03a22ffe-df8d-5216-a48f-85f3759896bf | note | AS 2159 Delivery dockets
f2cb471f-8d3c-4527-bec0-c6ea480722c3 | section | Part 5 – Post-Installation & Handover (photos where applicable)
599fb7be-57eb-482a-a989-6d5ac6d0af60 | checkpoint | As-Built Survey
c7d75710-acb8-550c-9706-97e8fc4e603a | note | Confirm final location, depth, and alignment
ce878e2f-a8c4-5b90-9f53-635343568e43 | note | AS 2159, WBS-SS-CI-SPC-0007
f60fbd38-ae7e-4b4a-864c-50afd710dbc7 | checkpoint | Cleanup & Debris Removal
cb35dbe0-87cb-5639-b5a1-ab063eed28b4 | note | Ensure worksite is left in clean and safe condition
4ebc0ae9-0ca9-5de4-99e9-52298be66635 | note | AS 2159, WBS-SS-CI-SPC-0007
df3838f2-5e1b-4e03-b26c-f82a602e9899 | checkpoint | Engineer’s Sign-Off
91b6ffff-2a54-5e0a-b65f-d909c9e97851 | note | Obtain approval for compliance with design
c2cda212-f4ca-5ede-9fa5-cb8632ae68cc | note | WBS-SS-CI-SPC-0007
b5817ae5-8ef3-4a9f-86aa-33c49bc52258 | section | Document Sign-off
b7b26045-c24f-4dc2-9a3a-a3e9f415c720 | checkpoint | Prepared by:
71444eca-e80f-5a52-9e6f-1fa2d53cf1c9 | textbox | ROBAR - Name:
72f9ce19-a982-5a07-a721-289cf353ecae | textbox | ROBAR - Position:
5cdcfe06-3969-5756-a56f-aee07576738b | date | Date:
962e4ed6-46bc-433e-82dd-b981f90181b3 | signoff | Add Signature
95d50195-4288-4b00-940b-b10f405b6a72 | checklist | RR-SEPD-BESS-FIC-008 - Cable Trench Culverts |  | RR-SEPD-BESS-FIC-008 - Cable Trench Culverts
2ae94fac-561a-432d-8071-ba6b5e9b9a2b | section | Part 1 – Preliminaries (photos where applicable)
f21cc7e0-39c7-4ccb-a536-c948ec59d2f4 | checkpoint | Review of approved construction drawings and specifications
cb718378-383f-5835-95d2-5c20776940f5 | note | All drawings and specifications approved and up to date
0c33a736-e9af-58b8-93f8-379b0fa71445 | note | Specifications/Drawings ReferenceWBS-SS-CI-SPC-006
5d932a5c-6dfc-4449-a3ed-9855e52d5dc1 | checkpoint | Verification of permits
b9dbdf1f-67ce-52d6-b284-890eaf6300ed | note | All relevant permits (GDA/GDP) in place
92e51176-1803-54ff-92f3-67688631082d | note | Specifications/Drawings ReferenceGDA/GDP
072fd7b3-4fe8-4373-9e8f-82f46a26f103 | checkpoint | Site access and safety preparation
403612cb-5062-5499-9766-951f4b397228 | note | Site access cleared and made safe
19e8ccda-224d-5ab6-9c42-14c3055972f7 | note | Specifications/Drawings ReferenceWBS-SS-CI-SPC-006
3b128f99-24ab-4c90-add9-bb43e3519cf7 | checkpoint | Safety inductions and toolbox talks
94fd209b-98e4-5cf2-a00b-444a9f7ab0b9 | note | All personnel inducted; safety briefings completed
8994113f-b292-5bc7-b9e5-1ab57ac56390 | note | Specifications/Drawings ReferenceInduction record
9db54fbd-9bf1-4432-956b-e876d8ac618b | checkpoint | Environmental controls in place
7018b55a-89bb-5924-9968-58b83cdc1318 | note | Dust, noise, and sediment barriers installed and functioning
3dd6cb84-4212-5f30-b575-31493717f25a | note | Specifications/Drawings ReferenceSEPD environmental requirements
e33c085a-3bca-4233-a37b-ab36cac92bde | section | Part 2 – Excavation and trenching (photos where applicable)
658def57-c7ff-47d2-9df8-4fa67221fae0 | checkpoint | Trench depth and width comply with design
b1c07366-bb72-59b5-a7e6-80af239e93a5 | note | Set-out verified and matches IFC drawings
58dd21b1-4135-5e15-963a-4bcb3be9fb06 | note | Site IFC Drawings - AS/NZS 3500
959efc0f-348e-4f1c-bed8-8fbaef869bc8 | checkpoint | Stable trench walls (benching, battering)
82933834-21a5-5116-a62a-6835df7b8279 | note | Trenches deeper than 1.5m require benching or battering unless certified by a geotechnical engineer.
b734c6e7-b81b-51d1-a2af-89c126ae084e | note | WBS-SS-CI-SPC-006 - AS 4744
b29fa775-7f37-4d2f-a2b4-593babb15f8a | checkpoint | Culverts inspected for defects before installation
548bdc19-2861-5de5-8476-a35228514d09 | note | Material certs from manufacturer and visual inspection
97cd703d-75c4-5538-bd1d-c9a0e29c6dae | note | Material to align with design drawings and load rating
719698d4-7e9e-59b6-91ac-a133358f760f | note | Specifications/Drawings Reference - Manufacturer certifications
085d368f-3229-4375-8767-fb7c205334ea | checkpoint | No water accumulation in trenches
1fb8e1fc-4f09-535f-879b-4bc035141d63 | note | No standing water or excessive moisture inside the trench.
d9ddb00d-2c66-5d64-8660-e6b3990eb1c9 | note | AS/NZS 3500
c2d3c094-aead-418d-9a28-dbde934d62ad | checkpoint | Spoil stockpiles located at least 1m from trench edges
45cb9963-bd3f-52b1-aa54-4cacaa87a5ce | note | Stockpiles away from excavation to maintain safety of batters
9a94baa1-7ee0-54fe-908d-e89cc38f01f2 | note | WBS-SS-CI-SPC-0006
7362176b-b0e0-4232-a32d-523bd17b6440 | checkpoint | Correct bedding material used (sand, gravel, etc.)
a96b7642-5d74-5777-8324-d0821307f218 | note | Material complies with particle size, moisture content, MMDD
4b0ba86d-72a1-5f89-bf33-fa49705fe909 | note | WBS-SS-CI-SPC-0006 Test material results
bf88ab8c-9727-465b-a341-eb6b1842a126 | checkpoint | Bedding compacted to required density
6bbfbaa4-582f-5a74-9dba-1090c3d65ebf | note | Layers placed in maximum 300mm (loose) thickness
4ff5f106-d37a-536f-adbe-0f802a51f654 | note | WBS-SS-CI-SPC-0006
1fa1b70f-c4ec-4581-9594-b6cd63fe898a | section | Part 3 – Culvert Installation (photos where applicable)
bd2be6b0-d0a3-4252-ac5f-60b135ebd759 | checkpoint | Culvert Installation
95e009dc-8ce5-5ee1-8834-c7ab7f810c7a | note | Installed to design grade ±10mm and alignment within 5mm tolerance.
5a66f055-242c-5dc0-b7db-e2f464030749 | note | AS/NZS 3500
1ee9c047-9bb1-4d72-85f3-049f0d0784e8 | checkpoint | Culverts laid at correct grade and alignment
3241697b-2827-55b4-af96-d3df8812d9ed | note | Levels and grading match design tolerances (+/- 15mm)
c63d2ca5-0e2f-557e-8099-6c4ff27dc8a0 | note | WBS-SS-CI-SPC-0006, Survey Report
f7955b7c-1f2f-42aa-98d0-15d904ee9705 | checkpoint | Correct culvert joint sealant method used (backing rod, sealant, bituthene tape
d4077d6b-9c37-5c21-9ef7-35fd2e22ecf5 | note | Joints must be fully engaged and sealed per manufacturer specifications
1e3a822c-6fc8-5b67-920a-3588d01e4f1e | note | Manufacturer specifications
48085826-5f20-4c07-bf16-cdc949c11b3e | checkpoint | Concrete Lid Installation
fa901a0c-3756-5b72-b46e-738969ce988d | note | Installed to design grade ±10mm and alignment within 5mm tolerance.
9cdeee9a-b520-564b-aecc-0558a829b346 | note | AS/NZS 3500
e18fb33f-9cb9-4e82-9bb7-4520ae41af56 | checkpoint | Joint Sealant as per manufacturers specifications
d13f0369-1381-50e1-bbc2-fa380b52a341 | note | Joints must be fully engaged and sealed per manufacturer specifications
25f596d7-394b-5bda-a229-74d4e28426fe | note | Manufacturer specifications
42b075cd-4474-421e-aac7-1c1dbfc24a85 | checkpoint | Reinforcement Protection
2d9816a9-24dd-5851-8333-5717b12e0bca | note | Apply 5mm layer of Megapoxy P1 or approved equivalent
617fba79-934d-5004-8133-6bfe65b6d5fd | note | Manufactures Specifications
a1bb802c-7f69-40e3-a0f1-406e8d6f207f | checkpoint | Penetration Patching
78682069-5e7a-52ee-9ce8-8fdb25e8e6ef | note | Expanding Foam, with Sikaflex or approved equivalent to make good
687bda99-950f-5d67-99dc-8bbce74d4c79 | note | Manufacturers Specifications
d9f763bc-f094-4c48-a608-6199003fb9b4 | section | Part 4 – Backfilling and compaction (photos where applicable)
0fd7f223-59db-4a4d-ad61-24a93effd044 | checkpoint | Initial backfill material placed evenly around culverts
5791cb97-0f7b-5e72-a59f-727bf18db83c | note | Site-won material approved by geotechnical engineer
1baab585-5e09-5a2f-96d7-4c03ee0f924c | note | Geotechnical report - AS/NZS 3725
0b029630-caa0-4b7b-9048-ca07dd378d8b | checkpoint | No large rocks or debris in backfill
d41b5c7f-a996-5230-9f4e-ab6c8e29f512 | note | No rocks or debris in backfill
27f7ccac-afb5-5acd-aeda-27bb24ac63c5 | note | WBS-SS-CI-SPC-0006
f6b120c2-963a-4db8-9c2c-9e2fc959a8fd | checkpoint | Backfilling in controlled layers (300mm lifts)
3dc94cf5-7329-58c6-98d4-25c9a7c073ba | note | Backfill in uniform layers of maximum 300mm thickness
24a29b4c-b186-518b-a233-b954794915aa | note | WBS-SS-CI-SPC-0006 - Drainage drawings
4c8a9454-eaa6-4753-a5f7-3ed31bfca68a | checkpoint | Backfill shall be placed to a depth of 300mm above collars of pipes or conduits
7ca8b63e-0538-510e-af32-ffb1c20959e7 | note | Minimum 300mm above collars of pipes
d2992283-d664-5048-a09b-d828b78ce210 | note | WBS-SS-CI-SPC-0006
21da1d1e-bb3e-4fe7-968d-382d924bab43 | checkpoint | Compaction tests performed and passed.
8ee89392-06e9-5b1b-bbf0-c2b724128d94 | note | Compacted as per specifications
4979a7a9-25cd-5c39-ab6c-78ee9ce56cb9 | note | WBS-SS-CI-SPC-0006 - AS 1289
29b505bf-0c4d-4972-aa13-65cf8d142efe | checkpoint | Surface reinstated as per project specs (concrete, asphalt, topsoil)
f57fdebb-b048-56a0-9a5d-f3de848a8217 | note | Backfill to match existing ground levels with ±10mm tolerance.
9fe5965a-ca7e-5e3a-a2ec-93052d5e0919 | note | IFC drawings
4be28d8b-d60a-485a-a5ab-9e22f25a021b | section | Part 5 – Final inspections and acceptance (photos where applicable)
d3c22932-3cd2-4762-b776-6c9d902c10a5 | checkpoint | As-built survey verification
309c4f39-e779-54f4-87d2-21a0d6dca33b | note | As-built levels and layout match design
4230e8db-6b2d-57b6-bf12-bdce8bb5d98b | note | As-Built Drawings - Survey Report
722ebcc8-66ea-4180-a927-587f0c7cfc73 | checkpoint | Removal of temporary works
a70009d6-7221-5558-aa56-109eb9038b9b | note | All temporary structures, barriers, and access points removed
ac48f9c8-76f1-582d-a635-01e3d5cbbce2 | note | Site inspection
41055941-19f8-49ca-a431-053927524bc6 | checkpoint | Final inspection sign-off
0251ef89-221e-53fe-890f-7ac74ea2d72e | note | All drainage activities completed and accepted
602fe3cb-2adb-50ed-9227-be6a3eed1d0e | note | WBS-SS-CI-SPC-0006
dc515c72-64d9-4e36-9169-a00eaa55a822 | section | Document Sign-off
f596c94b-2621-4d11-bacd-3f5cbe0f9f30 | checkpoint | Prepared by:
2f5a64e9-0e9c-5938-a1da-f0c932f10fdf | textbox | ROBAR - Name:
1701c3c6-917b-5e9e-bbca-eba40cf67f97 | textbox | ROBAR - Position:
ac1e971d-b668-536d-ae2e-8b9d70390dc6 | date | Date:
cda45600-ac76-4bcb-9186-bd678f84cbe0 | signoff | Add Signature
4179c91d-7f59-466a-a726-0f1c39795541 | checklist | RR-SEPD-BESS-ITP-001-01 - Earthworks | itp | RR-SEPD-BESS-ITP-001-01 - Earthworks - Layer
32e5e86d-ff97-4af1-9c74-dc449e940113 | section | Section 1: Earthworks
409d1609-0995-45e8-9afc-4dfe337d8526 | checkpoint | 3.1 - Excavation to subgrade – verify lines, depth and dimensions
7d8e196f-d342-5157-acee-bcb07665f212 | note | Responsibility - SE/PE
9220892c-62d6-5d55-a764-a0bc84dedd42 | note | Specification Reference - WBS-SS-CI-SPC-0006
771e2794-58fc-573c-af02-f00d1ad8034c | note | Conformance Criteria Summary - Compliance with design drawings and subgrade preparation
1a540eed-1db3-5010-bed9-5580e3b46665 | note | Method - I
0de44e87-4ad8-5892-b07f-dc0cb38b5e6e | note | Frequency - PL
155b56dd-7411-5bf6-88d6-0246dbf17b99 | note | Hold/Witness Point Requirements: ROBAR - V
1c10a1c6-6aef-54f7-87a1-c6b6a8a6d61f | note | Hold/Witness Point Requirements: SEPD - V
e54b82d8-0ad8-5ea8-8df9-428153e385fd | note | Hold/Witness Point Requirements: Client - NA
55188513-fb90-5e33-bd48-243255745252 | note | Records or Checklist Document Number - IFC Drawings
a6f02a31-b623-497e-9200-2704507faf4a | checkpoint | 3.2 - Stockpiling of excavated material – manage and segregate by type
05858e3d-b25d-5637-af53-0de042c21db6 | note | Responsibility - SE/PE
6965bc3d-551b-5e8c-8447-160d2a0775d5 | note | Specification Reference - WBS-SS-CI-0006
df49beda-534d-5a07-a657-fb2a321bd3af | note | Conformance Criteria Summary - Material stockpiled appropriately, no cross contamination
3820134d-36b8-58b7-a1d5-40d26841339e | note | Method - I
9bd26fee-5b57-5beb-8b8e-dd854cdc0d88 | note | Frequency - PL
a5eb04c4-53ba-5bb1-9d73-fde2ddbe96b2 | note | Hold/Witness Point Requirements: ROBAR - V
1d3b5edb-a68d-58eb-8426-07732ec9e54a | note | Hold/Witness Point Requirements: SEPD - V
25fa1a3d-b5f5-529e-bcc2-b4747fec05a3 | note | Hold/Witness Point Requirements: Client - NA
4492186b-ac54-5047-b97c-2adbb9195039 | note | Records or Checklist Document Number - SEPD environment-al plan
a160b9ef-41bf-49db-9c8c-cc51009ac802 | checkpoint | 3.3 - Subgrade proof roll
4ad682db-fc7a-5f49-801a-aa663f84f2be | note | Responsibility - SE/PE
3a604f03-5344-5510-afdc-f3d5b8043377 | note | Specification Reference - WBS-SS-CI-SPC-0006
fd5db355-bff8-592f-9601-ad8223ca71ab | note | Conformance Criteria Summary - Subgrade meets stability requirements
3f1c8074-2558-50b8-9a88-843d04fd39a8 | note | ○ Subgrade proof roll shall be inspected by the Principal
762d0fb1-cf36-51c4-a7b8-c69fd7330a36 | note | Method - T
6feba1f9-7f04-5c46-af13-f9e458339008 | note | Frequency - PL
6f095dc4-a3a0-599d-b20b-e1e82ff9bb5a | note | Hold/Witness Point Requirements: ROBAR - HP
43060b07-e0ad-545e-ac15-d9d2710064f3 | note | Hold/Witness Point Requirements: SEPD - HP
cb3ad0a5-712d-5b60-9752-d7c887fe3b28 | note | Hold/Witness Point Requirements: Client - NA
83b4993e-59fb-5020-9589-2a4062116699 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-910049
951bf58a-2653-47f9-af51-93cf05fda6be | signoff | HOLD POINT
c6837b5d-d3d6-4c95-846f-1c7f65629b70 | checkpoint | 3.4 - Backfill under slabs and compaction of lifts
87c1ab8f-c8cc-5973-b478-be2c82720aa5 | note | Responsibility - SE/PE
59f7e2f1-601e-51a9-a8b8-b17a07842ceb | note | Specification Reference - WBS-SS-CI-0006
4eee7b4c-20a0-58d1-8788-7262c74e1e76 | note | Conformance Criteria Summary - Backfill material compacted in layers to required thickness
c54e752e-29b0-5f9a-9b82-d70fba6a168f | note | Method - I
3b56e54c-25fe-532f-9ebc-fdff55c3348e | note | Frequency - PL
f766f266-2d19-5ec7-aa35-4542517b8334 | note | Hold/Witness Point Requirements: ROBAR - V
df5f7aaf-e852-50f9-96dc-a711318feed1 | note | Hold/Witness Point Requirements: SEPD - V
72afa0e3-c281-5f11-b3b8-4bb5d94f9d1a | note | Hold/Witness Point Requirements: Client - NA
dc18306d-0de8-5103-b6cf-895ac6181c47 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
3a4c7c05-33fc-4957-81ea-4ca3f54a7582 | checkpoint | 3.5 - Compaction density ratio for backfill
12c26bf3-2458-57c5-943f-3363fb47d834 | note | Responsibility - SE/PE
2cdca4dc-fbd2-56cd-af4e-c14fe1bab472 | note | Specification Reference - WBS-SS-CI-SPC-0006
fd6a8930-3a68-5699-8ed9-8a57aca97eee | note | Conformance Criteria Summary - Compaction test report showing >95% MMDD
28152ca1-4fef-5098-b55f-8b4c48be7747 | note | ○ WBS-SS-CI-ITP-920049
91d23bee-d4fe-53ff-800a-c0ba0cc2477c | note | Method - T
31411ae6-0dcd-5a80-80bd-654ce4b51a1b | note | Frequency - PL
3450dcc8-078c-5db2-a693-1c443a4cbf1c | note | Hold/Witness Point Requirements: ROBAR - HP
7e8fcd6c-770d-5619-b9b1-2a5e2b4d7052 | note | Hold/Witness Point Requirements: SEPD - HP
9fa5fedc-4a8a-5484-a2fc-60c01f46cba4 | note | Hold/Witness Point Requirements: Client - NA
663d39cb-671e-5075-80fd-71a8cae9e4b2 | note | Records or Checklist Document Number - Test results
8cd80d5c-fa6e-4967-9cb2-f6f9c0920732 | signoff | HOLD POINT
e8c16635-b45e-4c56-b607-215fdda7422c | checkpoint | 3.6 - As-built survey pick-up
84038a20-0ebf-5a6a-bcc9-e6671409f289 | note | Responsibility - SE/PE
600aa93c-6cb1-50a8-abe6-eadef4b38657 | note | Specification Reference - WBS-SS-CI-SPC-0006 PPR
91ca7949-02ca-5221-a7a0-92a7ae2161b0 | note | Conformance Criteria Summary - Survey records and as-built drawings
ffed2b1f-d1c1-5b16-b480-878b148447c9 | note | Method - S
5aa38fab-3f35-502b-a0c6-22d74d64c547 | note | Frequency - PL
2821ad7c-99c5-5d59-a4b6-f7b729cb83f1 | note | Hold/Witness Point Requirements: ROBAR - V
749dd50e-2c5d-5911-a7d3-f801eea12e80 | note | Hold/Witness Point Requirements: SEPD - V
b629a5db-ef6a-598d-986b-db669e5ef242 | note | Hold/Witness Point Requirements: Client - NA
5c90e751-34a1-5012-b36f-0c2a703c9d59 | note | Records or Checklist Document Number - As-built drawings
075f1a4a-f63b-43bc-911b-723f305bfdc3 | section | Section 2: Final Inspection
788ddbc0-7039-439f-9f41-ad358963467d | checkpoint | 4.1 - Finish level compliance with design drawings
e386080f-081c-50ce-b494-3cd619518c7c | note | Responsibility - SE/PE
d2b0c26e-d63b-546c-b71b-0a3d5e9ee86e | note | Specification Reference - WBS-SS-CI-SPC-0006
855711b9-a553-5ab2-bfc3-725abca6aa4e | note | Conformance Criteria Summary - As-built drawings
bfb22895-b1ed-5cf8-a7ee-2cffcaf72ac6 | note | Method - S
705dc6df-4a60-586d-aa4b-43463be36596 | note | Frequency - PL
1d3ea53c-79d0-535c-9d68-ebcee0276881 | note | Hold/Witness Point Requirements: ROBAR - V
1da04910-6ffe-561d-840b-6185a9118ea8 | note | Hold/Witness Point Requirements: SEPD - V
3f8df9ae-e57d-550a-8f49-6311889eca20 | note | Hold/Witness Point Requirements: Client - NA
dd35270e-b32d-513f-9f84-e5f52eecd9ba | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
cdc440b9-82d9-43c9-aa73-8eb04a07f916 | checkpoint | 4.2 - Final Inspection Checklist (FIC) completion
c7678f25-ac04-5dc5-8825-d38e0d46eb5a | note | Responsibility - SE/PE
335bce92-3836-5391-8dbc-775d69dd3a06 | note | Specification Reference - WBS-SS-CI-SPC-0006
34d66d2a-c656-52a5-a0cf-844951e8c9de | note | Conformance Criteria Summary - Signed FIC
eeda8ddd-b33b-5518-8112-a64d9f4e1807 | note | Method - R
0a18ebe4-6d71-5c51-82e8-505ab375d691 | note | Frequency - PL
cdde9182-5ad2-5dcd-a80f-3cf36daf18bb | note | Hold/Witness Point Requirements: ROBAR - V
e258f138-f9b3-583c-95af-cfef8c27a64f | note | Hold/Witness Point Requirements: SEPD - V
f661ca9c-3783-5572-b04d-46a41cb36c94 | note | Hold/Witness Point Requirements: Client - NA
f093581e-cd19-51d4-a8d8-75bbb1203ff7 | note | Records or Checklist Document Number - WBS-SS-CI-ITP-920049
2f4854da-23dd-49ca-b3ad-ca005807721b | section | Document Sign-off
b15c39b8-fb46-4c77-a0d3-eb28e7b22a7b | checkpoint | Prepared by:
13697973-3d1d-5a34-927e-c5a62a2be058 | textbox | ROBAR - Name:
ba49da7f-b716-55aa-9546-51b5b90672ce | textbox | ROBAR - Position:
58cd4340-6fff-5a01-99cf-4e196282bc5c | date | Date:
8e54f05a-187e-45df-b04b-22c418cd40d6 | signoff | Add Signature
c1e29112-85d3-4797-a9b7-afe0f0dc934e | checklist | RR-SEPD-BESS-ITP-002-02 - Concrete Works | itp | RR-SEPD-BESS-ITP-002-02 - Concrete Works
c0713e5b-f38b-427e-a0c2-d1cc91e9f790 | section | Section 1: Preliminaries
3216f4d6-e026-4dc4-8e39-1631c19f513b | checkpoint | 1.1 - Review of approved construction drawings and specifications
30634337-aeb9-52c7-a6a2-ba6931542675 | note | Responsibility - SE/PE
ce342923-6474-5f8e-a3f9-cf15f52d378b | note | Specification Reference - WBS-SS-CI-SPC-0007
e8b694d1-d11b-5f0b-aa17-8c31e81465c0 | note | Conformance Criteria Summary - Approved IFC drawings and project specifications available on-site
40cc3de6-96a7-554c-92c1-38745e565429 | note | Method - R
746b7796-8b06-5be1-8c9e-aa9d7e9ecc17 | note | Frequency - PW
c7e54883-f05d-501e-96e4-95ac5a6683bb | note | Hold/Witness Point Requirements: ROBAR - V
07aa42f2-cff4-53a9-9644-12309f1207ef | note | Hold/Witness Point Requirements: SEPD - NA
7eaa43f8-0d26-5581-b636-7608bd854ca4 | note | Hold/Witness Point Requirements: Client - NA
ea9ce35b-619c-59ef-b6b2-8f00a36c0300 | note | Records or Checklist Document Number - IFC Drawings
53062163-1859-4fa7-b2f8-31d64cbc3bb6 | checkpoint | 1.2 - Site condition check and access preparation
50484d3a-6a21-5a02-b740-996091e20fee | note | Responsibility - SE/PE
e0f6344d-7d90-573f-beb2-f539a4499265 | note | Specification Reference - WBS-SS-CI-SPC-0007
ad2ba613-c194-51a4-ae48-44754689465e | note | Conformance Criteria Summary - Site cleared, accessible, and suitable for concrete slab works
170533d8-1743-5c2a-a532-6a15da98fd28 | note | Method - R
c151e7d2-767a-5ec8-8a0f-9524abd6f7fe | note | Frequency - PW
a2e0bbc1-f547-57e3-be5e-69089a81717d | note | Hold/Witness Point Requirements: ROBAR - V
e7a141bb-9085-5661-ae0a-617dc04088ab | note | Hold/Witness Point Requirements: SEPD - NA
aafa5886-f65f-5524-b7cc-b102e3712376 | note | Hold/Witness Point Requirements: Client - NA
3c567f8e-313c-4573-85ac-be41f5c7d487 | checkpoint | 1.3 - Site safety induction and toolbox talks
cb2fe68b-bcfc-5124-8280-3d03c8e39cbe | note | Responsibility - SE/PE
9f1aaf4d-b4cf-5803-96da-facc6d644cd1 | note | Specification Reference - WBS-SS-CI-SPC-0007
f744793a-e557-52c7-b6fb-0ee18fb0a5e2 | note | Conformance Criteria Summary - All personnel inducted and briefed on safety, site-specific risks
ef7736e8-4815-5444-8a18-2e53b68fe7d9 | note | Method - R
720a21eb-e8c2-5fd1-85bd-c22fd51cf8b3 | note | Frequency - PW
daff337a-af5a-5ad0-8d85-0ab42a1cf25b | note | Hold/Witness Point Requirements: ROBAR - V
15ea763b-c6ae-587b-a525-db22c81ab913 | note | Hold/Witness Point Requirements: SEPD - NA
5c427e72-f2d5-5172-9d0b-66b8ffb00715 | note | Hold/Witness Point Requirements: Client - NA
578a4538-b90d-5ba6-925f-e6949a837e66 | note | Records or Checklist Document Number - Site inductions records
ca5e858f-d4ad-4075-8b8b-ecdc4d15e0fe | checkpoint | 1.4 - Inspection of plant and equipment (e.g., concrete pump, vibrators)
fc620d9c-78e3-5f66-a773-b8379dd08c05 | note | Responsibility - SE/PE
96f8c4ee-db01-5b5f-9b4b-114857c0495a | note | Specification Reference - WBS-SS-CI-SPC-0007
bd11f0e9-597d-5efa-a9e0-f7d589d32012 | note | Conformance Criteria Summary - All equipment calibrated and operational
8d8cffb2-f356-5851-a3d2-67fc5866e434 | note | Method - R
d2fc6994-6cc7-57e4-9fd9-4121df7daf71 | note | Frequency - PW
b4199594-5402-5dcf-9677-2d0b90087c56 | note | Hold/Witness Point Requirements: ROBAR - V
6e449897-3023-5f59-82d2-99b9c4d56d9f | note | Hold/Witness Point Requirements: SEPD - NA
499815ea-5f9e-5056-b60c-448ed769b38e | note | Hold/Witness Point Requirements: Client - NA
1ae04ce8-9a84-58bf-8050-33ffdaf63f94 | note | Records or Checklist Document Number - Calibration/Pre-start
e2941036-a84d-40e2-a845-9ac73cb9f93a | checkpoint | 1.5 - Foundation preparation
0102e900-2156-56f3-b919-24ef3c683755 | note | Responsibility - SE/PE
d8aa87a3-620f-5534-8488-b12e6a4a8a3a | note | Specification Reference - Geotechnical report/memo/ geotechnical engineer’s specifications
81c28f69-232a-50d6-95d2-694dc492f75c | note | Conformance Criteria Summary - Compaction test reports/geotechnical engineer’s specifications
b56713b3-ce50-596d-9332-cd41cbddea3e | note | Method - R
adc1dbe3-a81e-5403-9895-9a180ed15f2e | note | Frequency - PW
85fb2871-e84f-5d12-b281-c69d53ee2413 | note | Hold/Witness Point Requirements: ROBAR - V
e5965c68-eec9-585c-9cfd-c4cc37b39a08 | note | Hold/Witness Point Requirements: SEPD - V
20c21cc9-4ed2-52f3-90ff-24ce1b5e7c05 | note | Hold/Witness Point Requirements: Client - NA
b0a498c2-6073-5dcb-a4c7-1043e769b680 | note | Records or Checklist Document Number - Calibration/Pre-start
27628760-c1d0-4925-a906-d92d297e2d37 | section | Section 2: Pre-pour preparations
eb123bd9-2cc5-4fa8-9d14-1bb322177202 | checkpoint | 2.1 - Verification of work permits
6e14a383-699a-5c04-96c4-29dc5797e344 | note | Responsibility - SE/PE
7dd8df56-24cd-5077-a1d1-0a2963f3965f | note | Specification Reference - WBS-SS-CI-SPC-0007
178c7b72-ad5e-5bbb-b779-30f759a22404 | note | Conformance Criteria Summary - All necessary permits for concrete works in place (GDA/GDP)
fa935abd-695d-5741-9510-d499ec26ee50 | note | Method - R
3c16a583-4ccb-5678-9e8b-f72e5e392a6a | note | Frequency - PL
f8e3d89b-ded6-5dc7-b75f-d9f3e1007698 | note | Hold/Witness Point Requirements: ROBAR - V
8009902f-1a5e-597e-b980-29b7279ae0d1 | note | Hold/Witness Point Requirements: SEPD - V
980f19a2-aa00-586b-9735-9de0b69cdef9 | note | Hold/Witness Point Requirements: Client - NA
0c6ffcdb-e15e-51d6-8bc2-5925e2868f17 | note | Records or Checklist Document Number - GDA/GDP
10a621f5-d2ac-4f6c-9f81-2ceb5acff69e | checkpoint | 2.2 - Blinding concrete installation
f28599cf-70df-5bd5-ac3c-78130525c8fc | note | Responsibility - SE/PE
c5357609-9551-5a4e-8b45-de6f8afc283a | note | Specification Reference - WBS-SS-CI-SPC-0007 Design drawings
9e040952-9858-5800-93ed-98705a77cadf | note | Conformance Criteria Summary - Approved mix design
1c6bb724-c40c-560e-a898-e5c31cb0caf9 | note | Method - R
3cb0c7fe-c406-5b1c-8fda-adffb51d9d43 | note | Frequency - PL
1bacabb1-5693-5469-9ffe-50f2b0ccb849 | note | Hold/Witness Point Requirements: ROBAR - V
80196435-c18c-5c71-a024-ad99c6f878e3 | note | Hold/Witness Point Requirements: SEPD - V
f9cc6e4d-a4d7-58c4-86ed-828135a477e7 | note | Hold/Witness Point Requirements: Client - NA
b15b8af5-1c3c-5e70-bc8a-155e96385cf8 | note | Records or Checklist Document Number - FIC
e3436f17-5aca-4d41-9129-eacb7bffaa00 | checkpoint | 2.3 - Review of concrete mix design and material certificates
367029cb-334e-565c-8ce0-605af9ddcc4b | note | Responsibility - SE/PE
cd9d91f7-8e40-57aa-a54e-858275268dbb | note | Specification Reference - WBS-SS-CI-SPC-0007
47130eeb-6259-5d53-b2a7-41f7a4e4025a | note | Conformance Criteria Summary - Approved mix design, material certificates compliant with AS 1379
f9fd0a5b-0eaa-5c6c-aa42-b69d37639467 | note | Method - R
6c95c87b-cdd9-5567-a647-671614d38aa0 | note | Frequency - PW
aa4f5da2-9f5a-514c-a4ab-8a31dfff6459 | note | Hold/Witness Point Requirements: ROBAR - HP
0dab5c73-3849-5514-8143-9ef691c51e71 | note | Hold/Witness Point Requirements: SEPD - HP
8f28c926-0fda-5dc8-9930-83e9eeb289ae | note | Hold/Witness Point Requirements: Client - NA
7db7a1cf-1022-5ad1-b813-00ef7b8460f0 | note | Records or Checklist Document Number - Product certificate of compliance
b5601acd-f415-4999-bc62-db3019f63715 | signoff | HOLD POINT
9de0b92e-2b18-4ae6-a65b-70aafcd2cf16 | checkpoint | 2.4 - Formwork inspection – alignment, cleanliness, and dimensions
66900275-64a4-5bc3-98e7-122dde270939 | note | Responsibility - SE/PE
266f612d-35d8-598b-b293-80e4cf752777 | note | Specification Reference - WBS-SS-CI-SPC-0007
c4149233-a951-586d-a51a-c653dfb6abd7 | note | Conformance Criteria Summary - Formwork in line with drawings, clean, and dimensionally correct
c1ec5f01-8d50-5ac6-992a-3977e52f4acb | note | Method - R
ec32cd81-e65c-5646-8918-6b3630d68fe8 | note | Frequency - PW
7a653f91-226f-5af5-bb31-b694ee48887f | note | Hold/Witness Point Requirements: ROBAR - HP
debce9a9-9263-5736-9081-8a0d0c5b2e2a | note | Hold/Witness Point Requirements: SEPD - HP
b0c7df6c-9a13-51ed-867b-9531c2eaad55 | note | Hold/Witness Point Requirements: Client - NA
d8e0bfe7-2b37-58de-aba4-7168516b7a93 | note | Records or Checklist Document Number - TWD FIC
98a61297-bc49-46ca-928c-b243f4232028 | signoff | HOLD POINT
a2578135-830c-40a3-921b-0c5c8795197a | checkpoint | 2.5 - Reinforcement inspection (size, spacing, placement, cover)
d7e2d0ac-21d7-5b31-bd12-ed44f75a4926 | note | Responsibility - SE/PE
7c37ba0c-d41f-5998-9895-5dc3d6bbfd67 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 4671
187b5e04-9887-5bbc-8632-897274060343 | note | Conformance Criteria Summary - Correct bar size, spacing, reinforcement securely tied, adequate cover
daf55450-c312-5d5a-a4b7-e9b8f8253dcc | note | Method - R
4ef04433-d51e-5075-912a-30fa5c9371a5 | note | Frequency - PW
bc31033c-7a03-5c99-a7c7-007016017627 | note | Hold/Witness Point Requirements: ROBAR - HP
c0c2a46b-d33f-5577-9f2b-b958eefb3239 | note | Hold/Witness Point Requirements: SEPD - HP
499c692f-9855-56c9-ba22-9f2db3dee9e7 | note | Hold/Witness Point Requirements: Client - NA
30d30c58-48c1-5854-a5fc-451091a3bc69 | note | Records or Checklist Document Number - IFC Drawings FIC
f1bd02c9-7876-4621-9bd8-bde7df88e2fe | signoff | HOLD POINT
8718e6e0-14fb-4f78-88f3-81b87b0bc863 | checkpoint | 2.6 - Verify waterproofing membrane
cd6fd7a0-3e3f-5422-b0c0-66d0cb42d60b | note | Responsibility - SE/PE
dcd8b975-7714-5784-96af-3e69a8f05d65 | note | Specification Reference - WBS-SS-CI-SPC-0007
2497f945-16d2-5cb7-a105-7f7e614f42c4 | note | Conformance Criteria Summary - Membrane installed as per drawings/specs
49be7852-a4a7-5c70-8235-453e437a0d13 | note | Method - R
635120b5-52a5-500f-9065-92bb9791268f | note | Frequency - PW
7b4d2db9-80fb-5d46-9e94-f8b82f1791e7 | note | Hold/Witness Point Requirements: ROBAR - WP
738b9293-d850-50b2-8006-96eb5072413c | note | Hold/Witness Point Requirements: SEPD - WP
6b9b70ab-9fb3-5e10-b46c-dac0b496dacc | note | Hold/Witness Point Requirements: Client - NA
b53602e9-aa3e-5e8c-9754-341c6b36c198 | note | Records or Checklist Document Number - IFC Drawings FIC
ece605ee-80df-45ad-86c2-f138e5ed941b | checkpoint | 2.7 - Re-entrant bars (starter bars) and corner reinforcement
88a20c18-be9c-5e53-8ccf-803e61082746 | note | Responsibility - SE/PE
60993089-3351-5c21-95d4-47648b756f47 | note | Specification Reference - WBS-SS-CI-SPC-0007
0fa97f51-0098-54db-b517-9bbda23bef54 | note | Conformance Criteria Summary - Correct positioning of all embedded items per drawings
5154db5b-609a-5a72-aa24-70c3cb481a91 | note | Method - R
0f82c95f-1340-5d65-89b7-d841dba08163 | note | Frequency - PW
c0aeb55c-eba4-506b-b9ae-31ea18ed0476 | note | Hold/Witness Point Requirements: ROBAR - WP
72ccc7e8-ef5d-5a40-9675-84e6e6e6856c | note | Hold/Witness Point Requirements: SEPD - WP
00868fa0-7a42-5060-a7e7-418b47ab641c | note | Hold/Witness Point Requirements: Client - NA
4ee9788f-b91e-5fcc-ae53-e725868c2130 | note | Records or Checklist Document Number - IFC Drawings FIC
fa7d4f37-3895-4ffd-a2ef-d92c6686c831 | checkpoint | 2.8 - Concrete batch plant inspection
f60f8fae-6678-5783-a839-a31b0993db9e | note | Responsibility - SE/PE
7e4838f5-a7a8-542a-877c-dec96477fc6c | note | Specification Reference - AS 1379
6b66915f-37d8-5a60-bd25-fe01c014963f | note | Conformance Criteria Summary - Batch plant adheres to mix design, and delivery meets timing requirements
9a5d1052-c6ff-5036-9199-badac204888b | note | Method - R
f0a5a163-c484-5b25-a2a9-a18f5d0563f7 | note | Frequency - PW
38adc346-98fe-5c12-8502-e56cdeeb4fd4 | note | Hold/Witness Point Requirements: ROBAR - V
2eabf117-319b-584a-9c85-9b6324c9b122 | note | Hold/Witness Point Requirements: SEPD - NA
3ba16d47-d848-50b3-a3b1-e0b5885bb16a | note | Hold/Witness Point Requirements: Client - NA
e380650d-628f-57f5-b340-42c9cb14b3e7 | note | Records or Checklist Document Number - FIC
d91b75fb-2922-473f-b447-f2474fe0faaa | section | Section 3: Concrete placement
bd6ac0f9-b080-4d76-ab6c-ae288768079f | checkpoint | 3.1 - Pre-pour concrete delivery inspection
f8b39c44-4ca6-5951-a24c-4e95bb5acaa2 | note | Responsibility - SE/PE
2ad44689-d242-57ca-bf88-0fdd60acaa63 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 1379
5a0c8737-c154-5718-b885-5d3edfc2f066 | note | Conformance Criteria Summary - Batch delivery dockets match approved mix
96668dfc-a4a4-51ab-902f-e39cbe7fa872 | note | Method - I
a7d0f23e-245c-52a7-b20b-a69242f8f994 | note | Frequency - PL
4c364b81-4828-5a82-bb16-92f7817fd615 | note | Hold/Witness Point Requirements: ROBAR - WP
fd79ace6-3972-5d6d-a2ba-1efefccb7f0b | note | Hold/Witness Point Requirements: SEPD - WP
40507f8e-ade4-56c1-8d97-c70018165e09 | note | Hold/Witness Point Requirements: Client - NA
2f7bc74b-64f2-54ab-a1ba-f18dee18f39a | note | Records or Checklist Document Number - Delivery dockets
b54d4119-444e-46cd-9d08-7d8085a9e8a8 | checkpoint | 3.2 - Slump test at site (conformance to mix design)
de747406-436f-5961-b5d3-03898932de2d | note | Responsibility - SE/PE
acab73ee-0f2a-56fd-9f88-6a9f48820eb9 | note | Specification Reference - AS 1012
65f4aa4d-bb0d-5e36-b2e5-23d2a0ff61d7 | note | Conformance Criteria Summary - Slump within specified range (e.g., 100mm +/- 20mm)
e3b4777a-ab47-5cc9-97bf-9fc82c411c65 | note | Method - I
0f9236f4-ab8d-5cc4-8466-931781f7227e | note | Frequency - PL
f6d2dcdf-79b8-5850-ad96-ab4faed025a5 | note | Hold/Witness Point Requirements: ROBAR - HP
575c12e3-6be4-5b22-b5ed-bb9e5190d577 | note | Hold/Witness Point Requirements: SEPD - HP
b2733ba8-4c79-5c48-878a-2e6e89d7dc56 | note | Hold/Witness Point Requirements: Client - NA
5a7aadc7-bc3e-5cbe-9705-3673a779d04f | note | Records or Checklist Document Number - Lab test report
975b30c2-101a-4c50-bc3e-a4fbd4e005d3 | signoff | HOLD POINT
6dd6541f-207a-4133-9ba5-70fc44199bb4 | checkpoint | 3.3 - Concrete placement and compaction
5e112f03-e68a-5392-a69f-843d62038f46 | note | Responsibility - SE/PE
633c403d-aa39-59d3-9941-f8a03d038de0 | note | Specification Reference - WBS-SS-CI-SPC-0007
d60c8780-e496-5f8f-b20d-61126272d58a | note | Conformance Criteria Summary - Concrete placed within formwork, no segregation, fully compacted
d79622da-dd58-5cbc-8cc0-02bb085789ec | note | Method - T
259d53e1-2863-5be4-a96a-1aa36cbba1b5 | note | Frequency - PL
0802b771-d0d9-51f7-8b1a-0edf01f9eb92 | note | Hold/Witness Point Requirements: ROBAR - V
8712583e-ad8b-5e4d-b4e2-22178fc8ac58 | note | Hold/Witness Point Requirements: SEPD - V
c8ac6499-6bf4-533f-8824-6ffc4172f071 | note | Hold/Witness Point Requirements: Client - NA
b6121063-047d-5cea-9f1d-46dca9e69676 | note | Records or Checklist Document Number - Pour record
e6345b64-520a-424a-b091-c788b42bdc35 | checkpoint | 3.4 - Cylinder samples for compressive strength testing
ec3bffc4-6faa-5fdb-b15e-c3741acfe2ab | note | Responsibility - SE/PE
1fe84b2e-9a29-509e-8244-45c9b206638e | note | Specification Reference - AS 1012
d806c331-c457-5b92-a4b4-ac8cc52f8f8a | note | Conformance Criteria Summary - Minimum of 12 cylinders in total for 7, 14, 28-day tests
10fa576a-ab3c-5d0a-aa83-178422deebf6 | note | Method - I
cbf8fbf2-3f93-59d6-ad0c-4c5673d32707 | note | Frequency - PL
7d2112ca-8f78-5c62-82da-01016756f6fd | note | Hold/Witness Point Requirements: ROBAR - HP
3b129134-a3ce-5fda-9a3c-e8aaac27c13c | note | Hold/Witness Point Requirements: SEPD - HP
3dd15563-7c26-5420-9da6-fa1d66c323f3 | note | Hold/Witness Point Requirements: Client - NA
5be6af63-e816-5180-8aed-d91c7bd54390 | note | Records or Checklist Document Number - Lab test report
45937ee0-755c-46ea-9c23-8eb4e1e503b8 | signoff | HOLD POINT
d0d4dba8-d687-4a86-a731-3a126e5fd88e | checkpoint | 3.5 - Concrete temperature monitoring
d9f21a2d-5674-5421-b25a-6bce74f67a18 | note | Responsibility - SE/PE
a741d70a-1192-5aed-987a-c396452fba6a | note | Specification Reference - WBS-SS-CI-SPC-0007
c8fe1e39-00cf-54c4-a719-21f5d1f92640 | note | Conformance Criteria Summary - Temperature within acceptable range
c8da645a-00eb-5c5b-bc3b-5cdd23f2dda3 | note | Method - T
94a81f5d-f277-59ba-bcf3-6eb407d6a6fc | note | Frequency - PL
96f7d7f5-5c21-5a9e-b8f1-a794f02f2122 | note | Hold/Witness Point Requirements: ROBAR - HP
a2d9899d-1b3e-551e-bb85-a2353b0f53a4 | note | Hold/Witness Point Requirements: SEPD - HP
2f32b917-27fe-5b79-bc87-07496f48e316 | note | Hold/Witness Point Requirements: Client - NA
06c39e7a-a7fd-5674-a2ec-ec667c188c7b | note | Records or Checklist Document Number - Pour record
1597b5b4-f875-45ee-bd88-31f21912e974 | signoff | HOLD POINT
9a9e8fdc-e71c-4cff-a15b-d3aa44109cae | checkpoint | 3.6 - Placement monitoring – free- fall limit
fdb4f8f4-b6e0-501d-a10e-40c1498024e3 | note | Responsibility - SE/PE
9d7ebeb1-516e-599f-924b-50bca72e4aec | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3600
32768342-5af1-54f7-9839-1ba498bff81c | note | Conformance Criteria Summary - Concrete poured with a maximum free-fall height of 1.8m to avoid segregation
29a31854-290c-5b3a-a28f-3b06a9fd6d0a | note | Method - T
7429ed1e-3729-5119-8c8d-e0a783e9e0ca | note | Frequency - PL
f06dce4a-29ee-53e0-a5f6-1faf537bc855 | note | Hold/Witness Point Requirements: ROBAR - V
a2e26af6-b960-5726-af35-fa0a074a131a | note | Hold/Witness Point Requirements: SEPD - V
1c527c74-95bd-5f3e-a6a2-26b2a2ae94b9 | note | Hold/Witness Point Requirements: Client - NA
edaaa740-4f53-5d44-a1fa-1b5482b4bc86 | note | Records or Checklist Document Number - FIC
da2ba581-3222-4c25-8552-bef73aadeb3d | checkpoint | 3.7 - Vibration and compaction monitoring
a38f60c3-3c06-50b6-8a6d-cbdcf01a049d | note | Responsibility - SE/PE
d6d792a6-5244-5ddc-8510-1ec817bbe75b | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3600
3f01d66d-2c45-5782-a4f6-646b4faf8923 | note | Conformance Criteria Summary - Concrete properly compacted with vibrators, no voids or segregation
6a6f1e14-6cbf-5d59-a107-ec428e9cbeb9 | note | Method - T
8d036460-884b-53b3-ae81-2afb3136ea04 | note | Frequency - PL
c10b337e-59b8-5fb4-9289-d82714ae0900 | note | Hold/Witness Point Requirements: ROBAR - V
51a06a0f-ab0c-5be9-9727-73671f3ed1c5 | note | Hold/Witness Point Requirements: SEPD - V
9af94fa9-57b2-5654-87ec-f67addf7c35a | note | Hold/Witness Point Requirements: Client - NA
0c57dcae-72e2-579c-a4d9-84f6330284dd | note | Records or Checklist Document Number - FIC
d4769162-d2ef-4fd9-9e09-a9307143cb02 | checkpoint | 3.8 - Concrete curing
142806cd-fa84-5c60-9471-0e675971c93f | note | Responsibility - SE/PE
7ef5e448-ccd8-537f-b14b-86d42ec8b4df | note | Specification Reference - WBS-SS-CI-SPC-0007 FRP section 4.25.11 AS 3600
0eb0dac7-945d-5a84-af83-70bd28c7e5c2 | note | Conformance Criteria Summary - Concrete curing per approved concrete curing method statement
e0202387-6819-5814-8c27-fa54c3b3e2e9 | note | Method - T
d61b9875-2362-553f-9bed-4dee2a73baf0 | note | Frequency - PL
1d5aab0f-f7af-5e59-8d6d-15b949e1b9b3 | note | Hold/Witness Point Requirements: ROBAR - V
749ef53d-2796-5065-892f-768ccb8a3b39 | note | Hold/Witness Point Requirements: SEPD - V
efb3b021-ba05-5aeb-abed-1158c47cdfab | note | Hold/Witness Point Requirements: Client - NA
bb0928a0-a8ca-53fa-8eef-9c1dd560be14 | note | Records or Checklist Document Number - FIC
0fce9922-410e-41e0-a522-9a56897c0359 | section | Section 4: Final Inspection
6b2c6b91-fc8b-4c8e-a5b0-c03093a9ddcd | checkpoint | 4.1 - Surface finishing (Class of finish per AS 3610)
b2376cea-e273-5516-8f2b-3b7030aca2e2 | note | Responsibility - SE/PE
2e98a060-20c4-5176-a964-c1b95bc736b8 | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3610
7f4fb86f-d7b7-5260-92fd-17e07b055acf | note | Conformance Criteria Summary - Class 5 finish for surfaces that are not visible after construction
702156b3-9252-5d0c-af6e-b17cdba54a77 | note | Method - S
bc7aa6db-3887-5e47-80f1-69a1be526331 | note | Frequency - PL
314e0ad7-0575-5312-903b-8b6d5ee75d58 | note | Hold/Witness Point Requirements: ROBAR - V
6e5746de-2bf7-58df-bc1e-8cc1b8d7d3bf | note | Hold/Witness Point Requirements: SEPD - V
38a257e5-3454-5b27-a76f-9854e1c15220 | note | Hold/Witness Point Requirements: Client - NA
69a7d7b0-7b7b-5ebc-8cb6-9df4e160f0f8 | note | Records or Checklist Document Number - FIC
cacb5021-9b66-4488-9f88-34bc4a86c48a | checkpoint | 4.2 - Curing procedure inspection
b3da11f3-0c35-59b4-b6fc-2f8ab77c9b68 | note | Responsibility - SE/PE
857b04a7-1824-5448-8067-cee8f258261c | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3799
4b6537f4-2943-5f7c-8395-aef3fe510149 | note | Conformance Criteria Summary - Curing compound applied or wet curing in place
c1114067-78a0-546a-ae10-fd462b26242c | note | Method - R
d1306182-775b-5179-8584-a01f83c17c0e | note | Frequency - PL
225cd55e-e7b3-58c8-8df2-88fd0b1f1fea | note | Hold/Witness Point Requirements: ROBAR - V
59736eb5-1de1-5547-a281-668ac8d43872 | note | Hold/Witness Point Requirements: SEPD - V
5cb32a25-57a8-5b2c-9079-8e56b1dff107 | note | Hold/Witness Point Requirements: Client - NA
d2f9a708-37da-5983-ba15-6c5f487550ab | note | Records or Checklist Document Number - FIC
8bd48a35-4dfd-460a-a80a-82b5b408feb4 | checkpoint | 4.3 - Formwork stripping and post-pour inspection
c7d43e7a-8f9d-5093-8a4b-4d52e321f13e | note | Responsibility - SE/PE
fe81a14f-24f1-55d9-8a00-bfd5bb8bcdca | note | Specification Reference - WBS-SS-CI-SPC-0007 AS 3610
852b2853-72f6-506d-98fa-8577e69f3c53 | note | Conformance Criteria Summary - Formwork removed at required strength, surface defects repaired
b8b3d43e-c038-5c94-9648-4636c1a9e025 | note | Method - R
9891ca5e-7ccb-5095-9720-d0e3e92df07a | note | Frequency - PL
fda86d00-3400-5903-8bb8-fb82c43a4023 | note | Hold/Witness Point Requirements: ROBAR - WP
85e96d13-2f5d-5f17-9507-b0b3fece3847 | note | Hold/Witness Point Requirements: SEPD - WP
0a4bd7b1-f33e-5730-ac11-612d5da9ef9d | note | Hold/Witness Point Requirements: Client - NA
75b70505-10e2-5d9b-9e25-7904a5df9da6 | note | Records or Checklist Document Number - FIC
7a2a3f79-c721-4d1e-b947-dc18d1f5a776 | checkpoint | 4.4 - Compressive strength test results
d9424698-e6e0-5ff7-9bfd-0e2c53e547ae | note | Responsibility - SE/PE
6ec2627f-8a97-5c03-af5a-019c415a48bc | note | Specification Reference - AS 1012
78c43181-4c63-5d3f-b231-1f9d99b1a146 | note | Conformance Criteria Summary - Compressive strength >32 MPa at 28 days
cca553e5-00e7-5383-9d91-a6d653cf8fa1 | note | Method - R
607b4b93-1450-5001-be97-b35ea35a03dd | note | Frequency - PL
94eaf632-b594-5c0b-9f3a-a4812d66b815 | note | Hold/Witness Point Requirements: ROBAR - HP
63c0599b-0391-5eea-bdcf-a9597d2f9a5b | note | Hold/Witness Point Requirements: SEPD - HP
5b762ccb-2aeb-56dc-bd68-f471fa2a718f | note | Hold/Witness Point Requirements: Client - NA
60e482d8-15b7-539f-8e9c-c18a26028d0e | note | Records or Checklist Document Number - Lab test report
d0aef6d6-2150-4101-8e0f-81db433cde14 | signoff | HOLD POINT
754cee9b-6ff9-4082-a63a-38db378a303c | checkpoint | 4.5 - Final inspection and acceptance of slab
19e7fb18-214c-57e6-9909-296009cfac42 | note | Responsibility - SE/PE
e1c03586-ca07-51c8-b828-2db389458790 | note | Specification Reference - WBS-SS-CI-SPC-0007
ec7f5f5f-009a-5e4d-9e8c-52a7b8cf27a3 | note | Conformance Criteria Summary - Surface levels, dimensions, and finish within tolerances
15729b03-188a-57a0-9a63-bbef6f700186 | note | Method - R
ab13780c-6628-5fc8-9c78-2de7863d1a8a | note | Frequency - PL
3e70de93-b5bc-54c4-95b9-8d8bfafa920b | note | Hold/Witness Point Requirements: ROBAR - V
e715a105-9bef-5711-9bd2-d3a852abb44e | note | Hold/Witness Point Requirements: SEPD - V
b544548c-1ee1-5e14-8f80-4e4da6d3aa3f | note | Hold/Witness Point Requirements: Client - NA
d9af8fda-c33d-5797-9eef-2fc4ed471e18 | note | Records or Checklist Document Number - FIC
6a4b7727-c31f-4f3f-9ffc-65e3a23434d7 | checkpoint | 4.6 - Joint Inspections
68f77389-68f1-537d-be80-4aedb6198137 | note | Responsibility - SE/PE
292252d4-ba6b-57b1-8d88-9430546fea3e | note | Specification Reference - WBS-SS-CI-SPC-0007
05331d1f-0998-5aba-92bd-37d3797a0095 | note | Conformance Criteria Summary - Expansion and contraction joints installed per design drawings
a4e1f2bb-de84-52a6-bd68-3ff6303ad730 | note | Method - R
238f8c81-da40-5b76-9223-e37dfafd3e04 | note | Frequency - PL
de8ca190-b7fa-55e2-b8d7-459808244d8b | note | Hold/Witness Point Requirements: ROBAR - V
1061bf03-34d5-529c-958d-26d20acbef6e | note | Hold/Witness Point Requirements: SEPD - V
a87ebd78-a4e2-56a6-af7f-12fd6ef0f031 | note | Hold/Witness Point Requirements: Client - NA
ec114ab5-f914-5cf2-ae93-ff224ac08977 | note | Records or Checklist Document Number - FIC
1635f63b-0b62-4c92-b120-68538e3f2114 | checkpoint | 4.7 - Post-cure inspections for shrinkage and cracking
779eed81-666d-5aee-bdfd-430a6de3d917 | note | Responsibility - SE/PE
10f54d9a-f47d-5f34-acff-0622826d9618 | note | Specification Reference - WBS-SS-CI-SPC-0007
6a2dbdf8-eac5-5d22-990d-a8a92ed97afd | note | Conformance Criteria Summary - Inspection for early shrinkage cracks and proper curing continuation
9a17d4a9-6bd9-5867-b4dc-9f8c7e0062b0 | note | Method - R
b48d1dfe-fa23-5409-b831-6e65898162b6 | note | Frequency - R
dea41777-1402-52ed-bc59-67ac9d610e5e | note | Hold/Witness Point Requirements: ROBAR - V
51576a8f-309d-52af-8afe-cb6b4ec9bfa4 | note | Hold/Witness Point Requirements: SEPD - V
e32cfdcc-1195-5c4d-9b08-a8a1f39587e1 | note | Hold/Witness Point Requirements: Client - NA
8d7d55ce-d725-57e0-99af-c380d3d2e264 | note | Records or Checklist Document Number - FIC
0f77a9d0-91bf-4c50-974a-5e4b817153d4 | section | Document Sign-off
285b1dfd-1fcc-480c-9911-3619506cb373 | checkpoint | Prepared by:
3982596a-a761-59db-ad28-1c2aeac32f1d | textbox | ROBAR - Name:
6447d541-e5a2-5787-a5da-be793cb495a1 | textbox | ROBAR - Position:
7b0724fa-534e-540a-8353-8dfc35931028 | date | Date:
ac70b828-d2fc-45d5-9f27-d38c654d3ce1 | signoff | Add Signature
cd03e5a5-d6ae-4eb4-b05a-71ef778feedd | checklist | RR-SEPD-BESS-ITP-003-00 - Electrical trenching | itp | RR-SEPD-BESS-ITP-003-00 - Electrical trenching - Layer
7654f174-92c8-49ba-a266-48cab6573c83 | section | Section 1: Preliminaries & Permits
53ef67cc-597e-48cf-8066-464e2d03e5a1 | checkpoint | 1.1 - Pre-Excavation Site Inspection
d0190c04-b1e1-5522-a84c-908056f468f8 | note | Responsibility - SE/PE
9f18be9e-5460-5be8-936b-7b3d97dfcc13 | note | Specification Reference - WBS-SS-CI-SPC-0006
80d52f20-b71c-5486-9438-c69f35b52b1f | note | Conformance Criteria Summary - Work area is clear, utilities and exclusion zones are clearly marked, permits are approved.
87f025b7-5419-57f6-8f33-b4054172d215 | note | Method - R
6a775003-1bc1-5daa-be5a-35fa689f6ae2 | note | Frequency - PW
3fd9e18c-da0c-5eee-94c0-d4c97024b39a | note | Hold/Witness Point Requirements: ROBAR - V
5b2512b0-0bc4-58c5-beec-cc17f24b2452 | note | Hold/Witness Point Requirements: SEPD - NA
91b08320-5cb9-5a72-a6b0-d8a3aaaa044b | note | Hold/Witness Point Requirements: Client - NA
bed6299e-f473-401c-87b4-74252aca392a | checkpoint | 1.2 - Permit approval (GDA/GDP)
bcc6f6c3-8b0a-543d-996f-9939e91305d8 | note | Responsibility - SE/PE
ed29ea22-a91e-54bb-973d-9768bb22d89f | note | Specification Reference - WBS-SS-CI-SPC-0006
e2baf64a-52b1-57f8-a2a8-2f0a24c894ad | note | Conformance Criteria Summary - Approved excavation permit (GDP) prior to commencing works
3384d2e5-ad57-5395-b6c9-4d5ac12a575f | note | Method - R
90901ba7-6d16-5d87-9e4d-691472cd9dd8 | note | Frequency - PW
b88b6350-b39e-5be4-95ca-0de667a17173 | note | Hold/Witness Point Requirements: ROBAR - HP
f6916a4d-ad15-5fca-b6ff-8841b604b53d | note | Hold/Witness Point Requirements: SEPD - HP
c775a648-5a49-594e-8c87-4f59b3502158 | note | Hold/Witness Point Requirements: Client - NA
246d147b-14d5-47ab-bb84-cbdab832323b | signoff | HOLD POINT
db7f275c-50ae-4277-b2f1-56cd36432ca4 | checkpoint | 1.3 - Site set-out
aec9a6f4-f0dc-52ad-80b1-4a4eb7af25f8 | note | Responsibility - SE/PE
f83b7dc9-3a88-5238-b6b4-dcf1c47b1786 | note | Specification Reference - WBS-SS-CI-SPC-0006
3d740ad1-75d7-5cbe-9cd8-bdbdc72f83e1 | note | Conformance Criteria Summary - Verify levels, site boundaries, and physical bounds per IFC drawings
c1efc1fd-e7b2-5c0e-b958-c123a3fb85f8 | note | Method - R
9bda7d91-b885-5d98-a34c-503d6c101043 | note | Frequency - PW
0c5f3e18-bfd6-53ed-a309-1c46411881a4 | note | Hold/Witness Point Requirements: ROBAR - V
1548f9f1-7e1f-581e-9f0f-124d8af96389 | note | Hold/Witness Point Requirements: SEPD - NA
1b246dd2-287c-5fe2-9c7f-f1f182cdaa1e | note | Hold/Witness Point Requirements: Client - NA
df8b91db-885f-4e11-93b3-af13a365f96a | checkpoint | 1.4 - Sediment control plan
1dd434c7-e769-514e-bd2f-0b9a05c9b6b7 | note | Responsibility - SE/PE
a83004f7-6c27-5777-a098-fc5943afe733 | note | Specification Reference - WBS-SS-PM- PLN-0024, WAE230103- 03-003 TM Rev0
7a003060-8a1b-55bd-a9bb-76bdf98be169 | note | Conformance Criteria Summary - Sediment control measures in place
aec5987b-2870-59ef-9ffb-22fe4ba2daac | note | Method - R
31caeda4-52f6-519b-9abb-8c36fe70ad13 | note | Frequency - PW
988e4824-e92b-51ee-96de-efb0b46c3bef | note | Hold/Witness Point Requirements: ROBAR - V
328aa11c-f685-5403-9e06-87d2bf076e93 | note | Hold/Witness Point Requirements: SEPD - NA
3165e1e8-2bcf-5742-a6d6-402e680e0db8 | note | Hold/Witness Point Requirements: Client - NA
7df50747-e5b9-482d-b66c-0d188aee1dee | checkpoint | 1.5 - Dust control plan
aa8f3a52-cd79-5ca4-83e1-233d4ca2c552 | note | Responsibility - SE/PE
de46817a-f16c-587d-8087-8fc1446db510 | note | Specification Reference - PP3 section 1.5 and section 4.1
cde58a9c-8ab5-5697-a5c7-b161fca1c505 | note | Conformance Criteria Summary - Dust control measures in place
66b80c25-d604-5ee2-96ad-56e3d5b4ea6c | note | Method - R
c4cd6564-ea86-51a1-a857-f368da47e832 | note | Frequency - PW
14c59c8c-342a-518a-b8f6-1a77d4a4e574 | note | Hold/Witness Point Requirements: ROBAR - V
e5915811-553e-56d0-b1c0-e21d4f59f595 | note | Hold/Witness Point Requirements: SEPD - NA
a25f7405-04da-5e48-8067-7773c72c3b76 | note | Hold/Witness Point Requirements: Client - NA
25ad360f-a523-4f42-a2b3-1631f1c1fd1a | section | Section 2: Materials
08df939e-d103-43e6-a9cc-280fac93927a | checkpoint | 2.1 - Import fill material inspection
13d613c8-3dca-5b48-855d-856922c3af88 | note | Responsibility - SE/PE
f82f7512-a719-53d8-aa79-bfe7b4122037 | note | Specification Reference - WBS-SS-CI-SPC-0006
14444482-9f51-57c5-b594-ef8ce1a8391f | note | Conformance Criteria Summary - Material certificate and test report for particle size distribution, moisture content, MMDD
eec94a03-3736-5fae-9f4a-ca3a4de87802 | note | Method - R
6c5e7c90-fed8-5dc7-9d9f-8bf2fcbf4ba3 | note | Frequency - PW
d4db6092-f967-53ed-b1f3-79b890d116bd | note | Hold/Witness Point Requirements: ROBAR - V
f99aeb19-9539-51a4-9378-70d7907924fc | note | Hold/Witness Point Requirements: SEPD - V
897bc3f3-188d-520f-adc1-00f465723d8b | note | Hold/Witness Point Requirements: Client - NA
848f7593-77af-4020-bfb2-22433371902e | checkpoint | 2.2 - Verify suitable foundation material (compaction >92% MMDD)
d1d483d3-febd-5825-af4a-2f5a6b30bf98 | note | Responsibility - SE/PE
cb7ee391-a714-5426-ad74-dd2c8ab23dd7 | note | Specification Reference - WBS-SS-CI-SPC-0006
b49385b4-4240-5352-952d-6d6849ebcbf7 | note | Conformance Criteria Summary - Geotechnical test results showing compliance
77852690-9264-5bb3-94d0-17133e7cc7fa | note | Method - R
72cadec3-5606-5821-b874-11a1027d8b17 | note | Frequency - PW
7066d96a-5fab-58c9-8d21-d795388d9a3d | note | Hold/Witness Point Requirements: ROBAR - HP
296635f4-e0f8-5048-aa19-9930848a54c3 | note | Hold/Witness Point Requirements: SEPD - HP
bd01c65a-a9ca-5e7f-9f16-d19d61d8034a | note | Hold/Witness Point Requirements: Client - NA
8e962a96-6c03-4db7-8ea8-6f6473d546b0 | signoff | HOLD POINT
c432d097-5f71-492d-885d-491e0b3b6637 | section | Section 3: Electrical trenching
87454746-1ed4-4c0f-9a3f-09af6db9993a | checkpoint | 3.1 - Excavation to subgrade – verify lines, depth and dimensions
cd53b764-42d1-589e-a589-e8e494c5d09c | note | Responsibility - SE/PE
c516f9ad-c913-5c86-9e57-50135b116dc3 | note | Specification Reference - WBS-SS-CI-SPC-0006
acb3ab0f-9431-5274-aeb5-509409f6d96e | note | Conformance Criteria Summary - Compliance with design drawings and subgrade preparation
07527758-acbf-5ca5-857f-33db8ed98c67 | note | Method - I
8ddf01d9-9b1e-5b60-a36e-9790482d79a7 | note | Frequency - PL
752a97c9-85a1-5f17-aeb9-277b9bc58c21 | note | Hold/Witness Point Requirements: ROBAR - V
590dfe67-208c-530d-ac74-a6ae6c08bfad | note | Hold/Witness Point Requirements: SEPD - V
6fc71692-3291-5fc3-98c6-218adb754d5d | note | Hold/Witness Point Requirements: Client - NA
c644692a-4714-44f7-9c2c-6206bf0ba7c6 | checkpoint | 3.2 - Stockpiling of excavated material – manage and segregate by type
033c0e1f-674e-50ad-8694-8b2de60fe1ad | note | Responsibility - SE/PE
33c4c894-c0d9-5e97-98ff-2325b7e79654 | note | Specification Reference - WBS-SS-CI-0006
a587f6c8-7a7b-5857-a80b-02a7fc384685 | note | Conformance Criteria Summary - Material stockpiled appropriately, no cross contamination
56ff2452-375b-5315-bf4b-c9b2348a780d | note | Method - I
e2853326-4ff7-5c48-949f-3c915cea64dd | note | Frequency - PL
301c205b-149b-5f5e-9498-eb611fe13a3f | note | Hold/Witness Point Requirements: ROBAR - V
18258a04-eaf6-566d-8876-8ec68b776a1f | note | Hold/Witness Point Requirements: SEPD - V
816bb2a0-58be-594a-9780-2c061c8fdab6 | note | Hold/Witness Point Requirements: Client - NA
30ce939f-69ae-4a05-ad22-f47d499b9f2b | checkpoint | 3.3 - Base preparation
c4b04a05-00b7-5fa5-b3d9-e44b0146a8c2 | note | Responsibility - SE/PE
92602d9b-e34e-51f0-8d19-58ee290ecccf | note | Specification Reference - WBS-SS-CI-0006
f3981a3a-b844-5091-ac80-8d8eddabdcaa | note | Conformance Criteria Summary - Base is level, compacted, and free of debris; compaction meets project specs.
293d5b9c-9218-50b0-95cd-faf4230a4278 | note | Method - I
57ea7975-81f3-5c8e-b683-a734dd531100 | note | Frequency - PL
0aec6e5c-48c0-5673-b46f-12c1638b4a43 | note | Hold/Witness Point Requirements: ROBAR - V
1929521a-83a1-55c0-a882-f48fe0494d8b | note | Hold/Witness Point Requirements: SEPD - V
3125e666-c8e1-5674-861b-c9b86474e173 | note | Hold/Witness Point Requirements: Client - NA
db6efce3-c5c5-4b4a-9d47-364f1a784530 | checkpoint | 3.4 - Initial backfilling and compaction
63793666-bd1b-5dfe-bbbc-41631e8462a8 | note | Responsibility - SE/PE
4e916971-f5bc-5f02-a2db-b3d501d43dad | note | Specification Reference - WBS-SS-CI-0006
9965f3a5-dda2-5e56-a4f9-34e4e4bb5692 | note | Conformance Criteria Summary - Backfill material compacted in 150mm layers to required thickness
fcc0d6be-481a-5748-bbf4-d75d76f04cac | note | ○ Material shall be placed to a depth of 150mm above the collars of pipes or conduits, 300mm above pipes and 600mm above culverts
fe5e11b6-2a2c-50ad-9a85-e7150a0db38d | note | Method - I
9e45b0ea-623b-5df1-a32c-fa2fad78ee63 | note | Frequency - PL
07ccba2c-447b-577e-86a9-bbea688fe3d9 | note | Hold/Witness Point Requirements: ROBAR - V
7b8c5ddf-51f4-5952-acec-9b503e7f7de2 | note | Hold/Witness Point Requirements: SEPD - V
137aee4d-6a8c-5c79-9ce4-419ddff47ffc | note | Hold/Witness Point Requirements: Client - NA
e8905af4-1fdb-4c36-bec1-e3462cdfa787 | checkpoint | 3.5 - Compaction density ratio for backfill
cf26edee-7497-595b-82ad-2af0059dcbd4 | note | Responsibility - SE/PE
470e0741-8996-587c-bd72-802740d76d57 | note | Specification Reference - WBS-SS-CI-SPC-0006
acb97759-5a5f-5e24-812a-1e505277f0d0 | note | Conformance Criteria Summary - Compaction test report showing >92% MMDD every 40 linear meters and every 2 layers WBS-SS-CI-ITP-920049
c8c88fa6-be73-5930-bad5-41f40d007f61 | note | Method - T
9afdacc5-ed15-5282-8055-930981ce925f | note | Frequency - PL
dcb8b992-dcb2-5c2a-a3de-017a8e7b9df1 | note | Hold/Witness Point Requirements: ROBAR - HP
12a2230d-d9c9-5ddd-8963-a0a0acd5696b | note | Hold/Witness Point Requirements: SEPD - HP
4a7b6c4c-e6b5-521b-9698-804864fea754 | note | Hold/Witness Point Requirements: Client - NA
8c79ef9e-58ff-44b8-9205-7dac3df879ad | signoff | HOLD POINT
8f69428c-7a6e-4b63-8efb-f8a58b87a724 | checkpoint | 3.6 - As-built survey pick-up
d1107f78-a62c-5759-87ef-ba4f47fafc00 | note | Responsibility - SE/PE
8a4a136e-7b35-51f8-8075-62542243884a | note | Specification Reference - WBS-SS-CI-SPC-0006 PPR
58911471-9709-5d97-a01f-2d83292b73af | note | Conformance Criteria Summary - Survey records and as-built drawings
d0459353-27a4-5827-8d07-093ae303797f | note | Method - S
57968d56-8cc5-5453-a2e0-507051660ddb | note | Frequency - PL
4dc61dd1-9954-5a24-8fc8-ca71f8a67073 | note | Hold/Witness Point Requirements: ROBAR - V
f0a942b1-4cf1-523c-b377-6c1547cacef9 | note | Hold/Witness Point Requirements: SEPD - V
da05514f-6030-5c97-bb2b-234505ab7f48 | note | Hold/Witness Point Requirements: Client - NA
7faf6ade-78e1-445a-8c5d-1f9e0a8561c8 | section | Section 4: Final Inspection
86fa1c40-2e06-4e1c-9c4e-2ba06186d42d | checkpoint | 4.1 - Finish level compliance with design drawings
602cde22-598f-5338-9fd7-76938ef525a4 | note | Responsibility - SE/PE
39c525cb-165d-51b0-8e04-520067683953 | note | Specification Reference - WBS-SS-CI-SPC-0006
0ea73b81-bd82-594c-ab35-fd98b24184e8 | note | Conformance Criteria Summary - As-built drawings
14a89535-2033-55ce-9a40-53149917dd74 | note | Method - S
5f0759e1-bb48-5f61-b3ce-87a7cff19b80 | note | Frequency - PL
cb55a035-0a3e-5fe0-9695-7757b4d8edfc | note | Hold/Witness Point Requirements: ROBAR - V
bcf59b43-8af8-55ab-9213-5e44a2a374de | note | Hold/Witness Point Requirements: SEPD - V
677063f4-e6b0-5de0-9927-4aa43c582e1e | note | Hold/Witness Point Requirements: Client - NA
ce53f0e1-828e-4bb3-84e5-0111285d9ef2 | checkpoint | 4.2 - Final Inspection Checklist (FIC) completion
c6a1eb85-f793-59f5-b9c6-9f376b18938d | note | Responsibility - SE/PE
6191a700-47f2-5930-b468-9e3679fa1f41 | note | Specification Reference - WBS-SS-CI-SPC-0006
bfeb2e33-5d2b-50ea-b8be-3dc1d76af61d | note | Conformance Criteria Summary - Signed FIC
5e0e1f85-ca57-5502-841f-5680afafd697 | note | Method - R
bd6ee844-197f-59b5-8a85-7e1684c8e798 | note | Frequency - PL
76372282-c736-5de5-905d-d2af6e33b474 | note | Hold/Witness Point Requirements: ROBAR - V
e2531e73-68af-526b-ad63-a5b4b96e243e | note | Hold/Witness Point Requirements: SEPD - V
3797a6b3-ffdd-5e00-9310-dfa448e3000a | note | Hold/Witness Point Requirements: Client - NA
942b0502-0b0c-47e4-9fd6-1ff440d90622 | section | Document Sign-off
c35b9e5a-1a34-4eb2-abb8-093847b0c633 | checkpoint | Prepared by:
0c294ba9-9199-5fe6-b1ed-104869f3c307 | textbox | ROBAR - Name:
edcc366f-77bd-54d0-bbb9-e120f59179db | textbox | ROBAR - Position:
9e1f6767-1601-5538-9d9d-1bf226fe14a8 | date | Date:
0b67d8d7-3778-46a7-aa98-e5649b64963c | signoff | Add Signature
37219507-935a-4c78-b17e-9d67ed64aea5 | checklist | RR-SEPD-BESS-ITP-005-01 - Drainage installation | itp | RR-SEPD-BESS-ITP-005-01 - Drainage installation - Layer
436b84c5-5f97-4c42-9d84-10a9d1647409 | section | Section 1: Preliminaries & Permits
27425897-a988-45ad-a6ae-320626e3a87d | checkpoint | 1.1 - Collect and verify information (Site boundary, utilities, survey map, design drawings)
a1cbd207-60d1-5504-a29c-047d947fb0bd | note | Responsibility - SE/PE
cd2e8b13-4b7e-5152-916d-df39215c8258 | note | Specification Reference - WBS-SS-CI-SPC-0006
70d477db-3067-52ac-9afc-7dba3310bd9c | note | Conformance Criteria Summary - Results included in work pack
5caa0d97-2387-5b65-a06e-212c9eb68955 | note | Method - R
96946c0b-51ad-5cbe-852d-2bcaff053625 | note | Frequency - PW
14dd2e93-911d-55e3-b631-bbb7aa016495 | note | Hold/Witness Point Requirements: ROBAR - V
3411205a-13c7-55e8-a9fe-ada270e515db | note | Hold/Witness Point Requirements: SEPD - NA
11ea78a1-0ef0-5e25-9094-9be4422c1403 | note | Hold/Witness Point Requirements: Client - NA
50145814-37e3-5cbd-88e7-b2bf754e5a5d | note | Records or Checklist Document Number - IFC Drawings
91b6a6f1-d3f8-49b9-9646-b7b6dcdcd4e8 | checkpoint | 1.2 - Permit approval (GDA/GDP)
a1502325-b03d-5b90-bb65-fdb86c5d1131 | note | Responsibility - SE/PE
3967094b-9e01-5704-b3d6-74b450af919a | note | Specification Reference - WBS-SS-CI-SPC-0006
1cd2c4c2-997e-511b-b1ff-66057692d84c | note | Conformance Criteria Summary - Approved excavation permit (GDP) prior to commencing works
ff549d39-83c0-5ce1-a372-99fa2d513422 | note | Method - R
32465b12-87f4-59f1-8d80-089fbe8bf904 | note | Frequency - PW
3eabfb22-3fab-5a4a-a8dc-310137defcd1 | note | Hold/Witness Point Requirements: ROBAR - HP
a5eb7bab-d45a-5431-9555-557826ac1a42 | note | Hold/Witness Point Requirements: SEPD - HP
4d64df7e-b53c-549e-b6f9-3907ee8dd86e | note | Hold/Witness Point Requirements: Client - NA
bc766235-9852-56bd-97d2-d6f184ac35ae | note | Records or Checklist Document Number - RR-SEPD-CI- SOW-002-01
a196f895-2f51-4aa6-b060-89bd43235302 | signoff | HOLD POINT
ed3d672e-54f5-445a-8777-297c6dee6942 | checkpoint | 1.3 - Site set-out
c9d77067-6a33-53b5-bb64-466d72b3045a | note | Responsibility - SE/PE
ad8cabd0-502d-567a-98bc-7b4691d82d4e | note | Specification Reference - WBS-SS-CI-SPC-0006
f7fc8c42-814b-593e-aaf7-6ec0134251d8 | note | Conformance Criteria Summary - Verify levels, site boundaries, and physical bounds per IFC drawings
73f9c019-05ef-55fb-bba0-28026f6cb21a | note | Method - R
3bd9f712-13f9-502d-a1b7-6f10cbdd65b7 | note | Frequency - PW
939327aa-5239-509b-9197-f5c11b77633b | note | Hold/Witness Point Requirements: ROBAR - V
4df215c2-112c-578e-942a-6084c1b486cc | note | Hold/Witness Point Requirements: SEPD - NA
92ecc7f0-44c7-56e5-acb3-57085dcaf119 | note | Hold/Witness Point Requirements: Client - NA
707d0a65-16de-51bc-97f4-7720036f876b | note | Records or Checklist Document Number - IFC Drawings
2e008a5a-4c83-4983-aba0-59671ddccdd7 | checkpoint | 1.4 - Sediment control plan
7ed1153e-5791-5a70-b9e8-7604c781bb7a | note | Responsibility - SE/PE
e1be991a-3748-5e60-b0a2-d0cc5dec55a8 | note | Specification Reference - WBS-SS-PM-PLN-0024, WAE230103- 03-003 TM Rev0
78b6f86d-ae06-5233-8843-202e1bfab6f9 | note | Conformance Criteria Summary - Sediment control measures in place
8e1554e0-3d95-5e76-bbc4-b52d9452e0aa | note | Method - R
29ee98f9-4b0e-54b7-818c-a9df45a4a473 | note | Frequency - PW
18f79cfb-4b32-5a78-8951-6499e53a2e95 | note | Hold/Witness Point Requirements: ROBAR - V
0b6a9226-476b-555b-a743-d00ac18bad2a | note | Hold/Witness Point Requirements: SEPD - NA
69435f86-3259-5336-af96-2cd2a2aa8329 | note | Hold/Witness Point Requirements: Client - NA
79571000-21c0-5343-8a13-9cb4cca656fc | note | Records or Checklist Document Number - SEPD environmental plan
7544c3a9-c050-4a4b-82db-20123c687b3a | checkpoint | 1.5 - Dust control plan
856d3e3f-1f86-563d-b335-4a0834ce908f | note | Responsibility - SE/PE
c8c6dcce-a2a2-593a-83ef-652a816a1f16 | note | Specification Reference - PP3 section 1.5 and section 4.1
6278cd07-8c47-5a9d-b81c-e8825d38af15 | note | Conformance Criteria Summary - Dust control measures in place
665f5894-a2f5-555e-8ed2-d9a5bb8f27db | note | Method - R
b92f959c-5f49-5ea7-a33f-43e5fb7949cc | note | Frequency - PW
77bab274-b02a-53bb-85fc-143273d6f69a | note | Hold/Witness Point Requirements: ROBAR - V
499017d0-7d94-54a8-bf7c-fe86fdcdca46 | note | Hold/Witness Point Requirements: SEPD - NA
f2e80817-9172-5054-912b-65c2b66e54f9 | note | Hold/Witness Point Requirements: Client - NA
539c58d1-99eb-54f1-9394-89fcf218157a | note | Records or Checklist Document Number - SEPD environmental plan
35c072cd-f5e6-4b8c-b044-66f56b55f8dd | section | Section 2: Materials
44e5b971-523b-436d-ba6b-3ba1b21de77d | checkpoint | 2.1 - Import fill material inspection
4ca2f01c-176a-53d6-9042-f712b8178a32 | note | Responsibility - SE/PE
7469d062-0814-5af5-9a44-18b9d76fc301 | note | Specification Reference - WBS-SS-CI-SPC-0006
ef937090-994c-5657-baf5-4c0385bdd737 | note | Conformance Criteria Summary - Material certificate and test report for particle size distribution, moisture content, MMDD
c9bd8f35-6da0-5421-83cc-fc99477f5094 | note | Method - R
c1d5d48c-cf6c-519a-983c-c273e1855a27 | note | Frequency - PW
de921931-daa3-5aab-8d6d-c41f6d9ae8ae | note | Hold/Witness Point Requirements: ROBAR - V
50fe4890-9887-5d15-9567-a0af5f565a0b | note | Hold/Witness Point Requirements: SEPD - V
9ddb2807-058e-549d-8231-fb73a8cc25f4 | note | Hold/Witness Point Requirements: Client - NA
abda1ab1-5e64-54a0-a166-0e8608d54508 | note | Records or Checklist Document Number - Material certificates
fa0fd4f4-deaf-4c92-b576-2e91767056c1 | checkpoint | 2.2 - Verify suitable foundation material (compaction >95% MMDD)
dad98bb8-87c4-59ab-ba68-a58f4c2fe194 | note | Responsibility - SE/PE
d949e8bd-7902-51b3-8cad-65948b11f127 | note | Specification Reference - WBS-SS-CI-SPC-0006
27dbd875-9f99-56f9-bbad-1d97f3952ddf | note | Conformance Criteria Summary - Geotechnical test results showing compliance
e1cf5025-f304-578b-9d36-68e8e23c5016 | note | Method - R
c3e7c1de-5b62-509d-a730-60eaf3de27a1 | note | Frequency - PW
b1b90902-4e8e-5f1d-a101-dd880aa0aecb | note | Hold/Witness Point Requirements: ROBAR - HP
36497c62-a023-5fd6-984f-e5dee0a7f1c6 | note | Hold/Witness Point Requirements: SEPD - HP
c271a7e3-4f57-5be7-ba3a-87311cc8252e | note | Hold/Witness Point Requirements: Client - NA
020ad674-9509-5787-bb18-10680a6c4960 | note | Records or Checklist Document Number - Test results
27e28b80-b0ef-4e04-abe9-b0ae60bc90a3 | signoff | HOLD POINT
10269c43-5631-4827-9193-11920983f7cd | checkpoint | 2.3 - Quality documentation RCP & precast drainage pits
f7336be0-1f85-5853-a975-8d7e689e46c2 | note | Responsibility - SE/PE
bfdbd015-6582-5251-bb9f-0e35661d3d43 | note | Specification Reference - WBS-SS-CI-SPC-0006
36e8ef5f-4771-531f-98bd-07080f0a3968 | note | Conformance Criteria Summary - Supplier’s quality system certifications
f146ff8d-1314-569c-81c7-82d812b7411e | note | ○ Product of compliance to AS 4058, AS 3500, AS 3996. (Load rating & liner shall align with design drawings)
5aa39559-4c64-58ba-a5ee-4481ff441d05 | note | Method - R
2cb4e406-a79f-593d-b8b6-c81725ab9d27 | note | Frequency - PW
06468ce6-efa5-5753-abc1-1845544122d9 | note | Hold/Witness Point Requirements: ROBAR - HP
778b94f5-d8fb-5807-ba8c-b556d4ebccba | note | Hold/Witness Point Requirements: SEPD - HP
a2ee3e6e-66fd-5126-a79d-587a524fa919 | note | Hold/Witness Point Requirements: Client - NA
4e2630fd-f48a-5b2c-8891-a1002fd6d5c6 | note | Records or Checklist Document Number - Supplier’s documents
ff372579-2782-4e6a-829a-a58f0e4cc4a0 | signoff | HOLD POINT
dbf87332-95e0-41f9-b6f9-eaee689bfb3c | checkpoint | 2.4 - Delivery acceptance of RCP
159e60f0-7dbe-5490-888a-fafab9a25fe5 | note | Responsibility - SE/PE
63c141a8-600b-5985-8793-5ee08677aa19 | note | Specification Reference - WBS-SS-CI-SPC-0006, AS/NZS 4058
12df593c-7ef2-5d2f-b6e4-6c8516eb60fc | note | Conformance Criteria Summary - Acceptability of defects of RCP’s.
86bcf5af-2c2a-5cfe-a8fd-91c16ee15d92 | note | ○ Fibre RCPs shall be rejected if fractures and cracks wider than 0.1 mm and deeper than 0.3 mm are present.
8f44ce19-6ac5-5c59-befa-31290b977152 | note | Method - R
83d49955-2214-5b32-a97a-aa615a2d6137 | note | Frequency - PW
ec12fc65-b31e-56e5-a55e-3ae0c65e2129 | note | Hold/Witness Point Requirements: ROBAR - HP
5af4d6e3-8be7-5d09-8371-0998ee9b8686 | note | Hold/Witness Point Requirements: SEPD - HP
73c8edf5-1914-5dd1-b66d-c8133381f307 | note | Hold/Witness Point Requirements: Client - NA
19198e37-f175-5065-b4ee-3dadb1a3cc7d | note | Records or Checklist Document Number - Delivery dockets
fe86dcac-f2b3-41f3-b7c1-2b5d3ffeacb5 | signoff | HOLD POINT
c4bc7d20-f3d7-4cfe-add5-25d8dad41281 | section | Section 3: Construction
608a94cf-e0fa-4782-bb69-7d708d607297 | checkpoint | 3.1 - Excavated trench
ba8b4b04-b885-5b98-86d2-6308fcb4c651 | note | Responsibility - SE/PE
697d3e42-01cc-515d-8a47-0f6952b545a7 | note | Specification Reference - WBS-SS-CI-SPC-0006
de61cbb7-ba82-5daa-a1c9-480f9e239b25 | note | Conformance Criteria Summary - Inspection following excavation of trench. Wacker plate to be use for compacting base.
c90b499c-bced-5f7a-8987-d43f6c487522 | note | Method - I
29525613-b690-5678-a8b4-e6f7aab0586d | note | Frequency - PL
22a1dc34-3912-5ea2-b2f1-ee09bafd499c | note | Hold/Witness Point Requirements: ROBAR - V
31b97e46-3138-5621-b0bc-9e7f66a4fb64 | note | Hold/Witness Point Requirements: SEPD - V
2be9607e-f4be-5143-886c-552d3627dac8 | note | Hold/Witness Point Requirements: Client - NA
693deb2a-a981-5291-ad95-8cd19b749fbf | note | Records or Checklist Document Number - IFC Drawings
67678156-39ca-4ffb-8e82-f94e075a8ec0 | checkpoint | 3.2 - Bedding
9926f445-caa3-5189-a7f3-eb29343078b4 | note | Responsibility - SE/PE
2b266d57-bc01-59a5-bfd2-dc198b5e8247 | note | Specification Reference - WBS-SS-CI-0006
a489f83b-5020-581a-9702-c1426c0a97f8 | note | Conformance Criteria Summary - Material to be compacted at 100mm depth minimum.
2700aba8-c700-5a25-b029-dbf0b9f90613 | note | Method - I
9aa378f9-8cd4-58b9-8413-520aab43061f | note | Frequency - PL
dcc01783-8804-5473-9b45-c87e7c05d2c4 | note | Hold/Witness Point Requirements: ROBAR - V
1d3f44b2-62cd-5bba-b2cd-db7db88d32ed | note | Hold/Witness Point Requirements: SEPD - V
038ef79d-c2d9-5879-a61c-61cebc91ae61 | note | Hold/Witness Point Requirements: Client - NA
41f3875d-4761-5248-8cdf-aa05c9ec6f96 | note | Records or Checklist Document Number - IFC Drawings
ae1a01e4-5712-40dd-ad8f-7e96336b5557 | checkpoint | 3.3 - Placement of concrete pipes
eb5011bc-a836-55b5-b55a-14d897bccfba | note | Responsibility - SE/PE
3d1e8594-c6c9-5d6f-9437-23705c81b05f | note | Specification Reference - WBS-SS-CI-SPC-0006 IFC drawings
4f261c80-f5eb-5404-b1a0-66791d8e5c05 | note | Conformance Criteria Summary - Placed and joint in accordance with the manufacturer’s specifications
2a737901-a66d-5be1-b163-d62a7b3cb15b | note | ○ Female ends upstream and lifting holes uppermost. Lifting holes in pipes shall be filled with plugs provided by pipe manufacturer
3b040e3a-e874-55ce-876c-0b4280116817 | note | Method - T
db633bf1-c313-5572-bcab-1a995ca99081 | note | Frequency - PL
e8a223fc-f20c-5109-b042-5931d3550ec0 | note | Hold/Witness Point Requirements: ROBAR - HP
dc94c861-0eff-5fa9-8300-7fa693cc5b8e | note | Hold/Witness Point Requirements: SEPD - HP
5c63ae49-f4c5-5ea6-ad1a-27e0346c9242 | note | Hold/Witness Point Requirements: Client - NA
bd74e0cc-63c9-5371-a5ca-90a8f2e89191 | note | Records or Checklist Document Number - This ITP
ea627f23-940c-4b9a-b5f3-4e95933677d0 | signoff | HOLD POINT
f5001589-f059-44de-9090-7e3b01c00563 | checkpoint | 3.4 - As-built survey prior to backfilling
05830a50-7c88-594a-bba8-7d36b5bdcbd9 | note | Responsibility - SE E
b0222b04-5906-526a-9e70-922f8ea5eecd | note | Specification Reference - WBS-SS-CI-0006
3989c0e7-1301-5427-baa8-421707525c08 | note | Conformance Criteria Summary - Variation of reduced level of invert from specified level:
3bc145cc-f26f-5cfc-851f-760995af4db4 | note | ○ Whitin +/- 10 mm of specified position. Invert of structure shall not impede the gravity flow of water into or from structure
1991bfac-e089-5ee5-b646-aac91d38202b | note | Method - I
f2b3bd5e-0674-5364-85d4-35e8becefcb8 | note | Frequency - PL
baa504ac-aae4-5294-a31a-7e0759f0dd2e | note | Hold/Witness Point Requirements: ROBAR - V
99b29e5f-bb58-5124-bdc9-7d9fd6bd450c | note | Hold/Witness Point Requirements: SEPD - V
0ace67fb-dec2-57a8-9a1f-d7c304dce237 | note | Hold/Witness Point Requirements: Client - NA
4ca19525-339b-550d-a2e5-1971a8b309f0 | note | Records or Checklist Document Number - Survey report
f3ce8f28-30ee-4c36-a41e-4f9498babdd4 | checkpoint | 3.5 - Installation of precast drainage structures
563dc397-7b00-5406-b27d-d98b6428771f | note | Responsibility - SE/PE
357b8452-fe0c-578f-a15b-f5731f26dd54 | note | Specification Reference - WBS-SS-CI-SPC-0006, AS 3500 Design drawings
25043b90-feaa-5e76-a0eb-50dbd18a1345 | note | Conformance Criteria Summary - Inspection pit cover to be installed flush with the final surface
fff2bdbe-3026-58b4-b53d-9296ad931b34 | note | ○ Where precast drainage structure is used, the external joint with pipe shall be strengthened with a concrete fill circling the joint.
76b295eb-9ccd-56e6-a997-2e25c745c510 | note | Method - T
16d40b8a-da10-582a-a15a-5d0d55b2bc5b | note | Frequency - PL
ac6a6e78-c307-54eb-bc6e-92e0768a75c0 | note | Hold/Witness Point Requirements: ROBAR - HP
1ae6030a-64fc-510c-ac1b-f37cbfb36105 | note | Hold/Witness Point Requirements: SEPD - HP
b0aef2ea-8257-5480-95e1-017995ee46b6 | note | Hold/Witness Point Requirements: Client - NA
8c206332-52f1-5d7a-8637-a69987b046ad | note | Records or Checklist Document Number - Test results, NER engineer specifications
f3bebc3d-a678-471a-848e-c525727f6e7b | signoff | HOLD POINT
464ebeba-3050-4fa7-b4b6-4730d376c91f | checkpoint | 3.6 - Drainage runs and pits fully installed and ready for backfilling
1b0466f7-a3ab-56f2-88ef-2161ef2d3264 | note | Responsibility - SE/PE
0fa7e02e-7298-5690-a4a6-060fd78b213a | note | Specification Reference - WBS-SS-CI-SPC-0006, AS 3500 Design drawings
8d5856ec-391b-5d6d-98d0-fff728f619e7 | note | Conformance Criteria Summary - NER engineer signoff prior to backfilling.
41c84220-6dde-5e69-bdbf-765a57ae0307 | note | ○ Drainage installed as per design drawings.
842f4ab5-7c92-5bc4-8b70-b0fb07d5cf42 | note | Method - T
93511fc4-01e4-5f6d-8ecc-9e29410952b2 | note | Frequency - PL
a20333e9-571f-50aa-b567-a3f4bcb599b8 | note | Hold/Witness Point Requirements: ROBAR - HP
1b34b5b8-7f60-5b8c-b850-54e65e9154c7 | note | Hold/Witness Point Requirements: SEPD - HP
1a21f6f3-f90c-5ddc-83e8-a44bd0e67688 | note | Hold/Witness Point Requirements: Client - NA
aaa83f2c-e89c-5622-a189-e4580824b937 | note | Records or Checklist Document Number - NER engineer specifications
2f6de4fb-cef6-494a-a621-b7c1d7a97ab5 | signoff | HOLD POINT
79fffcd6-9d0c-4f84-9df1-fb9594a607f7 | checkpoint | 3.7 - Trench/Precast drainage item backfill
019b45de-2787-569f-b62e-311318a60a1f | note | Responsibility - SE/PE
44985f41-c191-5d10-b1bc-2fade7f607a4 | note | Specification Reference - WBS-SS-CI-SPC-0006, PPR
2e554f5b-5fec-529b-848f-7775ac71adc2 | note | Conformance Criteria Summary - Unless specified otherwise, backfill layers shall be maximum 300 mm layers.
bfeeddd6-a41d-5663-86c4-af9573897ac2 | note | Method - S
63c02950-4e13-59be-9b86-d56bcccb268e | note | Frequency - PL
504c65b9-d339-5ebf-b899-31af4e663ec7 | note | Hold/Witness Point Requirements: ROBAR - V
69f0dd69-4caa-5f34-a66c-00dd980a564e | note | Hold/Witness Point Requirements: SEPD - V
07b2aa3d-6a77-5fb0-91fe-947462c4f8aa | note | Hold/Witness Point Requirements: Client - NA
9e64d17e-099b-5187-b97b-e6d5540bd099 | note | Records or Checklist Document Number - Compaction report
916be4fe-368d-4f67-a16e-d5f4a2e58d6e | section | Section 4: Final Inspection
908e64b5-47d7-4909-b4a1-1fcf92e59222 | checkpoint | 4.1 - Finish level compliance with design drawings
c1aca4b5-1051-551b-955c-debd3d956642 | note | Responsibility - SE/PE
1d7f5d50-6a75-5821-ba2a-780445846d0c | note | Specification Reference - WBS-SS-CI-SPC-0006
63518ed5-77ba-581e-8ef5-6045c5dbc5d9 | note | Conformance Criteria Summary - As-built drawings.
776c70cd-9f07-574e-a667-f971db6d671c | note | Method - S
169fb815-b773-5e5c-a002-8ab5318fa45c | note | Frequency - PL
4727fae2-1742-5287-91a3-3b728e9cf88b | note | Hold/Witness Point Requirements: ROBAR - V
0252ddf9-87fc-5f5d-9006-d1441de00421 | note | Hold/Witness Point Requirements: SEPD - V
864d9857-88f0-5da9-b26a-bd7c152ee1d2 | note | Hold/Witness Point Requirements: Client - NA
54473b72-d517-554d-ac12-6cf95e714cc9 | note | Records or Checklist Document Number - WBS-SS-CI- ITP-920049
b3004b26-9d8e-4afb-a541-5485c7be617f | checkpoint | 4.2 - Final Inspection Checklist (FIC) completion
12f63595-f802-5de4-a53f-c95faac00c2f | note | Responsibility - SE/PE
9c4fc9e6-34ec-53b8-87c6-c0bdd2e6fc4a | note | Specification Reference - WBS-SS-CI-SPC-0006
5952f050-ff53-53fd-92b7-b0393136cb7a | note | Conformance Criteria Summary - Signed FIC
b0eacdcd-b24c-557a-bc13-79f60442892d | note | Method - R
90aecb69-dc4e-5eb2-a55a-dd071f1a096d | note | Frequency - PL
675eeda5-4680-5350-ac04-f78ed10e33ab | note | Hold/Witness Point Requirements: ROBAR - V
6056fc06-c9ee-5f38-8599-262efd26c829 | note | Hold/Witness Point Requirements: SEPD - V
700d2c9d-63e5-50aa-b143-8fc9fb448d9b | note | Hold/Witness Point Requirements: Client - NA
0862c071-c7dd-5b8c-9bad-0b61eb2f597a | note | Records or Checklist Document Number - WBS-SS-CI- ITP-920049
625ec812-a878-4353-9dd5-b44d2268a565 | section | Document Sign-off
d946f204-738b-4c02-8744-bb054961bc70 | checkpoint | Prepared by:
7c5360b7-ef89-5b6b-9544-618892e6106a | textbox | ROBAR - Name:
6c694594-4a96-5f9d-8365-9ba69a3b132d | textbox | ROBAR - Position:
c4f48618-6811-581b-9f84-edb06b13d199 | date | Date:
78de3a49-b1b2-4c51-a2dd-00cacc052bbd | signoff | Add Signature
5bcc4286-813e-43f2-9a8b-4ec604f5ccc5 | checklist | RR-SEPD-BESS-ITP-006-00 - Sheet piling | itp | RR-SEPD-BESS-ITP-006-00 - Sheet piling - Layer
e38bb3a6-9ffc-4445-878c-870b5508e078 | section | Section 1: Preliminaries
35528bad-1a34-4285-ba04-19cba5a97e9d | checkpoint | 1.1 - Review of approved construction drawings and specifications
88d8eb78-9402-5035-8839-2790e67a0c26 | note | Responsibility - SE/PE
5afbde8d-599b-5940-8981-6647f3c2ab23 | note | Specification Reference - WBS-SS-CI-SPC-0007
191601a2-b8d9-58f4-b987-308bcfda1067 | note | Conformance Criteria Summary - Approved IFC drawings and project specifications available on-site
3fedd6c0-9c3d-5e19-ad9a-d491667a9693 | note | Method - R
784d8fb4-a769-59f7-9163-533f9b29abe4 | note | Frequency - PW
44cbcdc7-de02-5557-b65c-1ace2ed7ca72 | note | Hold/Witness Point Requirements: ROBAR - V
0cce41c9-aa5c-5b11-a100-536640134bb1 | note | Hold/Witness Point Requirements: SEPD - NA
e888aed3-0217-5716-9398-ba3eb99e9950 | note | Hold/Witness Point Requirements: Client - NA
fb170335-4099-5d13-ad76-4f3caaaf90bc | note | Records or Checklist Document Number - IFC Drawings
05f8a198-4079-4742-baf6-deced629fe79 | checkpoint | 1.2 - Site condition check and access preparation
5fce54a5-60b1-542f-a533-a523b442a1cf | note | Responsibility - SE/PE
b069e408-083a-565b-babd-bb371802992e | note | Specification Reference - WBS-SS-CI-SPC-0007
10bfdcb2-4b4c-509f-ac3f-6135ad54fb23 | note | Conformance Criteria Summary - Site cleared, accessible, and suitable for sheet piling works
f43333f1-083b-5071-a688-b229cb334c28 | note | Method - R
7263d2b3-deed-5d03-90a3-defa5ece14a1 | note | Frequency - PW
b1a0fb70-3ed0-5048-98a4-4646f5f1172d | note | Hold/Witness Point Requirements: ROBAR - V
78297045-cd31-5a80-8b9d-98f987a4d976 | note | Hold/Witness Point Requirements: SEPD - NA
a4ed57b4-7860-5333-bda6-a8918e494f2f | note | Hold/Witness Point Requirements: Client - NA
6f5447bc-6010-5e5e-9530-bc384cc59153 | note | Records or Checklist Document Number -
024c5cd4-1454-4613-8ca1-a72ccc56bb50 | checkpoint | 1.3 - Site safety induction and toolbox talks
d1f1aba9-8bf1-5856-bc61-f3c58b66e63c | note | Responsibility - S E
c932bc9f-9d7d-5c86-b4fc-d9aeed8f7b10 | note | Specification Reference - WBS-SS-CI-SPC-0007
27af3097-82da-5410-99d9-ac8f1eda3aec | note | Conformance Criteria Summary - All personnel inducted and briefed on safety, site-specific risks
ab860dab-392d-5e09-864f-30732cf722b6 | note | Method - R
b0ff81a0-cb13-5c88-bf3b-fffe5a30c81e | note | Frequency - P W
18f1c8cb-206b-52bd-b5d0-9eeba297f6a7 | note | Hold/Witness Point Requirements: ROBAR - V
a4d06172-4e31-5dbf-94ec-41c1c9435bdf | note | Hold/Witness Point Requirements: SEPD - NA
28bceea0-b8b4-58f4-8514-48addcf054fc | note | Hold/Witness Point Requirements: Client - NA
258de7fc-014d-54b7-b01f-4cf8afaba8dc | note | Records or Checklist Document Number - Site inductions records
a0906169-61a3-4a7e-8dc9-732bbb70a664 | checkpoint | 1.4 - Inspection of plant and equipment (e.g., excavator, vibro head)
610fde30-c69f-507d-b52a-5e4ee0c448bb | note | Responsibility - SE/PE
1197d90c-08f0-570a-86b4-486e96b35036 | note | Specification Reference - WBS-SS-CI-SPC-0007
06dbd220-10ff-5f5d-9ffd-d5bbe449c326 | note | Conformance Criteria Summary - All equipment calibrated and operational
ea53ff70-6ab6-585a-b46e-b2bf54885158 | note | Method - R
aa41bcde-64c9-53b1-9d40-6f46ded6d162 | note | Frequency - PW
5a2265ea-daed-5332-8e68-5932d73362de | note | Hold/Witness Point Requirements: ROBAR - V
0291f191-4109-5019-86a6-69a354512094 | note | Hold/Witness Point Requirements: SEPD - NA
2376727f-41fa-5a43-a175-771146c5dc2b | note | Hold/Witness Point Requirements: Client - NA
940e402a-9a44-5d19-b29f-e852cf3f7c7f | note | Records or Checklist Document Number - Calibration/P re-start
87d4ac8f-6e02-4d0d-8031-cd7e9e34758e | section | Section 2: Piling Works
4f13860a-d9f9-4263-9c42-061f791f20a7 | checkpoint | 2.1 - Verification of work permits
79188156-6a22-5527-8d78-6824924ce6b4 | note | Responsibility - SE/PE
309b9b45-4db4-594b-8424-cd724c54ff38 | note | Specification Reference - WBS-SS-CI-SPC-0007
cd74bc93-c1a2-5379-818f-0e7cf4a68bec | note | Conformance Criteria Summary - All necessary permits for works are in place (GDA/GDP)
3cc2690b-6ad0-5693-af4a-f960f0b3b23e | note | Method - R
c25ef95d-186b-5525-bf92-1abab298b505 | note | Frequency - PL
d99f95fb-ddf3-5a9d-a88d-15a5d8ce82c9 | note | Hold/Witness Point Requirements: ROBAR - V
1dbcc9ba-5e48-5199-b636-8669af845a03 | note | Hold/Witness Point Requirements: SEPD - V
7e773a6c-e7df-5526-8c03-239eab7c67d9 | note | Hold/Witness Point Requirements: Client - NA
3030efcd-37fe-5625-bbe4-3e96f1de14b8 | note | Records or Checklist Document Number - GDA/GDP
7a7410d9-1774-4b90-b884-0fa8ce10cad8 | checkpoint | 2.2 - Review of material, certificates & technical specifications
32c85b47-4e67-5e4e-b9f7-c61d148a53ed | note | Responsibility - SE/PE
b4b786e2-11c1-5880-9d7c-3400a02bf449 | note | Specification Reference - WBS-SS-CI-SPC-0007
dde2ae79-986f-5b5c-8393-6ef372ccbc49 | note | Conformance Criteria Summary - Verify mill certificates & compliance with AS 2159
66fbf21c-4935-5722-acce-eb3500950474 | note | Method - R
805e9715-8c19-585d-bcd1-3394f479a7bb | note | Frequency - PW
c425e5b4-a40e-50b7-ad7c-346a7ec8e70c | note | Hold/Witness Point Requirements: ROBAR - HP
f92c31ab-2e0a-5332-865f-6e6f538b19e0 | note | Hold/Witness Point Requirements: SEPD - HP
7ba9a1d9-5148-53b8-ac64-bfca5dcba674 | note | Hold/Witness Point Requirements: Client - NA
ab65f7e9-b47c-512b-9422-131a8407a107 | note | Records or Checklist Document Number - Product certificate of compliance
67c0ffed-715c-45ba-a69b-12d3707850aa | signoff | HOLD POINT
51c6086d-2e99-47ad-a41e-f91be014316c | checkpoint | 2.3 - Surveying of centre line of points for sheet pile(s).
114b6768-896d-5c79-930a-0e01b221a68d | note | Responsibility - SE/PE
2df8bb0c-0d6a-59eb-b356-b057cfc5fd16 | note | Specification Reference - WBS-SS-CI-DRG-0251
695bb3a4-0673-570b-9989-f29096b58936 | note | Conformance Criteria Summary - Confirm correct position as per drawings
7429ec58-30de-5414-b5d7-958ebca4a133 | note | Method - R
d8fabede-23e0-505b-9cea-e7fcf56405ce | note | Frequency - PW
6f4cc4d9-703f-5c69-968d-cab645720895 | note | Hold/Witness Point Requirements: ROBAR - HP
a1f68962-f49a-5ed8-8ce4-689bb0af8186 | note | Hold/Witness Point Requirements: SEPD - HP
745b66b7-d051-5160-8925-6455e7e3e5c6 | note | Hold/Witness Point Requirements: Client - NA
8d2b5ac8-a6a3-5a57-bcd3-e6030054eea9 | note | Records or Checklist Document Number - TWD FIC
84de8653-5903-485a-9b47-aaba761b20b4 | signoff | HOLD POINT
ad0c11cc-72f7-44eb-ba74-ca7cf4cd5ad6 | checkpoint | 2.4 - Installation Monitoring
9bfd4ad3-b12a-561f-9c19-8721eb2af1e0 | note | Responsibility - SE/PE
6c51d9d7-f8ff-5195-a5c1-65b4b2d2c33c | note | Specification Reference - WBS-SS-CI-SPC-0007, AS 2159 Manufacturer’s Technical Data
b938768f-4465-54d1-a713-dc04445c916c | note | Conformance Criteria Summary - Monitor driving sequence, depth and alignment
53c55a8b-3435-5598-bbec-75b33c96637e | note | Method - R
651770b4-de8e-56be-8745-bfa9a7deffad | note | Frequency - PW
4c7e1657-e8fb-5df8-8bb9-5ec94cc97008 | note | Hold/Witness Point Requirements: ROBAR - HP
d5dcf02f-e9c1-5789-881d-382aee36cbc6 | note | Hold/Witness Point Requirements: SEPD - HP
0dac3a76-9012-5f92-9afb-cd7ba542c806 | note | Hold/Witness Point Requirements: Client - NA
51c85b75-4b90-5903-9998-02410ca4f596 | note | Records or Checklist Document Number - IFC Drawings FIC
40319e96-4a92-41dd-b9be-94bfd765c931 | signoff | HOLD POINT
e78c3256-0dac-4922-a243-4afe1a202969 | checkpoint | 2.5 - Check vertical alignment during driving of sheet pile, and adjust if required
eb53bfaa-1b48-58eb-9ff8-0f63582fe198 | note | Responsibility - SE/PE
031e3e9c-6087-55ba-982f-48874840a1d2 | note | Specification Reference - WBS-SS-CI-SPC-0007
ca8fbc84-47d1-5ae4-a7f4-538573e62592 | note | Conformance Criteria Summary - Correct positioning of all embedded items as per drawings
9fce262f-1add-5465-bdfc-d595b90e9026 | note | Method - R
b8841339-7824-5ada-9eb1-70f7afa885e3 | note | Frequency - PW
37ba64cb-0a6a-5fa4-9395-2285203047dc | note | Hold/Witness Point Requirements: ROBAR - WP
312043f5-7b4a-561d-b03d-e151180b3ded | note | Hold/Witness Point Requirements: SEPD - WP
3f59faca-e657-5c09-b444-804a00d5569c | note | Hold/Witness Point Requirements: Client - NA
bc1f6baa-cc01-51e2-8958-9c075aaa90fe | note | Records or Checklist Document Number - IFC Drawings FIC
6f506aa0-0ecf-4a1c-8fba-afbaf007ecc7 | checkpoint | 2.6 - Ensure sheet piles are interlocked effectively as per technical specifications
f48c597e-1672-5dda-90cb-1e234e3e956f | note | Responsibility - SE/PE
ee953140-cb06-5ae5-8500-bfb38647cc08 | note | Specification Reference - WBS-SS-CI-DRG-0251, AS 2159 Manufacturer’s Technical Data
8d50622d-6922-5c0b-8772-ca3825a2e899 | note | Conformance Criteria Summary - Batch plant adheres to mix design, and delivery meets timing requirements
38530442-2fa6-579d-91f9-90ad5ae00091 | note | Method - R
cfa25d70-cc0d-5743-9930-3fc856ec8512 | note | Frequency - PW
713dcc5b-6034-5236-887b-9e1d65467262 | note | Hold/Witness Point Requirements: ROBAR - V
6ced302c-68ef-55e4-a995-11b1322b99c9 | note | Hold/Witness Point Requirements: SEPD - NA
3b883642-9273-5ec3-9a06-2c01505542ec | note | Hold/Witness Point Requirements: Client - NA
56a6eeb5-439f-5af3-9d91-05c313ecde30 | note | Records or Checklist Document Number - FIC
8793affd-0492-4975-82fe-3d7db3d39955 | section | Section 3: Final Inspection
bc7d65d0-ae08-4d2b-945a-2d7cd24a9f54 | checkpoint | 3.1 - Pile Verticality Check
c9dcdd0e-3a94-5299-926a-dc99a58f1766 | note | Responsibility - SE/PE
abc6530f-da7c-5fed-8081-65ef39df5456 | note | Specification Reference - WBS-SS-CI-DRG-0251
be76a8a0-70d8-5b75-bbce-8da306651955 | note | Conformance Criteria Summary - Ensure piles are plumb and no gaps or misalignment
c30f6898-9b5d-5b19-ae18-7217de045e84 | note | Method - S
ff4ff283-7afc-55e0-86aa-5c87a9f9d4dd | note | Frequency - PL
2627ee87-5d51-5377-81fd-f9f949a47196 | note | Hold/Witness Point Requirements: ROBAR - V
c53232e1-c134-525f-8f2f-73f2c9fa8d15 | note | Hold/Witness Point Requirements: SEPD - V
2eea13fa-fb34-57d8-9bc7-68e68367a7c1 | note | Hold/Witness Point Requirements: Client - NA
8a6d1eab-c78f-5dd3-bfd2-7dd22ed7fba6 | note | Records or Checklist Document Number - FIC
27644a18-e4ac-4a2c-80f8-081955faf83c | checkpoint | 3.2 - As-Built Survey
eae944a3-886d-5f00-a1f1-7ed005ba3e58 | note | Responsibility - SE/PE
c2ba56f8-d4f1-5c91-93ad-3be465dcdd18 | note | Specification Reference - WBS-SS-CI-DRG-0251
a9520e83-8f79-526d-8087-dd94ca8169f6 | note | Conformance Criteria Summary - Confirm final location, depth & alignment
f0efca59-411a-590d-85a9-e88bf357a93f | note | Method - R
41b5a781-064b-56e0-9ec4-525622cc3209 | note | Frequency - PL
b6c08d9c-e74b-5182-9736-bb72c76bc44e | note | Hold/Witness Point Requirements: ROBAR - V
98d97eed-47a0-5295-ab93-dda9cc0563a9 | note | Hold/Witness Point Requirements: SEPD - V
adaf5d36-4f96-51c0-8784-be1d580e324c | note | Hold/Witness Point Requirements: Client - NA
4e4a0427-5ae4-5a8d-8a98-a62a9863ccea | note | Records or Checklist Document Number - FIC
13bb3333-4cfa-4f32-8816-792046581a99 | checkpoint | 3.3 - Engineer’s Final Sign-Off
e1d78c7d-be6a-5dbb-b040-ef30b5a311b6 | note | Responsibility - SE/PE
0da57aff-8c3f-5fb3-9804-202b8fe6f188 | note | Specification Reference - WBS-SS-CI-SPC-0007, AS 2159
80a7f348-1922-543b-a077-68b89d7f005a | note | Conformance Criteria Summary - Ensure compliance with design
6c934d0f-09a4-534a-973e-f5f67d89a7a8 | note | Method - R
2c49ca5b-54a5-5f7b-ae20-ba140b6abb78 | note | Frequency - PL
e6368d0b-6e16-58f3-9fe0-3cad224999fd | note | Hold/Witness Point Requirements: ROBAR - WP
dd4d961c-6a90-56d9-a3b8-a57e569d5d8f | note | Hold/Witness Point Requirements: SEPD - WP
78c4d710-5d33-5196-b147-5321e11c0f64 | note | Hold/Witness Point Requirements: Client - NA
d559407a-60cb-5df2-b4cd-e8f49319e00f | note | Records or Checklist Document Number - FIC
288f4330-71e1-4dcd-860e-1879aab393ce | checkpoint | 3.5 - Final inspection and acceptance
b1c43674-6189-540b-a597-963f14ab7c99 | note | Responsibility - SE/PE
c9d7bcf5-4b3a-5625-be82-c25a147c5247 | note | Specification Reference - WBS-SS-CI-SPC-0007
e9e14d10-f246-534a-aec1-c2e3ec67ba16 | note | Conformance Criteria Summary - Finished levels, dimensions within tolerances
f7213aa6-be26-5452-a5c4-876da113419a | note | Method - R
64d19139-036c-5efa-92b2-c06546b4e5d7 | note | Frequency - PL
5b4836ad-5b4b-57b7-8164-5ab4147e9d46 | note | Hold/Witness Point Requirements: ROBAR - V
4092792a-703a-52db-b928-ec21cf8e8f72 | note | Hold/Witness Point Requirements: SEPD - V
b6643199-db49-5487-81e7-74fa679547d1 | note | Hold/Witness Point Requirements: Client - NA
8b37beae-9921-583f-8b90-dc460d53077d | note | Records or Checklist Document Number - FIC
3ce48c72-0ba3-4c08-b844-1676278d4f51 | section | Document Sign-off
20107e80-a576-4b97-8692-c508107ac26d | checkpoint | Prepared by:
188e333f-27a4-56ec-8371-255eb108d566 | textbox | ROBAR - Name:
da08690b-a565-54c9-b7ed-832a456ebfa8 | textbox | ROBAR - Position:
bc810d2f-44cd-52ac-92f9-a5ea41b21567 | date | Date:
625cdb96-5ddd-4bf4-907a-fa674b3eb1f2 | signoff | Add Signature
4a83d5a5-d96e-4a80-9be0-8bfaae6214b5 | checklist | RR-SEPD-BESS-QA-ITR-001-01 - Concrete Pour Record |  | RR-SEPD-BESS-QA-ITR-001-01 - Concrete Pour Record
ea74b003-0606-4ae1-af6b-a214e55f4c37 | section | Concrete Details
4c8e57af-2f8b-4d4c-bb4f-f9cbfe22e578 | checkpoint | Details
f5825e3d-fd11-5299-bc63-48e3abcf9781 | date | Date:
82afeed2-ccd5-5651-8fc1-01089bf2b8af | textbox | Premix Supplier and Plant:
a6e7cdec-ff43-5b4a-a8fc-34e973d97bc7 | textbox | Concrete/Grout Grade:
325ce011-a686-5b5b-acde-70b288016fc6 | textbox | Nominal Slump:
a84abc7b-403f-45b8-87a3-36961d9b3600 | section-nested-checklists | Concrete Pour Record