## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8cff2206-129e-4644-90b8-be16ef09adb0 | checklist | DN1211-001 ITP Stormwater Rev 0 | itp | DN1211-001 ITP Stormwater Rev 0
2d4d7028-cc67-47fb-bc4a-85c5fb76d593 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
4527df09-8192-41d9-91e4-0a524ba75d96 | checkpoint | 3.01.01 - Construction Pack
ed941b59-045d-5324-935c-4edacad53d24 | note | Acceptance / Conformance Criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
7607b137-0671-51a1-951e-8fe699bca7cf | note | Standard / Specification - Downer
1a261d26-8d45-54cd-974c-ca5bb4ac14e5 | note | Verifying Document - Construction Pack
dea16211-027b-5047-9162-7ec4d561fef0 | note | Frequency - Submit 5 days prior to commencement of works
e9ed4920-b239-5865-b2fa-0990017f31df | note | Verification Activity: Activity - H
a5d7357f-7bdd-5493-86b3-a183043befc6 | note | Verification Activity: By - PE
0f7a9e73-1447-4c56-b835-e7944a700dd0 | checkpoint | 3.02.02 - Survey Setout
560b023e-147d-55a2-8e7a-6f19ffb12b8f | note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
4a613baa-0a12-558a-9c2d-7fd82d39c8f2 | note | Standard / Specification - Downer
ae9eaa9a-093e-5ab9-9194-2e331e70a97f | note | Verifying Document - Survey Records
c218bedd-8cca-5021-8535-712a63f6ba1a | note | Frequency - Prior to Works
331200dc-2a8c-5760-bf25-c2480cb1e2e3 | note | Verification Activity: Activity - H
2c23c83f-acf0-5b8d-a45d-f108326dc0ea | note | Verification Activity: By - SV
bfe23b37-5f1c-4380-b939-e4ed0c30ac3b | checkpoint | 3.01.02 - Service Location
4c237af8-4b41-5255-a9a3-16dc1c9cb2f9 | note | Acceptance / Conformance Criteria - Complete the Excavation permit process to identify, locate and protect all services.
70b89522-a4f1-59a0-a34a-0763adc06ad0 | note | Standard / Specification - Downer
2fc828f2-420d-566d-bf73-eeb8dee67d5e | note | Verifying Document - Excavation Permit
ab07887f-321d-5f8c-90d1-45ba4fd516de | note | Frequency - Prior to Excavation
8a58eb97-5274-50e7-adf9-f0281a9d1263 | note | Verification Activity: Activity - H
d3bc6fa7-571e-57a9-9f9c-a1f93196bfc6 | note | Verification Activity: By - SE
4f68fe33-f844-431a-a65d-f2861ef54a9c | checkpoint | 3.02.03 - Internal Permits
a347d2b0-a5ba-55b1-9e68-bfd7c210480a | note | Acceptance / Conformance Criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
4d2a1a95-aec1-51d6-927c-a766ee451138 | note | Standard / Specification - Downer
6e7adeed-b1bd-5543-8106-9a55f1345623 | note | Verifying Document - Internal Permits
85667c04-f2ca-5162-97df-39d3d645efdd | note | Frequency - Prior to Excavation
edd023ec-719b-5ce7-b19e-16a2885d6309 | note | Verification Activity: Activity - H
76da0f14-88c5-5dca-8c1d-05244ea3889b | note | Verification Activity: By - SE
321ebddf-81df-4ed6-91a5-aef27fd4ed7a | checkpoint | 3.01.03 - External Permits
467ca4c7-a6dd-5676-bcb1-2e7a71015ad7 | note | Acceptance / Conformance Criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
79a18264-8b33-5111-81b4-a0a57702ebde | note | Standard / Specification - Downer
12b31bbf-e3f9-5351-8e68-cacdbfa3358d | note | Verifying Document - External Permits
0c3697d8-606a-5355-88b4-ddff917a49e1 | note | Frequency - Prior to Excavation
85ad7aba-b471-542e-9548-bf1406fb8e7f | note | Verification Activity: Activity - H
19b250c0-3c4f-521b-bc99-55e8680c70b3 | note | Verification Activity: By - PE
5c76e8e8-367c-46b3-b7ab-81bf7505081c | checkpoint | 3.02.04 - Approved Construction Drawings
44e9c8ba-e41e-5511-8474-4941676b1db9 | note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
9b958b4c-d9cd-5460-9bd7-e0ba192ad0e6 | note | Standard / Specification - Downer
95dbed92-8d36-5187-b9f1-f7f29077e822 | note | Verifying Document - IFC Drawings
188acaf8-10f8-5fb7-b161-ddf2b5eee7b5 | note | Frequency - Prior to works start
cca3b916-fec5-57fa-a8fd-438689df35ab | note | Verification Activity: Activity - H
f7e4c0d9-2353-537c-aff2-ab5a287ae4c8 | note | Verification Activity: By - PE
b4243508-5f7b-4b84-acaa-52db86020dfa | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
195eaba4-e2c8-4dab-9b1a-f403d94170f1 | checkpoint | 4.01.01 - Concrete pipes
9adc9a2d-045e-5e23-a8ac-539783ed6e25 | note | Acceptance / Conformance Criteria - RC pipes shall comply with AS/NZS 4058 for the class nominated on the drawings.
4cefca3e-c621-5384-a3a7-52d9d3957ef4 | note | ○ Pipes shall be rubber ring jointed unless otherwise shown on the drawings and rubber rings shall comply with AS1646.
4b3af587-9683-5923-b97a-2bfc64d92402 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.1
d957498e-344a-57b7-bc91-3d990a19576c | note | Verifying Document - Material Certificate / Datasheets
bac41fe5-9ce6-59c4-b3ab-d1c73971b886 | note | Frequency - Prior to use
ac78369b-cfc5-5723-96e4-2361a3ea32fb | note | Verification Activity: Activity - R
4448271c-aec9-5d34-8708-fcdef0f9b7ee | note | Verification Activity: By - DES
a1d7b594-a2e5-4b36-9cdd-49a30fa661b0 | checkpoint | 4.01.02 - uPVC pipes
f0683e84-9738-50b3-a41d-35b92162d092 | note | Acceptance / Conformance Criteria - uPVC pipes shall comply either with AS/NZS 1254 or AS/NZS 1260 and have the minimum strength as detailed on drawings
34947458-a0d6-5828-ba75-4190b714238e | note | ○ Pipe joints to be factory‐made spigot and socket, flexible type
8b2d6460-6cff-5daa-b6e6-7f8288a29694 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.3
2f44b398-a028-5729-9e98-860cb7cc8c61 | note | Verifying Document - Material Certificate / Datasheets
84214fde-6e5e-5352-9163-1b824e0d5510 | note | Frequency - Prior to use
fcdf153b-3aca-58c7-a3bf-d188895bcd64 | note | Verification Activity: Activity - R
9bb0cce1-3ec6-5419-8760-d7c55f74dc34 | note | Verification Activity: By - DES
7e0ecffd-10d8-4ee8-8516-79c11f006f55 | checkpoint | 4.01.03 - PE Pipe – Profile Wall
9a308a55-0860-5992-9be5-44b36c805e80 | note | Acceptance / Conformance Criteria - PE pipe to be used in gravity situations shall be PE100 Profile Wall pipe to AS/NZS 5065.
aed94f90-05ff-55a9-91c5-c36e1f1afcbc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.2
35bad388-3360-5371-b7d9-77932a998b8b | note | Verifying Document - Material Certificate / Datasheets
6cad8bac-24a2-58fa-a02e-35d4e65dc46f | note | Frequency - Prior to works
a04ea7b9-a44d-5eb9-8261-97022c172090 | note | Verification Activity: Activity - R
b9872fda-1592-5ae4-941b-92c0d17856e2 | note | Verification Activity: By - DES
bd47eec3-a6f8-49ca-805c-35fcbc826807 | checkpoint | 4.01.04 - Other Specialised Materials
23d596fc-3fa7-5ae4-a8c0-c4b3e8b0ffde | note | Acceptance / Conformance Criteria - All other pipes and pipe fittings supplied as per drawings, including:
8d607cc9-c0b6-5df4-b5fc-7a77c38c3ccd | note | ○ Any Mortar Lined Mild Steel (MLMS) pipes manufactured from arc buttwelded steel tube with external black HDPE coating. Pipes joints to be flanged, welded hemispherical joints or jointed with welding bands.
be72994b-f283-591d-a395-ca199073eac8 | note | ○ Gibault Joints assembled as per manufacturers recommendations
3eb05f78-a6db-5899-8f27-69377fc491cc | note | ○ Flanged Joints made with moulded rubber gaskets or jointing rings as per spec. All proprietary products supplied and installed as per manufacturers instructions.
26689c0a-4f0e-5284-9764-c5cb9f2e9ac4 | note | Standard / Specification - Aurecon Civil Spec 17.11.5,17.11.6
737bfd8a-2e51-50a6-8bb2-b254641c9aeb | note | Verifying Document - Material Certificate / QA Sheets
f7d167bc-441a-50fe-a6ae-2bda3a7f34e9 | note | Frequency - Prior to Use
911ec583-2bc6-5bfc-820b-45d0ad9e6435 | note | Verification Activity: Activity - R
a28b0823-fdf8-55cc-8bd4-2d6e9f9cda4f | note | Verification Activity: By - DES
72a56231-7abc-44ef-885c-6aaf5ad520f1 | checkpoint | 4.01.05 - Concrete
127c0086-aff3-57e8-9c26-e03167393225 | note | Acceptance / Conformance Criteria - Any structural concrete or mortar mix requirements as per Section 14 of this civil spec.
9819d098-86ad-5654-bd5b-242509481579 | note | ○ Site concrete used for pipe bedding to be 1 part cement to 7 parts AP20 with water as required to produce firm, moist mix with min 10MPa 28‐day strength
7defe212-9dbe-50da-976a-ab20cf25d894 | note | ○ Arrange pre‐pour inspection with Engineer 1 day prior
506a82f4-c60f-51c6-a67c-56c06132ec5a | note | Standard / Specification - Aurecon Civil Spec Section 14,17.11.7
cd472632-f0f8-5553-a4d1-1cc26f09f46d | note | Verifying Document - Supplier Records, Concrete Dockets
149e14bd-6c58-531f-b542-fe6bfbc6d42a | note | Frequency - As required
7ed4c668-3f4f-5693-8b1e-9d8a5fcac2a3 | note | Verification Activity: Activity - H
3745e15d-fe1e-5e5a-8359-2e5960a922b7 | note | Verification Activity: By - PE
2b22b82a-c061-4034-995c-408cdd287b85 | checkpoint | 4.01.06 - Pipe Bedding and Backfill Material
debfae14-ef3a-55b5-98fa-91e693499337 | note | Acceptance / Conformance Criteria - The basecourse aggregate shall be sampled and tested by an IANZ Accredited laboratory for Crushing Resistance, Weathering Quality Index, and California Bearing Ratio.
a03d4765-5fb9-5c33-945c-d1720efc57d5 | note | Standard / Specification - Aurecon Civil Spec 17.12.15 TNZ M/4 Asset Owner Specifications
1364df2c-b6ed-5467-8ab4-0e54e447ce09 | note | Verifying Document - Material Certificate / QA Sheets
ce51d16b-059d-5684-8ab9-3b333f0090ff | note | Frequency - Prior to Use
c5b9cfa1-d202-57f0-b540-98d5abc01437 | note | Verification Activity: Activity - H
6cfc08a5-cc34-5264-8174-e6086579958d | note | Verification Activity: By - DES
cbcfc19c-9f81-4dfc-8f81-af17e67834f4 | checkpoint | 4.01.07 - Catchpits, manholes, and drainage structures
233fa766-7dd9-5a5f-b80c-37865b637a36 | note | Acceptance / Conformance Criteria - Manhole, catchpit & service pit frames and covers supplied and set to correct grade and finished level as per drawing details.Pre‐cast items manufactured and supplied as per NZ standards. Manhole segments to be minimum 20Mpa
8eedeedc-6c24-5800-9c29-160f7e065735 | note | ○ Manhole/service biscuits to be level with top of subbase.
6647dd47-6eda-590e-b7f7-dee6b0f2fe72 | note | ○ Re‐entrant corners require trimmer bars as detailed on drawings
95968c82-1db1-555c-8676-b97f79074adf | note | Standard / Specification - Aurecon Civil Spec; Section 17.11.16-18
cf6888f5-b4c9-5ca6-8f5d-daa500bcef3f | note | Verifying Document - QA Checksheet and Supplier Records
66a52d92-9afe-5042-8b89-7f159e8e617a | note | Frequency - Prior to place pavement concrete
bdb90f46-3150-5a49-8a21-2eedb579311e | note | Verification Activity: Activity - R
f64ca9f9-233b-5451-a09a-2eed002bb5dd | note | Verification Activity: By - PE
fdcb322e-f85c-432a-8b42-e0f44f21d46b | checkpoint | 4.01.08 - Step Irons - Access Ladders
1585664f-66c4-5f44-b291-8be4da1ffb82 | note | Acceptance / Conformance Criteria - Check if amended by Drawings to be Type 316 Stainless Steel or Plastic Coated.
f2163e57-1279-5bab-9bb4-f79a1bde9a7f | note | ○ Otherwise, Step irons shall be “safety type” 24mm dia mild steel to the dimension shown on the Drawings, galvanised after fabrication at the rate of 0.7 kg/m2.
2f11480c-647a-5753-a120-cabeddf52a92 | note | ○ Installation shall generally comply with section 5.7 of AS/NZS 1657 except that ladder cages shall not be fitted
95ab47bf-2125-591c-9a2c-e8f7bab25acc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.19
03f3f629-b02a-5fbf-b5c3-4d4a3f4c41d6 | note | Verifying Document - Supplier Records and QA checksheet
0dde39a7-86a2-5525-8b83-3d832eb6e3ee | note | Frequency - Prior to use
64df4f6d-5416-5dd9-8fff-99a21a97493f | note | Verification Activity: Activity - R
b2d03611-494e-5951-a765-cf6135780868 | note | Verification Activity: By - PE
ff1b383d-b706-431d-9ae4-42b8e629d255 | section | SECTION 5 – CONSTRUCTION ACTIVITY – DRAINAGE INSTALLATION
9d4d0c9e-435e-48f6-84db-f2992a12a460 | checkpoint | 5.01.01 - Protecton of Piplines
f78a821e-415f-5e2e-b73d-12755d4c10c2 | note | Acceptance / Conformance Criteria - During construction, the Contractor shall be responsible for the protection of all existing and new pipework.
79d110c4-a6f1-5a7b-9c4a-d4bb116e1575 | note | Standard / Specification - Downer
d5f090a2-98e9-5bb5-9c33-317628bfec03 | note | Verifying Document - QA Checksheet
7aa323ce-0bf2-51aa-bed4-bea82733419f | note | Frequency - Daily
e11d4164-f482-5196-b2f6-cfe5399e7ed0 | note | Verification Activity: Activity - I
bb8094cd-984d-53e2-ab88-a054c27a114a | note | Verification Activity: By - PE
a345a459-81d5-401f-9b6c-5efc0032e920 | checkpoint | 5.01.02 - Depth of Cover
243d57b8-72c2-5de5-8e07-495866fa8eb0 | note | Acceptance / Conformance Criteria - The minimum cover as detailed on the drawings.
52dd0f39-9f8f-5b99-9415-0d0f0bb8259d | note | ○ If minimum cover cannot be achieved notify Engineer and provide adequate protection to the satisfaction of the Engineer.
f932b781-7a84-51f9-8eb8-5480477b8911 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.17
63690037-5f08-537e-b78f-7239f40fa81e | note | Verifying Document - Site Record
cb9cd2d0-c8d0-5f02-b5f3-c8f666eacf4f | note | Frequency - During Installation
0e7f727e-040d-5830-a7ad-691f2a2c6464 | note | Verification Activity: Activity - R
378d59e2-471b-5ae4-9551-fa2d5219ec41 | note | Verification Activity: By - SE
782406fe-3996-4549-8990-75ef934d7938 | checkpoint | 5.01.03 - Length of Open Trench
be4d85dc-0814-58ae-b359-044c531fa8f1 | note | Acceptance / Conformance Criteria - The length of open trench shall not exceed the greater of one manhole length or 30m and when offsite this open trench shall be reduced to a maximum length of not more than 10 metres.
c1fc1e3f-0427-5c6d-8d7f-ceed5d0837aa | note | Standard / Specification - Aurecon Civil Spec Section 17.13.3
f60db694-6383-5f4c-8200-de2a6a2562b0 | note | Verifying Document - QA Checksheet
b02390a5-ab99-5a50-9c7c-467ae16684f5 | note | Frequency - Daily
cc9e8e61-6d2f-521e-9214-3253db507e97 | note | Verification Activity: Activity - R
a65c64cd-9b3b-56cd-887c-d2a6ae05f037 | note | Verification Activity: By - SE
5b80427c-41a2-40c3-b07c-5a2a6584f46d | checkpoint | 5.01.04 - Trench Dimensions
7bbb3f16-a2d4-57be-b31f-e6d1fd87fe10 | note | Acceptance / Conformance Criteria - Excavate trench to lines, levels, width and gradients shown on drawings.
9b504735-98aa-5d86-a5d7-1db6b1b9cceb | note | ○ Trench of sufficient width to permit installation of all materials and fittings.
a874d695-57ab-5bb3-b931-01c9114413f3 | note | ○ Pipes minimum 100mm from trench wall.
492749dd-1523-5761-b1b5-d6da9aa5d14f | note | ○ Trench width <600mm pipe diameter at top of pipe level.
29734e0c-11ca-5ec5-8e90-7f62f02dac9c | note | Standard / Specification - Aurecon Civil Spec Section 17.13.4
8c7ca7c7-788d-511b-aa79-e1397c8aeff1 | note | Verifying Document - QA Checksheet
b21a2c41-b238-5a2d-adf3-6f9bdc934c18 | note | Frequency - Every 10m
9416b7bc-a97d-5f66-bc1c-8a231bdfbd3d | note | Verification Activity: Activity - R
1eafbd54-b51c-50ce-b6ee-98564bf17c0f | note | Verification Activity: By - SE
5fdf8d9e-095f-4361-89bb-27b8cb8ec707 | checkpoint | 5.01.05 - Keeping the Excavation Free of Water
1a850783-2d0b-582e-a04f-6a1c76590acf | note | Acceptance / Conformance Criteria - Subsoil water shall be kept below the metal foundation
141cf7f6-e550-5f0f-af0e-a79cb3d9383f | note | Standard / Specification - Aurecon Civil Spec Section 17.13.5
1cd856c6-f750-5b18-a059-93049a8ed452 | note | Verifying Document - Site Record
2fac5181-acf0-57ba-b625-13a4d0d8672a | note | Frequency - Daily
69db99de-4638-53fe-99bf-b4a5cb5f4e8a | note | Verification Activity: Activity - R
9849c5af-a222-52aa-bac6-f9d48347e9c0 | note | Verification Activity: By - SE
89ca5935-9df6-4b6a-83c0-313c4a7c8d7a | checkpoint | 5.01.06 - Trench Subgrade
045a70b3-71d5-5287-b9e6-1d9ecd5a009d | note | Acceptance / Conformance Criteria - Trench subgrade to be inspected to assess if suitable for pipe laying or construction to proceed. Advise Engineer if unsuitable
040755ef-c1a0-5c4a-a018-520ed2ae7428 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.9
31180b77-512b-51cb-b23d-5f2c07b62905 | note | Verifying Document - QA Checksheet
973ed82b-de82-5f5a-954f-2255a59abbd6 | note | Frequency - Prior to pipe laying
552ba684-0153-5b26-a150-96e9121023c2 | note | Verification Activity: Activity - I
a5e69fa0-b3a2-577b-a9aa-bd02a31b1c94 | note | Verification Activity: By - SE
b014b3a8-e695-4f36-90b8-a1a4ee48c3d0 | checkpoint | 5.02.01 - Line and Level
1dc26ab6-a3fd-5455-8d0a-2e116f3feb33 | note | Acceptance / Conformance Criteria - Pipes laid to line +/‐25mm, grade and invert level shown on drawings. Lateral tolerance +/‐25mm from centreline between manholes or change in grade.
bab9ffc4-45ce-53ac-9d04-4cf32bb9532f | note | ○ Engineer notified prior to pipe laying.
3ea82a8d-8547-5028-b673-da7ff2fa58fd | note | ○ No pipe laying shall be carried out without Engineer being notified 24 hours prior
26db5922-2ff0-518b-83a4-ac59cb83f6c8 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
42c6fb70-72aa-5cff-8a2f-3377e7ef102a | note | Verifying Document - QA Checksheet
cf15610b-6709-56bd-8349-680cd7f3e761 | note | Frequency - Before Backfill
c2065efc-7a74-5eb8-928d-f9a1bf197541 | note | Verification Activity: Activity - HP
cd506cb8-369d-538d-a2cc-c27971e5e235 | note | Verification Activity: By - DES
d55230cb-87fc-47e6-a50d-3a73a887e4df | signoff | AUTHORITY HOLDPOINT
5e31d25d-ad2b-4c81-a38d-b41c1f84f1a8 | checkpoint | 5.02.02 - Cleanliness
0af505bb-9062-5fcf-821c-26439672b306 | note | Acceptance / Conformance Criteria - Internal pipe walls shall be kept clean and free of all dirt, rubbish and water. Spigots, sockets, rubber rings, etc. shall be thoroughly cleaned before jointing.
78d5aea9-466e-5f0d-a183-2076429b8ac6 | note | ○ Pipe condition inspected prior to laying and line checked prior to backfilling
8cda70bb-97fc-54db-8fc5-858a07049eac | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
d0e5cbca-1d5f-5644-a551-010c0a583b7b | note | Verifying Document - QA Checksheet
3f6c573c-8dcc-58ee-861a-884d28cea776 | note | Frequency - Before Backfill
47625cff-e74d-5e8f-a2c1-5a53769a4b4c | note | Verification Activity: Activity - I
02e1e9a2-a583-5c28-b078-8ff18d52c72f | note | Verification Activity: By - SE
046e59e8-5098-48d7-9b9f-f2b2e560e0de | checkpoint | 5.02.03 - Bedding and Haunching
0e03011d-35c8-55b1-a15b-e5013c4064f5 | note | Acceptance / Conformance Criteria - AP<12 granular bedding material.
6618dfb2-3482-5ed7-8258-cedfd360ea1d | note | ○ Any sand used must be clean and well‐graded
7e475510-b6e6-57a2-8ca4-ceb444d44b49 | note | ○ Bedding and Haunching ‐ Clegg Hammer test minimum CIV of 12.
9d5c5a5a-b214-5b1c-8300-643623b45267 | note | ○ Results to be attached to checklist with photos.
5a6ce6de-cbee-5660-82b7-99dfc8a78011 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
376eb8ad-6cac-55f1-b695-99daab7e05c0 | note | Verifying Document - QA Checksheet
81db3dc3-e702-50f6-b52e-90ae10f9e12b | note | Frequency - Every 10m
108ad5b7-4411-5c64-9af4-4f6c3a252c0c | note | Verification Activity: Activity - I
7b6b7c6a-d6cd-5b12-ab9d-683a8a86316e | note | Verification Activity: By - SE
59cfeed2-39e8-417d-9875-047bf9ef91be | checkpoint | 5.02.04 - Backfill Placement
31cff7bd-ce3c-5d2a-98f7-300be39ccfa3 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
859bb964-f286-5354-8b79-953ac6b7b317 | note | ○ Clegg Hammer test minimum CIV of 25.
bf6beecb-8536-5fc1-9593-ca8b2a7cf2c8 | note | ○ Results and photos to be attached to checklist with photos.
f82a8456-66a6-5a5c-b098-f0414837cf81 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
a87877e6-3a4f-58e5-8ca5-579b593d536d | note | Verifying Document - QA Checksheet
9f6d7840-3e3c-5c3e-b04e-3e7b7697a536 | note | Frequency - Every 10m, in 1m lifts
c7fa6895-b54e-5487-b72d-73aa626da828 | note | Verification Activity: Activity - I
313ab56a-1c6b-5fee-aa8e-7f13da98b7d6 | note | Verification Activity: By - SE
556adb63-ec3d-44e1-a072-47b950b882e5 | checkpoint | 5.03.01 - Alignment
2a5507d3-41b5-51b8-815c-939aa47e5f26 | note | Acceptance / Conformance Criteria - Structures shall be positioned within 50mm horizontally of the location specified. All structures shall be watertight.
49ac3cb9-39f3-5e13-935c-97f134f6cf65 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2fe2fa2e-8943-5a1e-8d39-51e02b34df88 | note | Verifying Document - Survey
d7353356-07b5-54ce-8b57-50bfe29a6e1b | note | Frequency - Each Manhole / Sump
74294371-5786-5745-9d73-973c301e8a47 | note | Verification Activity: Activity - C
e9d2e9ca-bdd0-5e6a-b104-7de62da52ae6 | note | Verification Activity: By - SV
eac41a61-564e-40df-a0ea-ef7181a260b8 | checkpoint | 5.03.03 - Drainage Structure Bedding
4b498e0e-de7a-54d8-8d7f-a76b8497ee04 | note | Acceptance / Conformance Criteria - Unless specified otherwise, all catchpits, manholes and other stormwater structures shall be founded on a minimum 150 mm bedding.
4db72a30-e2e5-57b7-b66c-76776888b6b8 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ac1a6220-36a3-522e-84d4-94618443f944 | note | Verifying Document - Site Records
9033a582-6abe-5407-b070-f17ffb48a613 | note | Frequency - Each Structure
23d9e508-9f50-53d3-b76e-81a7c148f583 | note | Verification Activity: Activity - R
4934ccd7-bd99-5921-8a57-22c572bdf8ad | note | Verification Activity: By - SE
03b960bc-b12f-4950-b50e-d4db8496a770 | checkpoint | 5.03.04 - Structure Backfill Testing
0b165c62-5756-5fdd-adf3-2e8134ae5072 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
7eb5fa30-0f81-59d1-917b-ed5246af465b | note | ○ Clegg Hammer test minimum CIV of 25.
1a7d9ceb-aa73-5e38-8f37-7494e8003176 | note | ○ Results and photos to be attached to checklist with photos.
a962c154-f6d6-534b-9b7d-c8ea96fb372a | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ffdde332-faf8-5fa5-955f-2be833774552 | note | Verifying Document - QA Checksheet
1b7f3a69-5b6a-52d6-9718-06a9783e4e45 | note | Frequency - One test every two layers per manhole
79a72f65-0b70-5915-871c-3777d3742d5c | note | Verification Activity: Activity - I
66926283-1cc5-5eaa-be19-58d5c86805b8 | note | Verification Activity: By - PE
2c9922e0-de78-4e14-8353-3209a20a8525 | checkpoint | 5.03.05 - Pipe Penetrations
83b73fc2-341d-58cf-b1ee-bcfa8ce2f6bf | note | Acceptance / Conformance Criteria - Pipe penetrations shall be formed by drilling holes around the line of cut before knocking the section out.
2beea6a6-ff8f-5576-8b40-234266f13fb3 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ecae186e-1d05-50b8-955b-3594be52ac23 | note | Verifying Document - Photo
53200386-00de-5655-8178-677dd359fcd2 | note | Frequency - Each Structure
41efd525-3470-5d13-8f14-e3576d1e8f45 | note | Verification Activity: Activity - I
29bbe744-ff00-5809-8d73-b167c394b396 | note | Verification Activity: By - SE
0eddba25-2fe6-41d3-be93-96000b567d92 | checkpoint | 5.03.06 - Benching
eaf9f5d3-a6c5-5d92-8855-f67ecb80ff03 | note | Acceptance / Conformance Criteria - The concrete shall be rendered to a smooth finish and shall slope towards the channel. Particular care shall be taken to create smooth transitions at bends and junctions. Benching is to be in accordance with the drawings.
7f3b5d67-b357-52c5-8753-8da01e36fafd | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2adc6455-2808-541b-b0d1-b986691e25dc | note | Verifying Document - Photo
b2ac9386-30e7-5dd4-a84d-cc6ae1997cec | note | Frequency - Each Structure
95477da3-238e-51aa-add5-33e48d8c1ae9 | note | Verification Activity: Activity - I
38b41d58-202b-5267-8310-293674658199 | note | Verification Activity: By - SE
5aede6b2-5baf-4f6b-b59d-3aeb04c8aa63 | checkpoint | 5.03.07 - Corbels
1b629889-2871-5781-9f4d-dddbcbaba577 | note | Acceptance / Conformance Criteria - Pipes shall be haunched and surrounded with concrete to a minimum distance of 200mm from the outside of the manhole in accordance with the drawings.
859eb528-5317-5bdd-aab8-70e7d22ccc74 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
e23c89f6-06b4-5a66-8467-7639c84b79d8 | note | Verifying Document - Photo
d8a7d9df-3370-516b-9aa8-d3162a6b57bb | note | Frequency - Each Pipe Entry
69b1725a-de06-5132-9d7e-aae25ff4b67f | note | Verification Activity: Activity - I
33423871-d2c8-5027-b60a-52d3a1813216 | note | Verification Activity: By - SE
37427201-020e-4f11-a046-9227ab94f4f1 | checkpoint | 5.03.08 - Pipe ends
311454d8-7750-5305-bfa0-62161cf191b0 | note | Acceptance / Conformance Criteria - Pipe ends shall finish approximately 50mm beyond the inside wall and be plastered with cement mortar or encased in benching concrete in accordance with the drawings.
29347e21-4363-5305-ba64-93dc74f0fc52 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
3ab18a1e-6d14-5f42-a592-00c340041c51 | note | Verifying Document - Photo
20660926-01af-5155-a4a1-d5b33f753b57 | note | Frequency - Each Pipe Entry
00572355-483f-5c33-8ca3-27da9b3d4a98 | note | Verification Activity: Activity - I
1aa6d669-cf88-55fd-8da4-15ecba24dfcb | note | Verification Activity: By - SE
028d0e8f-10d6-4127-b82f-dd68ba26687e | checkpoint | 5.04.01 - Pipeline Testing
c9c20f4b-5d5c-5920-ad5e-e43b398641d7 | note | Acceptance / Conformance Criteria - Pressure test wastewater and stormwater pipes; PVC, steel, GRP, ductile iron and PE pipelines, rising mains and connections for water tightness.
91c966f2-5075-5998-ac40-f400b6658114 | note | ○ As‐built location of all manholes, surface level of manhole lids, depth to invert of outlet pipes, junction locations relative to downstream manholes
4bcd055f-a961-57fe-bb46-e4291484cb8e | note | ○ The Test must be witnessed by the Engineer or their representative. A record of all tests shall be made and forwarded to the Engineer within 24 hours of test completion.
d621b457-ce52-5ff9-920e-36f0e7c02b1d | note | Standard / Specification - Aurecon Civil Spec Section 17.12.22 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
321a7d50-135d-5862-bc12-94d5d44d1a02 | note | Verifying Document - Test Report
31a8e963-b89f-5957-b157-a88f7d6d4f62 | note | Frequency - Each Pipeline
669bbe73-8c21-5e90-8042-7f3d8181bc33 | note | Verification Activity: Activity - HP
b3b3e6aa-7e64-5d56-b7ba-c40a9dc0a534 | note | Verification Activity: By - ENG
601600f2-7244-4a09-93df-b7ca16ba4d87 | signoff | AUTHORITY HOLDPOINT
2666c36a-10f2-464a-9c34-135ae2cbdccd | checkpoint | 5.04.03 - CCTV Inspection
1b3fecfc-5de0-529b-b0d9-75eb6eef726d | note | Acceptance / Conformance Criteria - Lines fully flushed immediately prior to CCTV inspection.
8a253ffa-1890-5286-88d5-6988f6dae2b7 | note | ○ Inspect pipelines for correct line and grade between manholes. Pipes to be checked for visible infiltration and debris. CCTV submitted and reviewed by Engineer.
90689c79-3a91-5e81-9584-d79d797e00fd | note | Standard / Specification - Aurecon Civil Spec Section 17.12.23 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2daa0de8-d726-5248-aba6-9bc43aecc181 | note | Verifying Document - CCTV Logsheet and Video
5f6d054c-e05a-5c0c-84f3-08441032f183 | note | Frequency - Each Pipeline
dbf10a59-2fc2-57b2-9172-c5ce43d61a3d | note | Verification Activity: Activity - HP
412477e5-c12d-57b9-b106-5e308f36fd52 | note | Verification Activity: By - ENG
e04848e4-2203-40f3-a22c-67c350706bb7 | signoff | AUTHORITY HOLDPOINT
2810c580-f74e-4b0c-85ce-c90fbd2f4943 | checkpoint | 5.04.04 - Manhole Testing
8ecf99e3-5f32-5fec-aa61-267e0b0bcaf1 | note | Acceptance / Conformance Criteria - Manholes and pipelines shall be checked for infiltration. Visible leakage in manholes and pipelines shall be rectified prior to acceptance.
02cc5bb6-a588-54bf-a86a-e710a85b8c0f | note | ○ Stormwater Manholes shall be free of visible faults or permeable zones and jointing or penetration repairs shall be to best trade standards
39b73db0-83a0-5c5b-988a-37efa896a833 | note | Standard / Specification - Aurecon Civil Spec Section 17.12.22 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2b418a15-749f-59de-9ef5-d102ecb8af8e | note | Verifying Document - Test Report
9ad4f95d-15c0-5e6d-8f08-8f30d38e3576 | note | Frequency - Each Pipeline
affac232-4189-51dd-aa94-d531cef68068 | note | Verification Activity: Activity - HP
c52cc343-043f-5fb5-939a-8f2d5baf385c | note | Verification Activity: By - ENG
6786d93f-3dd0-4a03-853e-ab7f662202fb | signoff | AUTHORITY HOLDPOINT
6eff4f33-dac8-46f2-a493-858539323533 | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
dc05f96a-a9fe-4d5d-82dd-a10d3cdd1d5e | checkpoint | 6.01.01 - Construction Record Compilation
05fbf73c-b0c6-56dd-80b6-5af9fd47d612 | note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
19053b39-aed1-5dac-aff5-6291198d3e79 | note | Standard / Specification - Downer
da20a950-2ef9-5833-8b40-b8a1794cbe3e | note | Verifying Document - Records
b52aceb2-c1bb-59fa-b386-46d3beda53c4 | note | Frequency - Post construction
ef181242-248a-5bcf-ba38-f1b93c6b1026 | note | Verification Activity: Activity - H
1fc31b8b-de60-56c5-a91b-27c074c62c12 | note | Verification Activity: By - SE
2a0db845-2476-4923-a971-74ef5157458b | checkpoint | 6.01.02 - Survey Records
da632324-26f1-582a-8fa3-fa3c6969a5a0 | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
98c2e71c-7c50-594e-aa1c-ff53238a0954 | note | Standard / Specification - Downer
598a8fd3-ffb2-55b6-b661-8f347a1ef381 | note | Verifying Document - Records
f27f5dbe-c222-55cc-8ee6-1a1a8ccca456 | note | Frequency - Post construction
5cbc269f-c871-5c8d-9585-13da86cbdfc3 | note | Verification Activity: Activity - H
5fd576f4-8fa0-5d10-b66a-2176e126a5dc | note | Verification Activity: By - SV
7c69b0d0-63c3-4a9a-aa46-c306afd7ce16 | checkpoint | 6.01.03 - Redline Drawings
c8c39aed-40ea-5a9b-8ba4-634a45caf263 | note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
a0f9ef5b-e757-5ec2-ad2e-41496c8a59da | note | Standard / Specification - Downer
d78c191f-c650-541d-8a9c-537abc151cf4 | note | Verifying Document - Redlines
ecf17b12-8c1c-52a3-93fe-311df23fa837 | note | Frequency - Post construction
6a2301fa-118d-5b70-b9eb-b2e594de4d33 | note | Verification Activity: Activity - H
68d587cc-b4d6-5a4b-a78e-6a48f93b8c2f | note | Verification Activity: By - PE
bce5c348-70ed-4be4-9eb8-50372ce6715f | checkpoint | 6.01.04 - Defect, Snag and Punch List
664c81e5-ec5c-5003-9536-cd943d060457 | note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
2c9185e0-efa9-5b1c-a558-e32bf0bf5f85 | note | Standard / Specification - Downer
d5793ac7-8cd3-530d-be9a-13f47f79a130 | note | Verifying Document - Register
8fe34fcd-9c07-5651-b70d-7ec7a6e35d33 | note | Frequency - Post construction
134e9368-dd0b-5bc8-a979-a689163e74fd | note | Verification Activity: Activity - H
a379b82b-f9e6-546f-ae9a-fa068099c087 | note | Verification Activity: By - PE
2a108de0-5d9c-405e-9e6c-1391f1b63163 | checklist | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet | itp | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet
d01bb0fa-981b-4257-b668-0f306a57ced6 | section | Materials
6375d497-c66c-411e-8e65-c821b8b7516d | checkpoint | Materials available and comply with specs (all materials)
dfc8a7fb-9923-5c27-ab86-aa4f27b84d37 | note | Comments - Sent to design engineer for review
f6ee3ef9-4655-4f4c-bcb1-e4cedf653d21 | section | Excavation
0b2aaef9-f488-4320-87f8-d16be8f71521 | checkpoint | Has the permit to excavate been completed
750d7c78-b56c-5cb2-bb08-c5151c3d8e64 | note | Comments - Services clearly identified (Both KR and DNZ)
a6249c29-bb87-56cd-91d7-a48b6f7b4d2d | note | ○ NUO standover on site if required
d8cf0920-849b-480e-a28a-bf2ab731bd04 | checkpoint | Set out complete
930f5fc4-91b2-5173-a32d-64345a7d446d | note | Comments - As per IFC Civil Drawings
17db364a-cf29-4213-ae66-a65ce559eecf | checkpoint | Protection of existing pipelines / utilities
ee79636b-9caf-4166-b768-2003fcef790e | checkpoint | Trench excavation to line, level and grade
512a44a1-88a9-5741-9f63-a507ff58d3ef | note | Comments - Every 10m
2b2fba20-fd9c-59ba-afa1-b1a91256db76 | note | ○ To lines, levels, gradient as shown on drawings
7df5fb38-572f-5308-95ab-c719b6df0de7 | note | ○ Sufficient width to permit installation, pipes minimum 100mm from trench wall
baa05405-c473-587e-96c1-0f64f1998c9d | note | ○ Width ,<600mm greater than pipe diameter
e5eb6bee-37c3-4fa7-b723-fd04ed8cacf9 | checkpoint | Trench excavation open length
33bda56c-2426-5500-b59c-bc83f26e5e24 | note | Comments - Not to exceed manhole length or 30m
3937519b-92a6-4ac0-a3cd-3433a30edbef | checkpoint | Materials removed and stock piled
99d6f212-7bdd-49d3-830e-175cac2ad942 | checkpoint | Bottom of trench foundation condition
f519ec45-2b30-524b-9b68-a830e6114c9f | note | Comments - Water ingress kept below bedding level
ea4cb0fe-ca55-576d-8ade-ebc14a5ab7fa | note | ○ Subgrade suitable for pipe laying
c8031554-cb2f-4a91-a18c-38150db3c5b7 | checkpoint | Over excavation required?
ded950d0-d587-5819-859c-1277ed1a653e | note | Comments - Engineer to be notified and approval received prior to undercut.
a0666b6e-f2f0-491e-bc07-8b9486f6c50f | signoff | HOLD POINT
ba394402-0b3b-4be8-9340-f1f9fd577a76 | section | Pipe Installation
a5f16f4e-ea65-4c6c-a76b-23bc4488bf77 | checkpoint | Hold point
aacd42fe-5b5e-5540-b8ca-2456368f2aaf | note | Comments - Engineer to be notified 24hrs prior to pipe laying
51add03e-2fcc-42ee-942b-162ce3bcfcac | signoff | HOLD POINT
65dd0300-17c3-4d8f-8f2b-278ff1bf8536 | checkpoint | Pipes transported to site , stored and lifted correctly to prevent damage
67eec2f8-b35f-465d-94a7-b04f9409d473 | checkpoint | Trench shield/Benched/battered
78ef0102-6181-5c8e-a32f-eafebfb34949 | note | Comments - If the trench is deeper than 1.5m
ff0fad76-9676-42eb-b206-45b8cfac80f3 | checkpoint | Line and level
5fe3b340-7fda-5832-96d1-b61bd7280c20 | note | Comments -
f06b8532-63b4-5735-8061-8b03398cc5f0 | textbox | Design:
e0b070e2-0f92-558e-a6d2-7510a13edaec | textbox | Achieved:
89e23c3e-aa4b-4d5b-b6c5-76b82ab003bc | checkpoint | Cleanliness and condition
79980bda-084a-5b83-99b1-6440a99602aa | note | Comments - Internal pipe and joints clean and free of dirt/debris
b7c9b724-65cc-5179-bb1a-e22f9c1312c5 | note | ○ Pipe condition inspected prior to backfilling
a91200ca-46c1-4c73-a4b7-0717a9b850a9 | checkpoint | Bedding and Haunching
370a2d05-8021-5929-a27c-b05ff0fd7fdb | note | Comments - AP<12 granular bedding material
9ee42627-75d2-5549-a1b6-262140f60db6 | note | ○ Clegg hammer tests (every 10m, min CIV 12)
316fcf5e-34e6-5ced-8047-7d2358042d97 | note | ○ Clegg Results:
84c6155d-2fc0-4699-8b47-4d0804851837 | checkpoint | Temporary capping of end of pipes
c4ebc408-9d1d-4018-afc7-14aa947b6edb | checkpoint | Backfill Placement
008a00f8-0ff1-5c52-a338-b35d96e96f3e | note | Comments - AP>40 granular bedding material
6288a32c-3e7d-523a-b0ba-d38a38a19780 | note | ○ Clegg hammer tests (every 10m, min CIV 25)
91d3d9aa-9de7-55fc-b183-e5c2df6731f9 | note | ○ Compacted in 200mm layers
a72828a9-2355-5256-8dde-0a4d7e9da188 | textbox | Clegg Results:
71395699-e98e-4c69-aa04-981879084797 | section | Manhole Installation
e92be3b1-1d0f-4238-8b40-153b93563954 | checkpoint | Alignment
32ae0601-296b-510e-9fb8-2e91758f7cb8 | note | Comments - Correct position (<50mm)
495de50c-8582-5a2b-a913-7c00c3b82bf5 | note | ○ Vertical
b43608b4-ee23-47ff-b835-b6204482687e | checkpoint | Bedding
4c8de7d6-de0e-5e9e-9b92-108286954e9b | note | Comments - Bedding material – min 150mm
3b0086bb-6939-5ef4-939b-ba1eda95e5e9 | note | ○ Clegg hammer tests (min CIV 12)
80bfd47f-05ed-5264-82b7-477b14419e81 | textbox | Clegg Results:
c8a5e9a8-cc24-4372-b29b-9167c21c5496 | checkpoint | Backfill Placement
df912de1-e683-5890-86d2-53a5cb241474 | note | Comments - AP>40 granular bedding material
7f8874d1-dd27-570f-8e4a-6f88e16b89a4 | note | ○ Clegg hammer tests (min CIV 25)
895ce9b5-c603-51da-94c3-38a48789aea1 | note | ○ Compacted in 200mm layers
726aabc2-a1e4-5d4a-94bc-059d0499bdec | textbox | Clegg Results:
5b273b34-232e-46fa-a213-21ea23e7f3e0 | checkpoint | Penetrations
a974ae65-477e-531f-8343-5c3388ae2d75 | note | Comments - Formed by cutting or drilling prior to knocking section out
81a53eb7-2d6d-46fa-9816-835dfee8e2ee | checkpoint | Pipe Ends
26aa13a1-4872-5b92-a366-2efac5679c24 | note | Comments - Finished approx. 50mm beyond inside wall
f83d50ae-c99d-5c09-9a8d-238b788841a1 | note | ○ Plastered with cement mortar or encased in benching concrete
47d8195e-e8da-4630-8ec7-58d0147515b6 | checkpoint | Corbels
7354aa82-1834-5050-88d2-369a4606c285 | note | Comments - Pipes haunched and surrounded by concrete by >200mm from manhole
b8a83028-f4c4-4cdf-9942-7ba34e706d68 | checkpoint | Benching
210fcd71-94fd-51a3-834f-5816bd719a9a | note | Comments - Smooth finish, graded to channel, in accordance with drawings
b272941b-fe4c-4a30-b891-b42dc5e6353e | checkpoint | Works completed as per design requirements and work area is ready to be handed over for sign-off
12d4a07d-7860-45c0-8701-8b6e8747b438 | signoff | Signed by Sub contractor Representative
645d8739-1e43-4519-9a72-77d5102eed3f | checkpoint | Final Approvals
f0fae84f-1101-57e3-9a4d-2af8502b247d | textbox | DNZ Check - Name:
a7496307-ebff-5601-932a-0c785cf07fa3 | date | DNZ Check - Date:
eaba1159-b424-5fdb-9f05-e1dbb65424bb | textbox | Engineer / Consultant - Name:
60f0f80b-2b22-5876-b492-fe8a7412ff73 | date | Engineer / Consultant - Date:
8e383c3e-00df-4eb5-a377-bb108e0aa8dd | signoff | Sign-Off
5f433e59-776e-4e8a-bf0e-cb809e243ac2 | checklist | Documents & Photos |  | Documents & Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dd77a1e6-4546-407a-bdc7-2fb24ca37b74 | checkpoint | Please upload the relevant document(s) / photos and press PASS.