## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
4bd53acd-6405-4e3e-a599-dc5d4aa54a1a | checklist | ITP-002 - Feeder Conduits and Pits Rev2 | itp | ITP-002 - Feeder Conduits and Pits
c0fdca6c-9fb3-4ae7-913f-6a4b051a60ac | section | 1 - Preliminary Works
a46884c7-852b-4bc8-8107-83cbce107959 | checkpoint | 1.1 Check for correct documentation
1dd02b6f-cb20-50b0-af91-29c941336207 | note | FREQUENCY: Prior to commencing any activity
74d3e9ed-67fe-5385-abae-33733cce56ae | note | ACCEPTANCE CRITERIA:
cb06cb9c-ec2f-56c7-ac67-68dc8af70f95 | note | • Ensure that all employees and subcontractors are:
7edbdd30-85f5-5bb3-a6ff-93580d65be30 | note | – using the correct and complete set of drawings
ef193c2a-8d93-5c32-8590-d75b06db3c49 | note | – all drawings are the latest revision
930331f8-238c-59e6-b164-afd483b350d6 | note | REFERENCE DOCUMENTS: Drawings and drawing registers
62de1c25-2d66-5785-ab8b-edb723f6c9b6 | note | INSPECTION/TEST METHOD: Visual inspection
3796e4e2-e520-5904-8cbe-3c6218e6ca9a | note | RECORD OF CONFORMITY: This ITP signed off
c9939422-5637-5878-93db-86a8bc3de6e3 | note | HP*
bb638971-8de7-5b83-a139-01a79b71c691 | note | RESPONSIBILITY: Fulton Hogan Engineer
5abb1941-da2c-5861-bb51-10776769e729 | textbox | DATE:
9b0cad6e-a5d1-45a0-b1c4-0af4c94088a4 | checkpoint | 1.2 Implementation of all measures and controls
0c73006f-2171-5f13-8e75-af39e9451324 | note | FREQUENCY: Prior to commencing any activity
db30c66d-9b03-55e2-8fd0-49c81aa634fa | note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
ea979269-855e-5d61-8c31-93defbcadb3c | note | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
ff0a736e-cf31-5f75-84c3-90ef359b193d | note | INSPECTION/TEST METHOD: Visual Inspection
6d4bc889-2df9-52f1-b3df-66d87db0aa9b | note | RECORD OF CONFORMITY: This ITP signed off
50a3cc96-050f-5cd9-bd0d-ada92a712982 | note | HP*
03e3e14d-2f87-5273-91ed-600a1dc081d5 | note | RESPONSIBILITY: Fulton Hogan Engineer
3510f2fe-8b18-5c80-8b30-7f212bd7ed29 | textbox | DATE:
51127dad-de18-408a-b4b8-8c4bd7cead89 | checkpoint | 1.3 Materials
cd71f4d7-f62a-5521-909e-683d75311c6f | note | FREQUENCY: Per Batch
89cbbdc6-5627-5fa3-abb7-de1601ef85a0 | note | ACCEPTANCE CRITERIA:
477fe3bc-18c4-5c50-8a8e-77ecbab99503 | note | • Electrical supply conduit to be Orange
0187fab5-714c-5479-9541-206fb528cfdf | note | • Heavy Duty 100mm diameter UPVC
31a6bd62-579b-5e79-b740-9ef6d5e62d9b | note | • Modula Stakka pits to be used for feeder pit, entry for conduits to be cut with hole saw
e17d7cc9-f5ca-55bb-9df5-8e91e376ff4b | note | • All pit covers to be class D or greater and installed in accordance with manufacturer requirements.
695bf958-fdf2-568a-a789-be08fcfd8844 | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4AS 2053
f76b0ca7-4bf5-5269-b265-69d34d90254a | note | INSPECTION/TEST METHOD: Verify
6c41a7b2-6e51-5498-ba67-cad5a1b5f70c | note | RECORD OF CONFORMITY: This ITP signed
a4ec63bf-b7cf-5bf3-a7ae-33cca2f6165f | note | HP*
dc835441-3994-5f4b-9d73-a8281cf2e1c4 | note | RESPONSIBILITY: Fulton Hogan Engineer
d567f42e-33df-5466-af48-b2c30a899760 | textbox | DATE:
1033c23c-c402-49ae-b26d-ec1c7717fbb5 | section | 2 - Construction Works
5ba0b3f0-ba25-4425-9842-d89ba5ecff7b | checkpoint | 2.1 Survey set-out
f4301acb-d642-58c3-9c91-54e6dda108bf | note | FREQUENCY: As required
c9e86ae9-3028-5f15-91c5-41e83d3d343c | note | ACCEPTANCE CRITERIA:
3a1642b3-eb16-54a4-8bef-8a45a510c6c1 | note | • Work is set out in accordance with drawings.
34f1a8d2-dc7e-58c9-87a8-3f5712644582 | note | • Ensure that pits are placed as shown on drawings and shall align with overhead poles which are suitable for connection with infrastructure from pits
c501af14-d912-57c5-9578-d28bcac86dc4 | note | REFERENCE DOCUMENTS: Work procedure
37426b98-c29d-5140-aaf8-33c6a9350155 | note | INSPECTION/TEST METHOD: Verify
0444e3f3-2ca7-5856-bdfd-0454c0f20988 | note | RECORD OF CONFORMITY: This ITP signed
a8e1d7fc-d755-5fc0-b698-932d2cb53031 | note | HP*
60e27b74-8d7f-50a1-9694-994558cbde7b | note | RESPONSIBILITY: Fulton Hogan Engineer
4a9e3882-895f-517a-b27f-0902b2a0e8bc | textbox | DATE:
e149b514-72a0-41c2-bc41-44211afed155 | checkpoint | 2.2 Excavation and Trenching
d257f2e6-1587-54ce-b5a0-e39009ff8322 | note | FREQUENCY: Prior to Installation
4ca53c3d-c27e-5042-9cb5-a1d5afcdb073 | note | ACCEPTANCE CRITERIA:
65eb0d15-fb8e-518a-a50c-9181451805e3 | note | • Minimum cover for underground conduits shall be 600mm
617eee52-1727-5330-a011-7de41c7b7a95 | note | • Open trenching only permitted in unpaved areas, line of trench to be at right angle to the track
7c9fcdfe-8631-5290-9ac2-4cdf29b46ba0 | note | • Trench shall maintain a minimum clearance of 300mm from all existing services where possible
137dc1b8-5945-5b7f-85a8-c2bfcf127aaf | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5 & 4.2.8
551c3555-25ba-52c0-a31b-a904f3b38f4e | note | INSPECTION/TEST METHOD: Verify
3d12bbcf-bf4e-5aee-8b23-40657afa4424 | note | RECORD OF CONFORMITY: This ITP signed
6df89054-41bc-5053-b592-6943742e5374 | note | WP
9628fea1-0b93-57d6-9347-e9177e8555da | note | RESPONSIBILITY: Fulton Hogan Engineer
9b6da768-b289-544b-9893-e07ad0d1c3bb | textbox | DATE:
7225e839-da4a-45a2-948a-60d6e7fb480b | checkpoint | 2.3 Installation of Conduits and pits
c832c8ba-8e13-5576-b77e-7d707229268e | note | FREQUENCY: Each Lot
c099495d-eafe-56ac-8c2f-54a3d87f2750 | note | ACCEPTANCE CRITERIA:
8bbddfbc-3ff5-5233-93c7-ddab287bdaab | note | • Conduits in the same run shall be spaced 50mm by using clean sand to pack voids
1dda2e31-5566-53b8-b178-5c4c90ba0066 | note | ○ Conduit shall be embedded in not less than 50mm sand and covered by >50mm - 75mm< sand
b77f9ef5-236e-5f41-b82a-107c9789d2df | note | • Mechanical protection shall be provided by installation of polymeric cable or cover strip of thickness not less than 3mm, and of a material equivalent of UPVC conduit complying to AS 2053. Protective material shall be placed not less than 100mm above the conduit, and shall not be less than 150mm wide.
25cb1706-cb3c-5884-826d-79b4c50b6512 | note | • Conduits shall be joined male to female ends and sealed with approved adhesive immediately prior to joining.
63a37aaf-930b-52fd-9b3f-71e527be293f | note | • Conduits shall not be subject to construction loadings
44ac61d9-f53d-58e7-bfcc-cf22ed64914e | note | • Pits shall be constructed as to allow for class D rated covers
d7ca8d42-7294-50a1-bec9-a00e641e6864 | note | • Bottom of lowest conduit shall maintain a minimum 100mm above pit floor, a 50mm gap between conduits shall be maintained as they enter pit face.
86a38c3b-55b5-5563-a9b5-85eb1a3ca008 | note | • Conduits exiting the pit as 'stub ends' shall extend a minimum of 50mmbeyond the pit face and shall be fitted with a spigot end and capped with UPVC electrical caps to prevent contamination to internal surface.
1693d599-26a2-5db9-bcea-e91a55976d89 | note | • Conduits shal be placed a minimum of 100mm above pit floor
4a76aea0-ab91-5d46-97d4-b73b3d27525d | note | • Conduits installed for future connections shall be installed to the track Margin
6de82dee-719c-50e1-adff-3adc0e3a5481 | note | • 100mm of concrete around and under pit lid
f6c9a846-0382-5487-84d3-383deda05fa8 | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4
73ca6c71-6ee6-5294-9efa-9ecd1ef6bd36 | note | INSPECTION/TEST METHOD: Visual inspection
b15e974f-0393-5c44-a5a9-c666a7888569 | note | RECORD OF CONFORMITY: This ITP signed
aacf2caa-b99c-581d-8649-036b5c2f9696 | note | WP
342950e6-b2ad-50ad-81a3-93406401b868 | note | RESPONSIBILITY: Fulton Hogan Engineer/YT
50280934-0bb4-5a28-bae4-e322d738a3ee | textbox | DATE:
037ee90b-47cd-42e5-b832-d64d6cf4d41b | checkpoint | 2.4 Inspection of conduit installation
680d57be-c1a2-5bee-bc0d-b26d7dea7497 | note | FREQUENCY: Each Lot
4ab9713a-916a-5125-b601-5df2b9f9db40 | note | ACCEPTANCE CRITERIA: Laying of conduits and installation of pits shall be inspection by superintendent and conform to design drawings before any backfilling procedure is to commence
50502878-4ef2-51e2-86aa-35a7391036bc | note | REFERENCE DOCUMENTS: Work procedure
77266c6f-dbf5-53db-8d4f-02ade1712c3e | note | INSPECTION/TEST METHOD: Visual Inspection
6a65f469-134c-52c1-9015-f83457acf783 | note | RECORD OF CONFORMITY: This ITP Signed
f9e33d29-3934-5a49-8280-75a3730388fc | note | HP*
44ea229e-2696-590a-8891-6c3ec09cf3e1 | note | RESPONSIBILITY: Fulton Hogan Engineer/YT
e58453ef-ea0a-56a5-82e5-d0d577fd9df4 | textbox | DATE:
0460ee88-5f82-4f99-8d42-74966ffdabe9 | checkpoint | 2.5 Back Fill of Trenches
38e9b78a-16b7-5fde-af32-b7769317baad | note | FREQUENCY: Each Lot
884f29c0-fcad-5d0b-9059-07402f3ad160 | note | ACCEPTANCE CRITERIA:
6ff2836d-94f8-52fb-8f48-92a0277edb60 | note | • Backfilling (Only to be used for road crossing trenches)
05b9fd81-93a7-5f3b-9473-b7510d25335c | note | – conduit trench shall be backfilled above marker tape with crushed rock or suitable excavated material and compacted to 90% standard compaction 150mm-200mm below sub base level, the last 150mm-200mm shall be compacted to 100% standard compaction
cb73b548-e6f7-5136-9398-1cd7b2baa95f | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5
b2852812-e46c-58d7-bc73-e4fb38df8f1f | note | INSPECTION/TEST METHOD: Verify
16e3ab25-2e01-53a0-ac5c-89c16803e07c | note | RECORD OF CONFORMITY: This ITP signed
9e89c5b6-a8fc-5ba9-a9d7-ba483bb284ea | note | WP
c3c2a196-db26-574b-9c63-29c835e28373 | note | RESPONSIBILITY: Fulton Hogan Engineer
fa22bae2-4241-5ca1-aad0-5315d4ef74da | textbox | DATE:
7c08edda-a5ad-4374-8060-88d932440622 | checkpoint | 2.6 Installation of Draw Cords
c267afaa-f569-5831-b99c-9af873e02a53 | note | FREQUENCY: Each Lot
14ae882d-8c13-517a-abf4-9d30b6d45ae9 | note | ACCEPTANCE CRITERIA: Draw wire shall be provided for each conduit, with extra 3m length at each pit. Material shall be 6mm 'telstra rope'
207eecf7-9b02-50bc-82f9-f09b75523e68 | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.6.2
44b04b8f-37b1-5cf7-9709-4e339847763b | note | INSPECTION/TEST METHOD: Verify
01a3ef3d-2436-5787-ac79-7c0574dcdc79 | note | RECORD OF CONFORMITY: This ITP signed
4ca78694-0202-5ed5-a302-b5be118da294 | note | WP
0259af1f-8864-555e-b3a6-f5844ebef30e | note | RESPONSIBILITY: Fulton Hogan Engineer
4d65725d-06e0-5a21-9c13-792fcc4ff712 | textbox | DATE:
5d7709fb-6c38-465e-848f-7c16d40450d5 | checkpoint | 2.7 Compaction
d7d9a326-831e-5775-b3da-348c1bffcae0 | note | FREQUENCY: Each Lot
9807efd3-112e-593f-b589-1dff7bb37bb2 | note | ACCEPTANCE CRITERIA: Bedding and backfill material to be compacted using mechanical plant During compaction optimum moisture content of bedding and select fill is within 85% to 115%
c34562e0-142d-5685-a626-26cc94b2c679 | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.8
aee163b4-25cc-5e10-b899-03b7c19b3c93 | note | INSPECTION/TEST METHOD: Verify
0d3c485b-a2a1-54f3-84df-3308a9f41e1e | note | RECORD OF CONFORMITY: This ITP signed
2162a43f-01ce-5819-861f-91f4860501a9 | note | IP
898fb964-89ac-50e9-abb3-f20b564b9095 | note | RESPONSIBILITY: Fulton Hogan Engineer
3eaea696-d67b-5800-82ff-271f3f19d4a6 | textbox | DATE:
81757977-3546-4c59-9538-3d82d7ecce0b | checkpoint | 2.8 Feeder Pits & Pit Lids
c50215c1-1617-561d-bb94-f0fd734cde58 | note | FREQUENCY: Each Lot
43ef3cfd-e862-5fbe-b64d-e4e707668cac | note | ACCEPTANCE CRITERIA:
71c052cd-dd63-5c3a-80cb-1054046c039f | note | • Feeder Pits constructed and installed as per drawings
7b82e055-38aa-5ef6-be3a-fb7831423ff8 | note | • All conduit connections to cable pits shall be neatly made and ends of conduit trimmed off and the area between the conduit and pit wall stopped with cement mortar
222acd19-d724-5a6d-aa9e-6d288a7e831b | note | • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
ca0a7b13-836d-5154-ab69-03806ad53bbb | note | • Gatic pit lids shall be filled with structural grade concrete
f82b7bf3-9e96-5151-b848-2e2cce6ad230 | note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.7
0cd1206e-f5b9-5de5-a0fa-7f4eb70a1b28 | note | INSPECTION/TEST METHOD: Verify
0c6f21e3-2390-5f81-9378-5a8f9999ae3f | note | RECORD OF CONFORMITY: This ITP signed
b0fdb187-67b6-59c7-9072-db596abf1337 | note | WP
89ae9fbd-0fc5-5489-b2a4-1c3553c6b966 | note | RESPONSIBILITY: Fulton Hogan Engineer
79ade2eb-391a-5102-8175-d1d419475791 | textbox | DATE:
78da752a-3eb2-409b-ad7c-09e0da86c9fe | checkpoint | Final Inspection
4889b1e6-cdf7-5283-836b-dff8808bd0b4 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
4adbe82e-a0db-58fb-8417-21fd7ca999a6 | textbox | Print Name:
a6714e63-3953-5b7b-9188-a6f235fc564a | textbox | Position:
81671e29-e7a6-5830-b391-36e62c60ca03 | textbox | Date: