## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Rough In (BUILDING-A)
| Scope |  |  | Rough In | BUILDING-A
Rows
|  | Level-2 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-2 | Apartment Wall Closure
|  | Level-2 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-2 | Apartment Ceiling Closure
|  | Level-3 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-3 | Apartment Wall Closure
|  | Level-3 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-3 | Apartment Ceiling Closure
|  | Level-4 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-4 | Apartment Wall Closure
|  | Level-4 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-4 | Apartment Ceiling Closure
|  | Level-5 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-5 | Apartment Wall Closure
|  | Level-5 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-5 | Apartment Ceiling Closure
|  | Level-6 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-6 | Apartment Wall Closure
|  | Level-6 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-6 | Apartment Ceiling Closure
|  | Level-7 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-7 | Apartment Wall Closure
|  | Level-7 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-7 | Apartment Ceiling Closure
|  | Level-8 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-8 | Apartment Wall Closure
|  | Level-8 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-8 | Apartment Ceiling Closure
|  | Level-9 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-9 | Apartment Wall Closure
|  | Level-9 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-9 | Apartment Ceiling Closure
|  | Level-10 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-10 | Apartment Wall Closure
|  | Level-10 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-10 | Apartment Ceiling Closure
|  | Level-11 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-11 | Apartment Wall Closure
|  | Level-11 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-11 | Apartment Ceiling Closure
|  | Level-12 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-12 | Apartment Wall Closure
|  | Level-12 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-12 | Apartment Ceiling Closure
|  | Level-13 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-13 | Apartment Wall Closure
|  | Level-13 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-13 | Apartment Ceiling Closure
|  | Level-14 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-14 | Apartment Wall Closure
|  | Level-14 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-14 | Apartment Ceiling Closure
|  | Level-15 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-15 | Apartment Wall Closure
|  | Level-15 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-15 | Apartment Ceiling Closure
|  | Level-16 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-16 | Apartment Wall Closure
|  | Level-16 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-16 | Apartment Ceiling Closure
|  | Level-17 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-17 | Apartment Wall Closure
|  | Level-17 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-17 | Apartment Ceiling Closure
|  | Level-18 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-18 | Apartment Wall Closure
|  | Level-18 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-18 | Apartment Ceiling Closure
|  | Level-19 (Apartment Wall Closure) | dynamic | Rough In | BUILDING-A | Level-19 | Apartment Wall Closure
|  | Level-19 (Apartment Ceiling Closure) | dynamic | Rough In | BUILDING-A | Level-19 | Apartment Ceiling Closure
Columns
|  | FCU installed in right location as per mechanical layout & the model number is in accordance with latest AC schedule? |  | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule? | Apartment Wall Closure
|  | FCU installed at right height to ensure grille is centred into the bulkhead & 5% slope towards drain point? |  | FCU installed at right height to ensure grille is centred into the bulkhead & 5% slope towards drain point? | Apartment Wall Closure
|  | Thermostat control cabling has been installed? |  | Thermostat control cabling has been installed? | Apartment Wall Closure
|  | Thermostat location is correct as per RCP? |  | Thermostat location is correct as per RCP? | Apartment Wall Closure
|  | Drains have been run to Tundish & does not protrude wall framing? |  | Drains have been run to Tundish and does not protrude wall framing? | Apartment Wall Closure
|  | Drains tested & witnessed by Boad Air? |  | Drains tested and witnessed by Boad Air? | Apartment Wall Closure
|  | All wiring including interconnection wiring & power from isolator to the condensers are roughed without defect? |  | All wiring including interconnection wiring and power from isolator to the condensers are roughed without defect? | Apartment Wall Closure
|  | Refrigeration pipes have been installed & all refnets are sealed & hard to soffit & don’t impede on ceiling height? |  | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height? | Apartment Wall Closure
|  | Refrigeration insulation is not damaged? |  | Refrigeration insulation is not damaged? | Apartment Wall Closure
|  | Refrigeration pipes run through cavity without being kinked or damaged? |  | Refrigeration pipes run through cavity without being kinked or damaged? | Apartment Wall Closure
|  | Pipe projecting the wall cavities in balconies have been sealed? |  | Pipe projecting the wall cavities in balconies have been sealed? | Apartment Wall Closure
|  | Exhaust Vent & Make up Air boxes are installed as per drawings & sealed? |  | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed? | Apartment Wall Closure
|  | Air Conditioning |  | Air Conditioning | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - Inspection Date: | Inspection Date: | Air Conditioning | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - FCUs are installed & other services are not impeding access to fan coil? |  | FCUs are installed and other services are not impeding access to fan coil? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - FCU filter track & filters are installed & nearby service is not impede filter access? |  | FCU filter track and filters are installed and nearby service is not impede filter access? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - Wiring connected to indoor unit electrical box? |  | Wiring connected to indoor unit electrical box? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - Condensate line has 2% fail towards the tundish & has support every 1m-1.5m? |  | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - Refrigeration lines supported by pipe clamps to avoid damage the insulation? |  | Refrigeration lines supported by pipe clamps to avoid damage the insulation? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - All FCU flexible ducts connections to air terminals & spigots have been air tight by using duct tape? |  | All FCU flexible ducts connections to air terminals and spigots have been air tight by using duct tape? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - All FCU flexible ducts installed & supported by intact load spreader? |  | All FCU flexible ducts installed and supported by intact load spreader? | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - All FCU flexible ducts connections to air terminals & spigots have been secured by using fixing ties/cables ties |  | All FCU flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties | Air Conditioning: | Apartment Ceiling Closure
|  | Air Conditioning - Supply boxes are installed & supported at correct location in the middle of bulkhead height? |  | Supply boxes are installed and supported at correct location in the middle of bulkhead height? | Air Conditioning: | Apartment Ceiling Closure
|  | Ventilation |  | Ventilation | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - Inspection Date: | Inspection Date: | Ventilation | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - Vent fans are installed with rubber isolation in the correct location as per drawing? |  | Vent fans are installed with rubber isolation in the correct location as per drawing? | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - All flex are installed & supported by intact load spreaders? |  | All flex are installed and supported by intact load spreaders? | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - All flexible ducts inner core & outer core have been mechanically secured & taped to spigots & air terminals by using duct tape & fixing/cable ties? |  | All flexible ducts inner core and outer core have been mechanically secured & taped to spigots and air terminals by using duct tape & fixing/cable ties? | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - Flexible ducts run on the right location & not jammed? |  | Flexible ducts run on the right location and not jammed? | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - Butterfly dampers are installed & they are in a fully opened position & air tight sealed? |  | Butterfly dampers are installed and they are in a fully opened position and air tight sealed? | Ventilation: | Apartment Ceiling Closure
|  | Ventilation - PVC ducts have been hung at correct height & supported by hanging straps? |  | PVC ducts have been hung at correct height and supported by hanging straps? | Ventilation: | Apartment Ceiling Closure
|  | Access Panel |  | Access Panel | Access Panel: | Apartment Ceiling Closure
|  | Access Panel - Inspection Date: | Inspection Date: | Access Panel | Access Panel: | Apartment Ceiling Closure
|  | Access Panel - Access Panel location has been marked on floor as per RCP & has been checked |  | Access Panel location has been marked on floor as per RCP and has been checked | Access Panel: | Apartment Ceiling Closure
|  | Access Panel - All other services do not impede access |  | All other services do not impede access | Access Panel: | Apartment Ceiling Closure
Rough In (BUILDING-A / Common Area)
| Scope |  |  | Rough In | BUILDING-A | Common Area
Rows
|  | Level-3 | dynamic | Rough In | BUILDING-A | Level-3 | Common Area
|  | Level-4 | dynamic | Rough In | BUILDING-A | Level-4 | Common Area
|  | Level-5 | dynamic | Rough In | BUILDING-A | Level-5 | Common Area
|  | Level-6 | dynamic | Rough In | BUILDING-A | Level-6 | Common Area
|  | Level-7 | dynamic | Rough In | BUILDING-A | Level-7 | Common Area
|  | Level-8 | dynamic | Rough In | BUILDING-A | Level-8 | Common Area
|  | Level-9 | dynamic | Rough In | BUILDING-A | Level-9 | Common Area
|  | Level-10 | dynamic | Rough In | BUILDING-A | Level-10 | Common Area
|  | Level-11 | dynamic | Rough In | BUILDING-A | Level-11 | Common Area
|  | Level-12 | dynamic | Rough In | BUILDING-A | Level-12 | Common Area
|  | Level-13 | dynamic | Rough In | BUILDING-A | Level-13 | Common Area
|  | Level-14 | dynamic | Rough In | BUILDING-A | Level-14 | Common Area
|  | Level-15 | dynamic | Rough In | BUILDING-A | Level-15 | Common Area
|  | Level-16 | dynamic | Rough In | BUILDING-A | Level-16 | Common Area
|  | Level-17 | dynamic | Rough In | BUILDING-A | Level-17 | Common Area
|  | Level-18 | dynamic | Rough In | BUILDING-A | Level-18 | Common Area
|  | Level-19 | dynamic | Rough In | BUILDING-A | Level-19 | Common Area
Columns
|  | Duct Installation - Are drawings on site the latest issue |  | Are drawings on site the latest issue | Duct Installation Checklist
|  | Duct Installation - Are plant & equipment location correct |  | Are plant and equipment location correct | Duct Installation Checklist
|  | Duct Installation - Fan in the duct run has been installed |  | Fan in the duct run has been installed | Duct Installation Checklist
|  | Duct Installation - Model of the fan is correct as per latest Fan Schedule |  | Model of the fan is correct as per latest Fan Schedule | Duct Installation Checklist
|  | Duct Installation - Duct size & location correct |  | Duct size and location correct | Duct Installation Checklist
|  | Duct Installation - Material & gauge correct |  | Material and gauge correct | Duct Installation Checklist
|  | Duct Installation - Is correct support method being used - Risers are supported at each level. |  | Is correct support method being used - Risers are supported at each level. | Duct Installation Checklist
|  | Duct Installation - Is correct jointing method being used |  | Is correct jointing method being used | Duct Installation Checklist
|  | Duct Installation - Are joints completed & cleated installed on flanges |  | Are joints completed and cleated installed on flanges | Duct Installation Checklist
|  | Duct Installation - Is correct joint sealant being used |  | Is correct joint sealant being used | Duct Installation Checklist
|  | Duct Installation - Has the spacer been placed between the fan & the silencer, & the splitter orientation rotated by 90°? |  | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°? | Duct Installation Checklist
|  | Duct Installation - Is 1 diameter of straight duct between pod attenuator & fan inlet been allowed to ensure impeller obtains even flow? |  | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow? | Duct Installation Checklist
|  | Duct Installation - Is adequate distance between attenuator & fans been maintained? |  | Is adequate distance between attenuator and fans been maintained? | Duct Installation Checklist
|  | Duct Installation - Are the attenuator splitters in the plane of the bend ? |  | Are the attenuator splitters in the plane of the bend ? | Duct Installation Checklist
|  | Duct Installation - Are transitions close to attenuators gradual? |  | Are transitions close to attenuators gradual? | Duct Installation Checklist
|  | Duct Installation - Is a settling duct between volume control dampers & attenuators allowed? |  | Is a settling duct between volume control dampers and attenuators allowed? | Duct Installation Checklist
|  | Duct Installation - Are fire dampers installed & break away joint complete |  | Are fire dampers installed and break away joint complete | Duct Installation Checklist
|  | Duct Installation - Are flexible ducts installed, supported & connected to spigot by approved method using duct tape on internal core & cable tie on outer core |  | Are flexible ducts installed, supported and connected to spigot by approved method using duct tape on internal core and cable tie on outer core | Duct Installation Checklist
|  | Duct Installation - Are flexible connections to equipment sealed & aligned |  | Are flexible connections to equipment sealed and aligned | Duct Installation Checklist
|  | Duct Installation - Is ductwork insulation as per drawings |  | Is ductwork insulation as per drawings | Duct Installation Checklist
|  | Duct Installation - Is ductwork fire rating complete |  | Is ductwork fire rating complete | Duct Installation Checklist
|  | Duct Installation - Are all spigots installed & dampers fully open |  | Are all spigots installed and dampers fully open | Duct Installation Checklist
|  | Duct Installation - Are all access panels for fire damper access installed & closed |  | Are all access panels for fire damper access installed and closed | Duct Installation Checklist
|  | Duct Installation - Is ductwork installation complete |  | Is ductwork installation complete | Duct Installation Checklist
|  | Lobby Area - Lobby Area: |  | Lobby Area: | Lobby Area
|  | Lobby Area - Inspection Date: | Inspection Date: | Lobby Area: | Lobby Area
|  | Lobby Area - Other services installed are not impeding access to fan coil |  | Other services installed are not impeding access to fan coil | Lobby Area
|  | Lobby Area - All Ductwork passing block walls are flushed & sealed |  | All Ductwork passing block walls are flushed and sealed | Lobby Area
|  | Lobby Area - Transfer duct installed at Accessible toilet wall & penetration flushed & sealed |  | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed | Lobby Area
|  | Lobby Area - Where passing the block wall flexible ducts has been equipped with Sleeve & penetration sealed |  | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed | Lobby Area
|  | Lobby Area - Refrigerant pipes passing through fire rarted walls are sealed at wall penetration by using approved material |  | Refrigerant pipes passing through fire rarted walls are sealed at wall penetration by using approved material | Lobby Area
|  | Ducting - Riser |  | Riser | Ducting-Common Area
|  | Ducting - Are drawings on site the latest issue |  | Are drawings on site the latest issue | Ducting-Common Area
|  | Ducting - Are plant & equipment location correct |  | Are plant and equipment location correct | Ducting-Common Area
|  | Ducting - Duct size & location correct |  | Duct size and location correct | Ducting-Common Area
|  | Ducting - Material & gauge correct |  | Material and gauge correct | Ducting-Common Area
|  | Ducting - Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method |  | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method | Ducting-Common Area
|  | Ducting - Is correct Joining method being used |  | Is correct Joining method being used | Ducting-Common Area
|  | Ducting - Are joints completed & cleated installed on flanges |  | Are joints completed and cleated installed on flanges | Ducting-Common Area
|  | Ducting - Is correct joint sealant being used |  | Is correct joint sealant being used | Ducting-Common Area
|  | Ducting - Is ductwork installation complete |  | Is ductwork installation complete | Ducting-Common Area