## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 561469-ITP-0001 Seacliff ITP - Culverts | itp |  |  |  | Yes | 561469-ITP-0001 Seacliff ITP - Culverts Rev 1
section | 1.01
checkpoint | Pipes
label | Acceptance / Conformance Criteria - Pipes shall be of material mentioned in the Drawings or approved equivalent.
label | Standard / Specification - Project Requirement Drawing C122 - C123
label | Verifying Document - Photo
label | Frequency - Prior to installation
checkpoint | Subsoil drains
label | Acceptance / Conformance Criteria - Drainage pipes shall be slotted smooth bore PVC or PE pipes, or corrugated polyethylene subsoil drainage pipes in accordance with NZTA F/5 for light duty applications or NZTA F2 for heay-duty applications
label | Standard / Specification - Specification 1131 14.8
label | Frequency - Prior to installation
checkpoint | Subsoil drain bedding
label | Acceptance / Conformance Criteria - Material used for bedding, duct surround and haunching shall be selected granular, non cohesive, free draining material with grading between 0.6mm and 19mm
label | Standard / Specification - Specification 1131 14.8
label | Frequency - Prior to installation
checkpoint | Concrete Manhole
label | Acceptance / Conformance Criteria - Precast concrete manholes shall comply with NZS 3106
label | Standard / Specification - Specification 1131 14.5
label | Verifying Document - Photo
label | Frequency - Prior to installation
checkpoint | Pipe Bedding
label | Acceptance / Conformance Criteria - Pipe bedding should be AP20 and in accordance with AS/NZS 2566.2
label | Standard / Specification - specification 1131 14.9.1
label | Verifying Document - Test Report
label | Frequency - Prior to installation
checkpoint | Backfill
label | Acceptance / Conformance Criteria - Backfill aggregate should be GAP 65. Samples of backfill material should be tested in accordence of NZS 4402 to determine the max lab dry density at OMC. The solid density of aggregate should be tested in accordance with NZS 4407.
label | Standard / Specification - specification 1131 16.1.1
label | Verifying Document - Test Report
label | Frequency - Prior to installation
checkpoint | Wingwalls
label | Acceptance / Conformance Criteria - Precast wingwalls as specified in Drawings or equivalent approved
label | Standard / Specification - Project Requirement Drawing C122 - C123
label | Verifying Document - Photo
label | Frequency - Prior to installation
checkpoint | Geotextile underlay
label | Acceptance / Conformance Criteria - Geotextile underlay bidim A37 or similar approved material
label | Standard / Specification - Project Requirement Drawing C122 - C123
label | Frequency - Prior to installation
checkpoint | Rock riprap
label | Acceptance / Conformance Criteria - Rock riprap shall comply with the dimensions and specifications shown in drawings
label | Standard / Specification - Project Requirement Drawing C122 - C123
label | Frequency - Prior to installation
section | 2.01 Preliminaries
checkpoint | Service locate
label | Acceptance / Conformance Criteria - Confirm location of services by completing a service trace.
label | Standard / Specification - Specification 1131 15.2.1
label | Verifying Document - B4UDig, Service Plans, Mark out, Check list or something
label | Frequency - Prior to Start
checkpoint | Set Out
label | Acceptance / Conformance Criteria - All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works
label | Standard / Specification - Specification 1000 3.2.4
label | Verifying Document - methodology, check list or something
label | Frequency - prior to start
section | 2.01 Construction
checkpoint | Topsoil removal
label | Acceptance / Conformance Criteria - Top soil shall be removed in accordance with Clause 4 of TNZ F/1 and stockpiled to provide for subsequent replacement.
label | Standard / Specification - Specification 1110 9.4
label | Verifying Document - methodology
checkpoint | Contaminated soils
label | Acceptance / Conformance Criteria - Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements
label | Standard / Specification - Specification 1110 9.3
checkpoint | Trench excavation
label | Acceptance / Conformance Criteria - Trenches for flexible pipes shall be excavated within tollerances below unless otherwise stated:
label | – – – – – – – – – – – – – – – – –
label | Pipe OD mm ¦¦ Minimum clearance to trench walls from pipe OD mm ¦¦ Minimum Trench Width mm
label | – – – – – – – – – – – – – – – – –
label | ≤ 150 ¦¦ 300 ¦¦ Pipe OD + 600
label | > 150 and ≤ 300 ¦¦ 300 ¦¦ Pipe OD + 600
label | > 300 and ≤ 450 ¦¦ 300 ¦¦ Pipe OD + 600
label | > 450 and ≤ 600 ¦¦ 300 ¦¦ Pipe OD + 600
label | > 600 and ≤ 900 ¦¦ 300 ¦¦ Pipe OD + 600
label | > 900 and ≤ 1500 ¦¦ 350 ¦¦ Pipe OD + 700
label | – – – – – – – – – – – – – – – – –
label | Standard / Specification - specification 1131 15.2.5
label | Verifying Document - Installation Check Sheet
label | Frequency - During installation
checkpoint | Pipe Bedding
label | Acceptance / Conformance Criteria - Bedding for flexible pipes should be in accordance with AS/NZS 2556.2 and have minimum embedment zone as shown below:
label | – – – – – – – – – – – – – – – – –
label | Pipe OD mm ¦¦ Bedding below base of pipe mm ¦¦ Bedding above crown of pipe mm ¦¦ Bedding either side of the pipe mm
label | – – – – – – – – – – – – – – – – –
label | ≤ 150 ¦¦ 100 ¦¦ 100 ¦¦ 100
label | > 150 and ≤ 300 ¦¦ 100 ¦¦ 150 ¦¦ 150
label | > 300 and ≤ 450 ¦¦ 100 ¦¦ 150 ¦¦ 200
label | > 450 and ≤ 900 ¦¦ 150 ¦¦ 150 ¦¦ 300
label | > 900 and ≤ 1500 ¦¦ 150 ¦¦ 200 ¦¦ 350
label | > 1500 ¦¦ 150 ¦¦ 300 ¦¦ 0.25 x Pipe OD
label | – – – – – – – – – – – – – – – – –
label | Standard / Specification - Specification 1131 15.2.8.2
label | Verifying Document - Installation Check Sheet
label | Frequency - During installation
checkpoint | Line and level
label | Acceptance / Conformance Criteria - Pipes shall be laid true to the design line and level within the tolerances specified
label | Standard / Specification - Specification 1131 15.3.12, Specification 1131 15.9
label | Verifying Document - Grade Check sheet
label | Frequency - During installation
checkpoint | PE pipe installation
label | Acceptance / Conformance Criteria - Buried PE pipes shall be installed in accordance with AS/NZA 2566.2
label | Standard / Specification - Specification 1131 15.3.2.2
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | PVC pipe installation
label | Acceptance / Conformance Criteria - Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2. fusible PVC pipes shall be welded and installed in accordance with the pipe manufacturers recommendations.
label | Standard / Specification - Specification 1131 15.3.1
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | Precast concrete pipes
label | Acceptance / Conformance Criteria - Concrete pipes shall be installed in accordance with AS/NZS 3725 and verification testing of compaction shall use a method recommended in table 3 of the CPAA Technical Note on Installing Concrete Pipe and approved by the Engineer.
label | Standard / Specification - Specification 1131 15.3.6
label | Verifying Document - Clegg/ scala test records
checkpoint | Joints in precast concrete
label | Acceptance / Conformance Criteria - Joints between precast pipe units shall be self-centering and shall be sealed with butyl mastic or similar approved to form a watertight joint.
label | Standard / Specification - Specification 1131 15.3.6
label | Frequency - During installation
checkpoint | Compaction
label | Acceptance / Conformance Criteria - Compaction shall be as follows
label | – – – – – – – – – – – – – – – – –
label | Table of Compaction Requirements
label | – – – – – – – – – – – – – – – – –
label | Layer / Zone ¦¦ Requirement in:
label | Carriageway^1 :: Footpath :: Berm
label | – – – – – – – – – – – – – – – – –
label | Basecourse ¦¦ 98% MDD :: 95% MDD :: N/A
label | Sub-base ¦¦ 98% MDD :: 90% MDD :: N/A
label | Deeper Fill ¦¦ 90% MDD :: 85% MDD :: 80% MDD
label | – – – – – – – – – – – – – – – – –
label | Pipe Embedment ¦¦ Flexible Pipes: Refer AS/NZS 2566.2
label | Pipe Embedment ¦¦ Rigid Pipes: to manufacturer's requirements
label | – – – – – – – – – – – – – – – – –
label | Standard / Specification - specification 1131 15.4.4
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - During installation
checkpoint | Backfiil - Under Carriageways
label | Acceptance / Conformance Criteria - Selected fill within 0.8m depth from finished surface shall be AP 65 and compacted to at least 95% of max dry density at OMC
label | ○ Subgrade and subbase shall be compacted in layers no greater than 200 mm thick unless otherwise agreed with the Engineer.
label | ○ Basecourse shall be compacted in layers no greater than 150mm thick unless otherwise aggred with the engineer.
label | Standard / Specification - specification 1131 15.4.3.2
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - NDM every 20m, each layer
checkpoint | Backfill - Outside Carriageways
label | Acceptance / Conformance Criteria - Backfill outside carriageways shall be compacted in layers not exceeding 200 mm thick to a maximum dry density of at least 90%, or to the same density as the surrounding ground, whichever is the lesser.
label | Standard / Specification - specification 1131 15.4.3.3
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - NDM every 50m, each layer
checkpoint | Cutting pipes
label | Acceptance / Conformance Criteria - where pipes need to be cut to form non stardard lengths, pipes shall be cut by a method which complys with manufacturers recommendations and provides a clean square profile
label | Standard / Specification - Specification 1131 15.3.7
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | Benching
label | Acceptance / Conformance Criteria - Benching concrete shall have a crushing strength of 20MPa at 28 days.
label | ○ Semi-circular channels and fittings shall be placed in possition simultaneously with concrete benching and be embedded in true to grade level and line.
label | ○ All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar and finished with steel trowel and rounded at corners.
label | Standard / Specification - Specification 1131 15.5
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | Laying subsoil drains
label | Acceptance / Conformance Criteria - Drains shall be constucted in accordance with TNZ Specification F/6. Geotextile shall be laid and jointed in accordance with TNZ specification F/6. Bacfilling shall be carried out in accordance with TNZ specification F/6
label | Standard / Specification - Specification 1131 15.7
label | Verifying Document - methodology
label | Frequency - During installation
checkpoint | Topsoiling and grassing
label | Acceptance / Conformance Criteria - Topsoil shall be used to dress areas disturbed by the contrat works to a minimum thickness of 100mm. Grass seed shall be sown evenly over the prepared topsoil area
label | Standard / Specification - Specification 1131 15.8.6
label | Verifying Document - check list
label | Frequency - prior to commencement
section | 3.01
checkpoint | Backfill Compaction Testing
label | Acceptance / Conformance Criteria - Prior to commencement of fill Trial compaction plateau test should be conducted under presense of Engineer or principal. Methodology to be confirmed in advance generally in accordance with TNZ B/02 specification
label | Standard / Specification - Specification 16.1.1
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - prior to commencement of fill compaction
checkpoint | Testing of Compaction in Carrigeway
label | Acceptance / Conformance Criteria - a) Testing of compaction shall be carried out in accordance with 16.1.1above.
label | b) All materials used for backfilling shall have been sampled and tested by a certified testing laboratory. The Engineer may instruct the Contractor to provide records of material test certification.
label | c) Density testing shall be carried out and recorded by a suitably qualified person at the following frequencies unless otherwise confirmed by the Engineer to suit the size and scale of the project:
label | Standard / Specification - Specification 16.1.2
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - i. For trenches in berms, testing is required at least one per layer of backfill per 50 m of trench, with a minimum of two tests for each pipe installation.
label | ii. For trenches in carriageways or footpaths, testing is required at least one test per layer of backfill per 20 m of trench with a minimum of two tests for each pipe installation.
label | iii. Where the excavated area is greater than 0.5 m2 and less than 5 m2 testing is required one test per backfill layer.
label | iv. Where the excavated area is greater than 5 m2 testing is required one test per backfill layer for each 5 m2.
label | v. Tests shall be carried out on every lift of each tested backfill layer to be assured of proper compaction of all of the backfill.
checkpoint | Testing of Compaction outside carrigeway
label | Acceptance / Conformance Criteria - a) Testing of compaction shall be carried out in accordance with 16.1.1, above.
label | b) Density testing shall be carried out by a suitable qualified person at the following frequencies unless otherwise confirmed by the Engineer to suit the size and scale of the project:
label | Standard / Specification - Specification 16.1.4
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - i. For trench lengths of 100 m or more, testing is required at a rate of at least one test per layer of backfill per 50 m of trench.
label | ii. For trench lengths less than 100 m, a minimum of two tests per layer are required.
label | iii. Where the excavated area is greater than 0.5 m2 and less than 10 m2, one test per backfill layer are required.
label | iv. Where the excavated area is greater than 10 m2 testing is required one test per backfill layer for each 10m2.
label | v. Tests shall be carried out on every lift of each tested backfill layer to be assured of proper compaction of all of the backfill.
checkpoint | NDM test
label | Acceptance / Conformance Criteria - NDM teting of fill placement shall be conducted for each 300mm lift and shall be tested 1 per 100m2 on a nominal 10m by 10m grid pattern
label | Standard / Specification - Specification 1110 9.13.2
label | Verifying Document - NDM or Clegg Hamer test records
label | Frequency - during installation
checkpoint | Pipe Testing
label | Acceptance / Conformance Criteria - stormwater pipes shall be by visual inspection for pipe diameters greater than 750mm and by water testing for diameters up to 750mm. Testing shall be in the presence of the engineer.
label | Standard / Specification - Specification 1131 16.2.1
label | Verifying Document - Test Records
label | Frequency - 24hr prior notice
checkpoint | Manholes
label | Acceptance / Conformance Criteria - manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. Testing shall be in the presence of the engineer.
label | Standard / Specification - Specification 1131 16.2.2.5
label | Verifying Document - Test Records
label | Frequency - 24hr prior notice
checkpoint | CCTV
label | Acceptance / Conformance Criteria - All pipelines shall pass a CCTV instpection. All pipelines shall be free of debris and flushed 24hrs prior to inspection.
label | Standard / Specification - Specification 1131 16.2.3
label | Verifying Document - CCTV footage and log sheets
label | Frequency - completion of works
section | 4.01 As-Built Information
checkpoint | As-built Drawings
label | Acceptance / Conformance Criteria - As-built drawings shall be prepared in draft and final versions in accordance with 5.20.3 of the conditions of Contract. Asbuilts shall follow Schedule 1D in NZS4404:2010.
label | Standard / Specification - Specification 1000 3.9.2
label | Verifying Document - QA records