## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Fire Sprinkler - Installation Pressure Test |  |  |  |  | Yes | Fire Sprinkler - Installation | 071fe027-db51-413f-bbf9-1afed7de7d03
checkpoint-status |  |  | checkpoint | Pressure Test Complete
text | cb58ccba-008f-57e5-8a97-fc474fbcef56 |  | textbox | Design Pressure
text | 39810a4f-f8d9-577f-9558-c05dcf0cb232 |  | textbox | Test Start Time
select | 0d404a58-3891-5d4f-a936-e9a7cf34a082 |  | dropdown | Test Pressure Start: | Nitrogen: 1000KPA,Water: 1800KPA
text | a601b515-a4b4-5d47-8a2f-d98f63dbd904 |  | textbox | Test Finish Time
select | 69a7148a-93e7-5b7b-a89c-d79ee1f77eda |  | dropdown | Test Pressure Finish | Nitrogen,Water
text | bcfcbf1a-a6ae-52da-917a-023ef7219961 |  | textbox | Location of Pipework
select | 59ff4f8c-09ee-5722-a617-0334bab1b99c |  | dropdown | Test Duration | Nitrogen: 30 mins, Water: 60 mins
checkpoint-status |  |  | checkpoint | Signed Off
text | 6dea9385-cf1e-5519-8783-2b6b21e141c7 |  | textbox | Technician Name
text | 2363a598-6bed-5b38-9e32-384b50066514 |  | textbox | Witness Name
checklist-flat |  |  | checklist | Commissioning Plan |  |  |  |  | Yes | Commissioning Plan | 15f10315-2c27-45d5-8488-30fb0cb55929
checkpoint-status |  |  | checkpoint | Upload commissioning plan here and press PASS
checklist-flat |  |  | checklist | Fire Pump - Pre Commissioning |  |  |  |  | Yes | Fire Pump - Pre Commissioning | 1b50b0b2-a4dd-405c-9b53-1053535fdb54
checkpoint-status |  |  | checkpoint | Fire Pump Room Sign Installed on Door to Fire Pump
checkpoint-status |  |  | checkpoint | Pump Room and Valve Room clean and tidy
checkpoint-status |  |  | checkpoint | Pump Running LED operates on Mimic Panel
checkpoint-status |  |  | checkpoint | Pump Batteries are Labelled A & B and Dated and cases secured to floor
checkpoint-status |  |  | checkpoint | Fuel Lines are tidy and trip guard installed if required
checkpoint-status |  |  | checkpoint | Fuel Tank Gauge installed and operational
checkpoint-status |  |  | checkpoint | Fuel Tank Supply valve to Pump securely locked open (Bottom of Tank)
checkpoint-status |  |  | checkpoint | Fuel Vent Installed outside of room in BLACK PIPE AND FITTINGS OR SS (NOT GALV)
checkpoint-status |  |  | checkpoint | Fuel Drum, manual pump and hoses connected.
checkpoint-status |  |  | checkpoint | Test pumping to confirm overflow does not blow out breather.
checkpoint-status |  |  | checkpoint | Fire Pump Controller power supply locked and on.
checkpoint-status |  |  | checkpoint | All Labels fitted
checkpoint-status |  |  | checkpoint | All Gauges on Pump Fitted with service valves
checkpoint-status |  |  | checkpoint | Pump Water Supply Shut off Valve monitored to FIRE and signals (Isolate DBA Fires) and also restores to normal
checkpoint-status |  |  | checkpoint | Emergency Cooling line bypass is strapped closed
checkpoint-status |  |  | checkpoint | Cooling line strapped open
checkpoint-status |  |  | checkpoint | Pump Shut off Gate Valve padlocked in open position
checkpoint-status |  |  | checkpoint | Open Before Pumping Sign on FSI
checkpoint-status |  |  | checkpoint | Gauges all marked (Standing, Defect, Fire, Pump Start)
checkpoint-status |  |  | checkpoint | All DEFECT, Fire, Pump Start Signals Match Block Plan and compliant
checklist-flat |  |  | checklist | Sprinkler - Second Fix |  |  |  |  | Yes | Sprinkler - Second Fix | 2d842f39-61ec-4e7b-9055-43f44f76634f
checkpoint-status |  |  | checkpoint | Sprinkler Heads/Flexis Installed Correctly
checkpoint-status |  |  | checkpoint | Escutcheons Seated Correctly
checkpoint-status |  |  | checkpoint | No damage to ceiling or tiles observed
checkpoint-status |  |  | checkpoint | Final Pressure Test Complete
checkpoint-status |  |  | checkpoint | Inspection Complete
checkpoint-status |  |  | checkpoint | Remedial Items Complete
checkpoint-status |  |  | checkpoint | Floor Cleared Of All Material
checkpoint-status |  |  | checkpoint | Pipe Slopes As Per Drawing
checklist-flat |  |  | checklist | Fire Sprinkler - Pre Commissioning |  |  |  |  | Yes | Fire Sprinkler - Pre Commissioning | 3abb1af8-1183-435c-b04d-6cf268e8a1e6
checkpoint-status |  |  | checkpoint | 230V for Jockey pump (Dual outlet)
checkpoint-status |  |  | checkpoint | No Water Leaks in system
checkpoint-status |  |  | checkpoint | All Valves, Gong, Pump Bypass labelled and Padlocked in correct positions in compliance with Standard
checkpoint-status |  |  | checkpoint | DBA Digital transducer calibrated and set
checkpoint-status |  |  | checkpoint | All main stop valves Signal FIRE, Padlocked & labelled
checkpoint-status |  |  | checkpoint | All Subsidiary Valves (if applicable) Signal Defect, Padlocked & labelled
checkpoint-status |  |  | checkpoint | All main Section/Floor Valves (if applicable) Signal FIRE, Padlocked & labelled
checkpoint-status |  |  | checkpoint | Pump Bypass Signals DEFECT, chained, locked & Labelled
checkpoint-status |  |  | checkpoint | Pump Umbilical cord removal signals – DEFECT
checkpoint-status |  |  | checkpoint | 230V Power Fail Isolated Signals – DEFECT
checkpoint-status |  |  | checkpoint | Pump Running Alarm operates & Manual Isolate works correctly
checkpoint-status |  |  | checkpoint | Pump Running manual isolate operated and silences alarm
checkpoint-status |  |  | checkpoint | Gong Operates
checkpoint-status |  |  | checkpoint | Gong Line shut off operates
checkpoint-status |  |  | checkpoint | Gong Line Locked open and labelled
checkpoint-status |  |  | checkpoint | 50mm Drain Locked closed and labelled
checkpoint-status |  |  | checkpoint | Jockey Pump Operates & Check Valves are installed correctly.
checkpoint-status |  |  | checkpoint | Block Plan installed and visible
checkpoint-status |  |  | checkpoint | FSI Butterfly valve installed
checkpoint-status |  |  | checkpoint | FSI (Fire Sprinkler System Inside) Sign is installed on FSI pipework/ Cabinet
checkpoint-status |  |  | checkpoint | Valve Room Sign is installed on Door of Valve-room
checklist-flat |  |  | checklist | Hydrant - Pre Commissioning |  |  |  |  | Yes | Hydrant - Pre Commissioning | 525f9852-fc87-421b-8af8-eac50d04ce86
checkpoint-status |  |  | checkpoint | Flexible couplings installed above and below landings
checkpoint-status |  |  | checkpoint | Test outlet installed
checkpoint-status |  |  | checkpoint | Pressure test completed
checkpoint-status |  |  | checkpoint | No Leaks
checkpoint-status |  |  | checkpoint | All Valves locked and closed
checkpoint-status |  |  | checkpoint | All Signs on Doors
checkpoint-status |  |  | checkpoint | Gauge installed at top of riser
checkpoint-status |  |  | checkpoint | Air release valve installed at top of riser
checkpoint-status |  |  | checkpoint | Gauge installed on Test point.
checkpoint-status |  |  | checkpoint | Hydrant Laminated P& ID Schematic installed in Valveroom near Hydrant
checkpoint-status |  |  | checkpoint | In Building Hydrant Sign is clearly displayed on Cabinet door in Valveroom
checklist-flat |  |  | checklist | Sprinkler Installation |  |  |  |  | Yes | Sprinkler Installation checklist | b701df88-6ead-45b0-91ca-73ca72643961
checkpoint-status |  |  | checkpoint | Mains & Ranges Installed
checkpoint-status |  |  | checkpoint | Flexible droppers installed
checkpoint-status |  |  | checkpoint | CS Sprinklers installed
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checkpoint-status |  |  | checkpoint | Sprinklers installed on Flexible droppers
checkpoint-status |  |  | checkpoint | Pressure test completed
checkpoint-status |  |  | checkpoint | Flexible droppers installed to Grid / Rondo
checkpoint-status |  |  | checkpoint | Orange protective caps removed and Escutcheon plate installed for tiled ceiling
checkpoint-status |  |  | checkpoint | Protective caps removed and Concealed plate installed for GIB ceiling
checkpoint-status |  |  | checkpoint | Sprinkler tiles are clean with no fingerprint marks or damage
checkpoint-status |  |  | checkpoint | Remedial Items Complete
checkpoint-status |  |  | checkpoint | Floor cleared of all material
checkpoint-status |  |  | checkpoint | Inspection Complete 1st Fix (3rd Party Inspector)
checkpoint-status |  |  | checkpoint | Inspection Complete 2nd Fix (3rd Party Inspector)
checkpoint-status |  |  | checkpoint | Handed over to Hawkins
checklist-flat |  |  | checklist | Fire Alarm - First Fix |  |  |  |  | Yes | Fire Alarm - First Fix | bad13fd7-f406-42b1-9723-cebf9807e480
checkpoint-status |  |  | checkpoint | Catenary wire - well supported, hangers in place, straight, turn buckle used
checkpoint-status |  |  | checkpoint | Wiring tidy- cables tied properly , cable ties spaced 300mm min and equally.
checkpoint-status |  |  | checkpoint | Cables positioned correctly according to drawings ready for 2nd Fix.
checkpoint-status |  |  | checkpoint | Conduit - Where installed is straight and saddles no more the 600mm apart
checkpoint-status |  |  | checkpoint | Junction Box / riser cable installed neatly on cable tray or cat wire
checkpoint-status |  |  | checkpoint | Panel/Junction Box Cables clearly labeled ready for 2nd Fix
checkpoint-status |  |  | checkpoint | Sprinkler Flow Switch / MV terminated correctly
checkpoint-status |  |  | checkpoint | Insulation resistance between individual conductors and between each conductor and earth above 5M ohm?
checkpoint-status |  |  | checkpoint | Vesda Pipes installed straight and as per drawings
checkpoint-status |  |  | checkpoint | Seismic hangers installed where required
checkpoint-status |  |  | checkpoint | Sampling Holes drilled to correct size as per drawing and sticker installed
checkpoint-status |  |  | checkpoint | Sampling Tube installed and long enough for 2nd Fix.
checklist-flat |  |  | checklist | Sprinkler - First Fix |  |  |  |  | Yes | Sprinkler - First Fix | c35b1377-ec73-4e11-867d-d4492cfeff97
checkpoint-status |  |  | checkpoint | Hangers Correctly Spaced
checkpoint-status |  |  | checkpoint | Seismic Bracing
checkpoint-status |  |  | checkpoint | C/S Heads Correct, Caps Removed
checkpoint-status |  |  | checkpoint | Pipework Installed As Per Drawing
checkpoint-status |  |  | checkpoint | Couplings Installed Correctly
checkpoint-status |  |  | checkpoint | Low Point Drains
checkpoint-status |  |  | checkpoint | Pipe Slopes As Per Drawing
checkpoint-status |  |  | checkpoint | Pressure Test Complete
checkpoint-status |  |  | checkpoint | Inspection Complete
checklist-flat |  |  | checklist | COC |  |  |  |  | Yes | COC | df83cd57-758f-468e-8d61-6d25293ec91d
checkpoint-status |  |  | checkpoint | Upload COC here and press PASS
checklist-flat |  |  | checklist | Fire Alarm - Second Fix |  |  |  |  | Yes | Fire Alarm - Second Fix | ea76f501-d29c-4d2d-a5e0-a04bdf6c2e33
checkpoint-status |  |  | checkpoint | Smoke Detectors installed correctly, labelled & are in compliance / spaced correctly
checkpoint-status |  |  | checkpoint | Heat Detectors installed correctly, labelled & are in compliance / spaced correctly
checkpoint-status |  |  | checkpoint | MCP's installed correctly, labelled & are in compliance / spaced correctly
checkpoint-status |  |  | checkpoint | Sounders/Strobes installed correctly, labelled & are in compliance
checkpoint-status |  |  | checkpoint | Sampling Points installed correctly, labelled & are in compliance / spaced correctly
checkpoint-status |  |  | checkpoint | Interfaces installed correctly & labelled
checkpoint-status |  |  | checkpoint | Fire Alarm Panel installed Level and at correct Height
checkpoint-status |  |  | checkpoint | Remote Mimic installed Level and at correct Height
checkpoint-status |  |  | checkpoint | EWIS installed Level and at correct Height
checkpoint-status |  |  | checkpoint | Vesda Unit installed Level and at correct Height
checkpoint-status |  |  | checkpoint | Power Supply installed Level and at correct Height
checkpoint-status |  |  | checkpoint | Crimp pin terminals or ferrules fitted to EOL Resistors and cables terminated
checkpoint-status |  |  | checkpoint | All Panels cleaned of debris ready for power up
checkpoint-status |  |  | checkpoint | Floor cleared of all rubbish and material ready for commissioning