## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 2b599487-d8ad-497c-845e-65045b79494c |  | checklist | Fit-Off |  |  |  |  | Yes | Fit-Off Checklist | 071ee2e4-756e-4c90-8320-7e6365aecc6c
checkpoint-group | 1b8f3396-e814-47ee-b0fd-d44f0361a060 |  | section | Internal
checkpoint-status | fc8ac15c-3c68-4d41-932a-bfa180e77723 |  | checkpoint | AC grille to living room installed with no defect
checkpoint-status | f52fd2f7-3d91-4299-936f-7068f273e5e7 |  | checkpoint | AC grille to bedroom installed with no defect
checkpoint-status | 4ea2ef38-e34c-480c-a537-0465a2f2ccc0 |  | checkpoint | Return Air grille installed as per RCP drawings
checkpoint-status | 75dfd2f3-8f8b-4d0b-a14d-81321f50d6cd |  | checkpoint | Range hood duct connected and taped to ensure air tight
checkpoint-status | 3667ef1a-5664-4cda-8e3e-4270b2182f0d |  | checkpoint | AC Controller installed as per RCP drawings
checkpoint-status | 10471e23-1e95-4049-ba75-6728b2e621a5 |  | checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point
checkpoint-status | 29ce787a-cb65-4a56-b12f-69df4ee196b8 |  | checkpoint | Ensuit Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-status | 79685fae-2207-42fc-8507-95a66d7eeb70 |  | checkpoint | Laundry Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-status | 3723e8c6-1830-41c5-ae75-2c2e15bf5416 |  | checkpoint | Toielt Exhasut fans installed and pluged in as per mechanical drawings
checkpoint-group | 7edad05c-65f8-4744-b938-c1fbdcbdfba0 |  | section | External
checkpoint-status | 5e6aebee-aeef-4b26-8afd-99de564655e0 |  | checkpoint | Access panels placed as per drawings
checkpoint-status | bafde3ea-498d-4bbb-af26-2741f3a72ca5 |  | checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked
checkpoint-status | 1219fafa-f3b0-4a6d-addf-c8d2611d47d1 |  | checkpoint | External louvres installed all gaps sealed between plenum box and wall/ louvre flange to wall , photo evidence provided for below
button | aa30a690-3f18-5443-834c-2aaed253e01b |  | button | Box sealed internally and the gap between the box and wall is sealed | Pass Fail, N/A
button | 65e4a0a0-09af-599e-bf46-40b15630f089 |  | button | Louvre flanges sealed to the external box | Pass Fail, N/A
checkpoint-status | a8bf7627-6666-46d0-904a-d3379a92a801 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | 06acdfe1-8dbf-58eb-ae08-2530dc96b490 |  | textbox | Inspection Date
boolean | 2bbe5eda-a463-5ee6-b780-bb9f1aa3f49a |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 68aadfce-602f-566d-bc0b-f682d8346656 |  | tickbox | Builder Representative Sign Off
holdpoint | e8403af5-b20d-455f-b287-b601bbfd724d |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | a40022a7-f871-4ac5-a838-7c93b3456e51 |  | checklist | Fire Box |  |  |  |  | Yes | Fire Box Checklist | 2d590588-632f-440d-999e-1897a2d1d2c5
checkpoint-status | 5c98bbe5-97c5-4c8e-b1ec-7cca16bdcd63 |  | checkpoint | Fire Box Nominally placed in the penetration opening
label | 6e234751-4322-560d-8771-a4725deb714d |  | note | Any issues with fit photo/comment below
checkpoint-status | d5085fd0-a855-4d5a-8502-c7946fdb58a4 |  | checkpoint | Fire Box Fitted Correctly - As per below
button | 1986dc12-2fc7-5805-ba0a-a348b0003659 |  | button | Fyreflex Mastic is applied around the FyreBox to at least 20mm deep to fill up the gaps | Yes, No, N/A
button | e8d8c0b3-d4fe-5d42-bb6e-2acddd96f17f |  | button | Mounting flanges are fitted around the Fyrebox and are hard up against the wall | Yes, No, N/A
button | d2f231ff-b84c-56ac-8f3c-d4f6b3775a73 |  | button | Steel Rivet or Screw used to secure the last corner of the flange together | Yes, No, N/A
button | c1afe467-ec75-52f9-bd44-946f2458ef24 |  | button | M6 masonry anchors used at 400mm centered to fix the flanges to the wall through preformed holes | Yes, No, N/A
checkpoint-status | 53d9efbe-441a-4b85-ab1d-5c6eb85e7646 |  | checkpoint | Black foam cut and placed in the Fyrebox to fill up any gaps within the services
checkpoint-status | 5038af71-a7f7-4dad-ae8f-ac89bb56146f |  | checkpoint | FyreWrap installed 450mm from the wall on both sides of the box
button | e6a79d32-e905-5d9a-a4e7-470c4afd881b |  | button | Steel strapping used to fix the Fyrewrap at three locations | Yes, No, N/A
button | 62f736ce-0d4f-5d66-a32f-5fd847658e15 |  | button | 25mmx25mm nominal fillet of FyreFlex sealant used to seal around the wrap and the wall | Yes, No, N/A
checkpoint-status | ca1a01d4-df1d-4041-9ada-e875f3928d4e |  | checkpoint | Pictures of Installation attached below
text | f8a49497-d929-5ff8-878b-781c3163a0a0 |  | textbox | Notes/Additional Comments
checkpoint-status | b3a1e011-0480-4daf-94b1-685e44a75d48 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | 26bd6748-cfe1-566d-89e5-a691b5f92b42 |  | textbox | Inspection Date
boolean | 4632ad6a-b880-5b43-bc1f-cf1a82a612da |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 043f1705-eba1-59c8-8f7a-1214c1d599eb |  | tickbox | Builder Representative Sign Off
holdpoint | c27ff049-5017-4925-b3e8-440aeb18fe3b |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 9c6073c4-809d-4b8f-8611-ced9d16e0e1e |  | checklist | Toolbox Talk |  |  |  |  | Yes | Toolbox Talk | 36161574-9f78-490a-b830-b3538fbc56dc
checkpoint-status | 24973db5-abdf-455d-aff3-911e9b9227f4 |  | checkpoint | Attach any photos or relevant documentation
text | 9b38ffd8-9758-595c-a2a7-8711ecde51e2 |  | textbox | Time
text | 7e623150-ceff-59b5-8dc3-d85292d62df2 |  | textbox | Duration
text | 6bd4ff14-674d-5c59-aebb-342b86b24228 |  | textbox | Subject of Discussion
text | 04749d14-59e9-5bb8-ba83-a51fbe42dd9d |  | textbox | Notes & Items raised
checkpoint-status | 57d79017-e568-47a5-a091-17eb80e6a7ae |  | checkpoint | People present, please sign on screen
checklist-flat | 7d404ea0-6fc4-4c4d-8aa8-87c9c121c70f |  | checklist | A/C Commissioning |  |  |  |  | Yes | A/C Commissioning Checklist | 4d165bb1-1202-4e5f-a891-54e973df8218
checkpoint-status | 70b65f51-3293-4917-87e5-3e4c70207bac |  | checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs
checkpoint-status | a6b3c0e8-4b25-4089-b447-8815d9cfdb8c |  | checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum
checkpoint-status | 1140aae6-882f-4e05-9002-755046a0546f |  | checkpoint | Indoor unit drains have been terminated to the tundish point
checkpoint-status | f71f9a7a-dc03-4d9b-ab66-d3d0b56a97a7 |  | checkpoint | Outdoor unit drains have been terminated to the tundish point
checkpoint-status | 29ae01c3-c8bb-473e-a473-9c8cfe8fc747 |  | checkpoint | Indoor unit flare connection has been properly insulated with specified insulation
checkpoint-status | a35f58a1-de8c-49f3-99d7-be26f9f718dd |  | checkpoint | Indoor unit drain connection point has been securely fastened and sealed
checkpoint-status | 078da090-8d7f-4115-b543-f6e231c60521 |  | checkpoint | A/C system has been operated for a minimum of 5hrs and no leaks are visible in the drain lines
checkpoint-status | d6d26c81-643c-4242-8e67-3b04d7fd5ab5 |  | checkpoint | A/C System Flows checked as per mechanical drawings
button | cca3eb6d-309e-56db-9573-d1d96bfcd8ff |  | button | Adequate flow has been achieved in bedroom 1 | Pass Fail, N/A
button | 20075961-6cc2-5ca3-a9f1-27d03c947f12 |  | button | Adequate flow has been achieved in bedroom 2 | Pass Fail, N/A
button | 7f9cf8ff-729f-5b10-bfb8-86acd7484637 |  | button | Adequate flow has been achieved in bedroom 3/study | Pass Fail, N/A
button | 4c5f9f21-ef87-52ed-bd89-de4e2d745c2b |  | button | Adequate flow has been achieved in living room | Pass Fail, N/A
checkpoint-status | e6ce00ea-ebe2-491d-83bb-fec97f7acf2e |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | c5f56fe7-897f-5ca7-a285-551ff4faa3a0 |  | textbox | Inspection Date
boolean | cbdb6a0f-026e-5605-abf5-804acde231c1 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 23680534-654d-5a3e-a8b2-b7301d4e20f5 |  | tickbox | Builder Representative Sign Off
holdpoint | 8b99e16c-d0c6-40ec-b796-b1a1320b78bf |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 3e57c0ce-c557-48c4-b175-f61582568c6f |  | checklist | Fire Damper - WSW6 |  |  |  |  | Yes | Fire Damper Checklist -WSW6 | 51c9a13a-9add-4376-90bd-7ddaa10500e0
checkpoint-status | 3878decf-0b8d-4a7e-8f45-fd0e8b4938e6 |  | checkpoint | Penetration details have been captured
text | 7889b0eb-a23f-5ecc-b2b5-7a72b775afc1 |  | textbox | Penetration ID
text | eb69f90f-9f32-557e-a90b-efab397a3b3c |  | textbox | Manufacturer
text | c2814545-3c77-5b84-ba0a-d4a083b6cc79 |  | textbox | Inspection Date
text | f945af79-7cb1-56c6-ae29-26b18243fa81 |  | textbox | Apartment
text | dad7bea8-5326-54d6-9b92-62680e186207 |  | textbox | Penetration Location
checkpoint-status | d5e9b433-86ee-4ea6-b7f2-50f39d4c1bbb |  | checkpoint | Centralise the casing and firestop the gap between the casing and wall with Kilargo intumscent sealant. Backing rod used as required to control sealant fill depth. Maximum annular gap between casing and wall 25mm
checkpoint-status | 66bee17c-4327-4b4c-bad2-d15eed526c42 |  | checkpoint | Approved fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint-status | 35312be9-d443-4852-8e85-ebe10f454766 |  | checkpoint | Casing perimeter is sealed with Approved intumescent sealant. No evidence of cracking.
checkpoint-status | eb47e223-94f6-46f3-8276-90a06d93c105 |  | checkpoint | O.7mm or greater Z275 Gal steel casing positioned centrally in penetration aperture
checkpoint-status | abefefea-3429-4517-94a9-5b4c4974bf15 |  | checkpoint | Duct Riser is connected to the casing usingSteel Screws or Steel Pop Rivet
checkpoint-status | 05d67ac8-4bea-4168-b0d3-6a2c2d7388e1 |  | checkpoint | 0.7mm (min) Z275 galvanised steel angles to all four sides, angle dimensions shall be continous and at least 2x the dimension of the gap between damper casing and penetrating element
checkpoint-status | 56443987-8b54-48a0-98bb-cbf42962faa8 |  | checkpoint | Ensure product and certification labels are in a prominent position for easy identification during subsequent maintenance inspections.
checkpoint-status | c1bb51c9-c436-4525-a2e0-1790e2e91218 |  | checkpoint | Access is provided to conveniently access fire damper for visual a inspections.
checkpoint-status | 492135f4-76d8-4fe0-ab4f-a2b1bb57021b |  | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint-status | 1339e08e-94c6-427e-8d85-d3bfecb2572b |  | checkpoint | Pictures attached
text | 72dfbe41-ca69-5bb9-85d5-8c6696dab081 |  | textbox | Notes/Additional Comments:
checkpoint-status | b715e4de-bba9-45c9-8f29-574f54dce773 |  | checkpoint | Signature (Contract/Subcontractor Assessor)
text | 261ead69-b1c8-53d7-a5fe-ff211774f916 |  | textbox | Date
checkpoint-status | 56c8d962-0bfd-451b-9026-db01d4c83c32 |  | checkpoint | Siganture (Builder Representative)
text | 7a6a5bdc-41e9-5ca6-9956-86a1ecf7e5f9 |  | textbox | Name
checklist-flat | 3fb3e3d1-b164-42ae-8d88-2d4c1da2cf01 |  | checklist | Ventilation |  |  |  |  | Yes | Ventilation Checklist | 712a8f0d-b56d-49d0-8610-ce1c003a0e65
checkpoint-status | 910fac18-134c-4006-b6db-206d049d4bb9 |  | checkpoint | Commissioned as per below (Pass once complete)
button | 90bab46b-f33a-596f-9d8a-99dd28ba7b22 |  | button | Fan has been tested and is operational | Pass Fail, N/A
button | 7e1fca0c-928d-5b5f-a561-50b555c18a7d |  | button | Adequate flow has been achieved in bedroom 1 | Pass Fail, N/A
button | 24dea72c-de6b-54b7-9ed5-a8f758de6053 |  | button | Adequate flow has been achieved in Ensuite | Pass Fail, N/A
button | e12a1c73-0e99-59be-a832-2d9d4baa9cb4 |  | button | Adequate flow has been achieved in Laundry | Pass Fail, N/A
checkpoint-status | bf7db893-3268-4ea8-a662-d37b6ac6d6a7 |  | checkpoint | Range Hood has been tested & is operational
button | d36cebfe-c0bb-5468-b3d9-07c0d7dd7381 |  | button | Adequate flow has been achieved Range Hood | Pass Fail, N/A
checkpoint-status | 824c5329-f81a-4906-ad6f-04c45871b249 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | ad9deea7-13b2-50de-880d-f8f5ef63eeab |  | textbox | Inspection Date
boolean | 5f54d9f8-5fe6-5ea2-af66-9436074faf04 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 6b811946-6907-5dc3-96cf-275235274e47 |  | tickbox | Builder Representative Sign Off
holdpoint | dcaad4ab-3fa3-4d9e-bda8-85970cdf0177 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-sectioned | 4a2472ce-3966-411c-a3be-67fb54ce2f06 |  | checklist | Pre-start Checklist |  |  |  |  | Yes | Pre-start Checklist | 8656cf67-af0d-4996-bb04-35c35de328e8
checkpoint-group | 3113dc1d-2bba-46d2-b8c3-a9f8c7c5e6b8 |  | section | Toolbox / Pre-Start Talks
checkpoint-status | ad4c0352-8ea1-4b43-9938-b45913d2f435 |  | checkpoint | Toolbox/Pre-Start Talks
label | e33fcdf5-8bfa-54f0-9a34-4c5b1b8ea1c8 |  | note | All Toolbox / Pre-start Talks undertaken on behalf of The Trustee for Broad Air Conditioning are recorded on this form and signed by participants.
label | 289793f9-3b52-5675-98c6-ff4116a8894a |  | note | All corrective actions noted on this form are implemented and signed by the nominated person. It is the responsibility of the Works Supervisor to ensure that all corrective actions are completed and reviewed for effectiveness.
text | 04ae855f-5719-5dff-8010-e6326974d823 |  | textbox | Workplace:
text | 7f955d23-4ae4-5b7f-9b3c-f0d99fad0503 |  | textbox | Subject of Talk:
text | b831d81e-bbf3-5e5a-9826-5d1f402d4706 |  | textbox | Presented by:
text | 39e162bb-1297-5bf2-a058-13ac811a83b3 |  | textbox | Duration:
text | dfdae6c1-da2b-58a1-9307-abfa8f8a4915 |  | textbox | Date:
checkpoint-no-status | cfeb8ff8-3bda-40ad-be01-0a991f536f93 |  | checkpoint | Persons Present
text | e44b9863-951c-59e2-bbd8-960d536f0c2e |  | textbox | Print Names:
label | 5499d2a0-6e71-5056-8c55-b6b162a08161 |  | note | Add Signatures Below
checkpoint-no-status | de14b46f-a9ee-42d5-a8b3-472dbbffebcd |  | checkpoint | Points Raised / Comments
text | cf0d726b-4701-5a2e-a75e-eeecd07d2a9f |  | textbox | Points Raised / Comments:
checkpoint-status | 885ec4a8-df08-4c18-be94-9ed80dba7c0b |  | checkpoint | Corrective Action
text | b463a8ec-de80-58cc-b48e-775b051085e0 |  | textbox | Action
text | 55ccd47e-d852-5532-a720-b781457fd4ff |  | textbox | Action by
label | 7535a75a-1232-533b-938a-23c513ef1906 |  | note | Action Complete
text | 9af3760b-0dba-5e09-980a-bb6580c7ba39 |  | textbox | Date
text | 5a5b1ed7-398e-50bf-b181-9ecaae2fe965 |  | textbox | Sign off
checkpoint-group | 1cb84d07-51e0-4a82-9909-1d2d07639482 |  | section | Plant & Equipment Pre-Start Checklist
checkpoint-status | b70f7baa-5b62-4a07-867e-e79a1d3eba43 |  | checkpoint | Plant & Equipment Pre-Start
label | 1d7db334-2c4c-5c83-b5d5-ed01fd43a75d |  | note | The Trustee for Broad Air Conditioning completes the following checklist prior to initial plant operation at the workplace.
checkpoint-no-status | 5d91d511-0431-4496-b9f1-f5be7152798e |  | checkpoint | Risk assessment
label | 9198da62-1b26-5a8b-a2ba-4aca345211d6 |  | note | A checklist should identify general hazards and associated risks relating to the use of the plant & equipment e.g. entanglement, crushing, striking, electrical or other. The checklist should then detail control measures to eliminate or minimise risk.
button | cbbd3994-9de5-5084-9c94-a919a48ecc81 |  | button | Check | Yes,No
checkpoint-no-status | 90a659a5-7d87-4ef7-9424-d7d7645eeebf |  | checkpoint | Log Book
label | 899596fc-99f6-5bfe-8d2e-16e1fa00c7d1 |  | note | A current log book recording daily safety Pre-start checks. These are subject to random inspection.
button | 89681b1a-5ee3-5aad-b0d4-0585dbe99ae6 |  | button | Check | Yes,No
checkpoint-no-status | 686dc412-021d-47cd-ae80-2e76c037d336 |  | checkpoint | Maintenance Reports
label | 7e24a062-60ee-5ad8-a040-e4b5e634a180 |  | note | Proof of ongoing maintenance, i.e. maintenance records. The records should note the most recent inspection and who conducted that inspection. It may also describe any repair work carried out on the plant. Most importantly, there should be no outstanding items noted for repairs.
button | 85a930cf-6a40-5f9f-adcf-9d63c0871613 |  | button | Check | Yes,No
checkpoint-no-status | 0c8defe9-34fd-4070-8428-0b65ffdbdf87 |  | checkpoint | Operator's Manual
label | abcff531-8312-544d-b1b3-081573e4fd56 |  | note | An operator's manual relevant to the item of plant and which is to be kept with the plant.
button | 03fb332c-7fab-5ad7-a7fc-a2ca7b821f10 |  | button | Check | Yes,No
checkpoint-no-status | 3f23f5bf-7219-4818-b539-7450511d1236 |  | checkpoint | Operator Certification
label | 2bbe9754-f6a1-5252-a0c6-03dc7530002f |  | note | Copy of operator's certification or licence to operate the plant. Where no statutory certification is required, evidence of competence by the operator in the use of the plant.
button | 15d64be0-859a-5ccf-a1d3-8948d0f27f30 |  | button | Check | Yes,No
checkpoint-no-status | e8f907b5-b378-4c0f-b544-d4dfdda7c11b |  | checkpoint | Plant Provider
text | 97c4a58e-999a-593a-a13c-5271d3afa4f2 |  | textbox | Name
text | 6a802d2c-d1e2-520f-88f6-22a4b98a734c |  | textbox | Date
label | 9990fee5-1ac0-5579-b75e-08a494fcdd25 |  | note | Signature
checkpoint-no-status | 40b300fd-6502-462d-83ab-cc3b672690bc |  | checkpoint | Plant Inspected
text | 1acbbcf5-f5ce-55f6-a76c-3ab1f16c8001 |  | textbox | Plant Type/Make
text | 6ac6fb84-cc66-56f8-b489-83014091f716 |  | textbox | Serial No.
text | 0a4f16f0-97ac-5914-aae9-9142c020e9eb |  | textbox | Company
checkpoint-no-status | 1a3556c8-8ef1-4d40-9a95-151f4da7a867 |  | checkpoint | Inspection Verified By
text | c244df65-0695-512e-a82e-c316cd40a35b |  | textbox | Name
text | 29668239-9761-595c-b28b-ae1fb45ad15b |  | textbox | Date
label | 8a7144b3-180c-5106-9977-a62905e31935 |  | note | Signature
checklist-flat | e7ddf6a9-172a-4076-9c9d-6b68c9ebecb4 |  | checklist | Common Area Fit-Off |  |  |  |  | Yes | Common Area Fit-Off Checklist | 8d4c59d5-cfdb-42d0-a25d-cd2bbb262fe5
checkpoint-status | 7fe503fd-733b-484f-8775-6850d7384a1f |  | checkpoint | Lobby supply grilles fitted
checkpoint-status | f4ce1256-1047-459a-a2b5-098d0f85dd0a |  | checkpoint | Lobby Smoke relief Air grille has been installed
checkpoint-status | ff17c268-afe4-4615-ae85-c063a64ed6fc |  | checkpoint | All fire dampers provided with an access panel as per mechanical drawing
checkpoint-status | 267275e8-5dca-424a-b6a7-e4fb2e0648ef |  | checkpoint | Garbage Room Grlille has been fitted
checkpoint-status | 7ee9538c-c498-41ef-acd5-abded1b02415 |  | checkpoint | All refrigeration pipes has been labelled as with approved label type
checkpoint-status | 3df4ecbb-64d8-4220-bf47-27e7e3eb4244 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
text | 6b60dd50-a0a7-57c9-b471-4850c49e357b |  | textbox | Inspection Date
boolean | a5a98393-647e-570a-91ad-db3c96c91260 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 8333ad9b-01b6-5020-8a8e-37adace0f428 |  | tickbox | Builder Representative Sign Off
holdpoint | 2c68b4c9-e30a-4df9-9e01-37bc779d1c5b |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 3ac5880a-2735-41bf-8aa5-57a8cf30b7ad |  | checklist | Duct Installation |  |  |  |  | Yes | Duct Installation Checklist | a7a533d5-b136-4627-8894-286d7716c731
checkpoint-no-status | be835f0d-9dd6-4c56-99ce-a7587291b69f |  | checkpoint | Riser
text | c00210bf-0ccd-5543-a9ec-0501fe207c47 |  | textbox | Riser ID
checkpoint-status | 788e8486-e6ec-44db-a26b-524b187a665a |  | checkpoint | Are drawings on site the latest issue
checkpoint-status | aa85d4cb-90aa-47e9-8746-c32bab372a1f |  | checkpoint | Are plant and equipment location correct
checkpoint-status | f6850078-2838-4222-b497-825ab11ad45c |  | checkpoint | Duct size and location correct
checkpoint-status | 74bc0542-0bf4-436b-afc5-08d095ecdc81 |  | checkpoint | Material and gauge correct
checkpoint-status | e2d4f6f7-e978-4583-aa7f-2bb2981fb298 |  | checkpoint | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method
checkpoint-status | db2a0c19-5aea-4096-b165-ed18fcb69d82 |  | checkpoint | Is correct jointing method being used
checkpoint-status | fcb5e1a7-af54-4f6c-af57-7539140b0990 |  | checkpoint | Are joints completed and cleated installed on flanges
checkpoint-status | 3ed1eae0-2b95-4cac-b40c-464c700f03df |  | checkpoint | Is correct joint sealant being used
checkpoint-status | 886f86e1-100e-4e0b-831b-add92f8f02bc |  | checkpoint | Is ductwork installation complete
checklist-sectioned | dd93e885-a942-4cf5-bc95-651c7395eb0f |  | checklist | Wall Closure |  |  |  |  | Yes | Wall Closure Checklist | bee2cf41-0cef-47ec-9746-cbec9573cff4
checkpoint-group | 500e53e5-0740-44c6-a95d-86980aee1428 |  | section | Air Conditioning
checkpoint-status | 8d8f0a28-8248-48d5-bd7c-af7755c3b977 |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | f1d58ee8-fc1b-505d-b5a6-d3c46a54b475 |  | textbox | Wall Closure Date
checkpoint-status | 4d587c9d-068d-4b4c-a002-440e1913f029 |  | checkpoint | FCU installed in right locaironan as per mechanical layout and the model number is in accordance with latest AC schdule
checkpoint-status | 5d2539f9-39b6-4e8d-8a89-0d6c19e74a7a |  | checkpoint | FCU installed as hight as possible with 5% slop tward the drain point
checkpoint-status | fa49607c-d208-44b3-85cd-d80d2a0c8a0f |  | checkpoint | Thermostat control cabling has been installed
checkpoint-status | 466442f0-91a6-435f-a8d4-d60e537bb718 |  | checkpoint | Thermostat location is correct as per RCP
checkpoint-status | e7b19c45-1082-4138-95f8-8d89e2cb9cce |  | checkpoint | Drains have been run to Tundish
checkpoint-status | b094405f-de12-4622-82db-6e5d1e1e3803 |  | checkpoint | Drains tested and witnessed by Broad Air
checkpoint-status | 68514478-a759-4782-b128-9385cd57cf60 |  | checkpoint | Pipe projecting the wall cavities in balconies have been sealed
checkpoint-status | 350cc256-1a68-48a9-9fbc-f152b34bbfc8 |  | checkpoint | All wiring including interconnection wiring and power from isolator to the condensers are roughed without defect
checkpoint-status | 7c464ba8-b5d7-4a50-9b9f-50d05c3810f8 |  | checkpoint | Refrigeration insulation is not damaged
checkpoint-status | f5b3b069-66cd-4544-b3d0-e7cc22be681c |  | checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation
checkpoint-status | ebda0acd-49d6-4770-b106-c4ae327a920f |  | checkpoint | Refrigeration pipes are run to condenser without being kinked or damaged
checkpoint-status | 55ba05d6-d9d4-405c-a03d-f5927a842631 |  | checkpoint | All refrigeration pipes, including bends where pass through stud wall are above the ceiling height (+2750mm Above Metre Mark)
checkpoint-status | e1cd37cf-2422-4867-b43a-fc502d2edf19 |  | checkpoint | Vent boxes are sealed
checkpoint-group | 308419a9-8f08-439d-a47a-8412b1027560 |  | section | Sign Off
checkpoint-status | 46d21d36-8b5c-464b-b8ac-d611af2816ad |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
boolean | b24ade79-4fee-5335-a494-8db2c016d9a3 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 4bb49df6-ebd7-5e03-b95e-b162778dd401 |  | tickbox | Builder Representative Sign Off
holdpoint | 0f0790b4-9b8b-442f-93a3-431b0b72a077 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-sectioned | 211d6a9c-6782-4672-8460-546c41157f1f |  | checklist | Ceiling Closure |  |  |  |  | Yes | Ceiling Closure Checklist | cabbe808-c506-4042-91c2-cb2f69397d44
checkpoint-group | e0620e84-ccf0-48a1-91ba-e4d8b7e2588b |  | section | Air-Conditioning
checkpoint-status | d5a7721d-1357-4165-b79b-6062f4497235 |  | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
text | 1b8001eb-898c-5ddc-b1c4-4d38284d19bc |  | textbox | Ceiling Closure Date
checkpoint-status | 4b025447-8c19-4290-a2e2-47361512df21 |  | checkpoint | Units all hung with isolation mounts and with 5% fall to drain point
checkpoint-status | f25a19d8-35f3-4621-8b5c-037e17d4f33e |  | checkpoint | Other services installed are not impeding access to fan coil
checkpoint-status | ac555c0e-2954-428f-8f0e-5d4cc20d28c8 |  | checkpoint | Wiring connections have been terminated to indoor unit electrical box
checkpoint-status | b79d4fbf-33d9-4d12-9569-1d6b773503c3 |  | checkpoint | Condensate drainage is in correct location and height
checkpoint-status | 91a0b356-8e52-4a7a-8950-967a9e00ca90 |  | checkpoint | Filter Track for return air have been installed at the back of unit
checkpoint-status | 1d9f6463-4d78-4cda-965c-b49bddbd6c1f |  | checkpoint | Zone damper instaled as per mechanical drawigns designated locations
checkpoint-status | ae25cdda-8dfe-4bcb-b1a9-7d0c6d69c0b2 |  | checkpoint | All flexible ducts connections to air terminlas and spigots have been air tight by using duct tape
checkpoint-status | fd3a8d69-7e1a-4441-8803-7084227e5b87 |  | checkpoint | All flexible ducts connections to air terminlas and spigots have been secured by using fixing ties/cables ties
checkpoint-status | 468f10e5-d0f1-41e6-a052-aed2b012b363 |  | checkpoint | Filters for return air have been installed at the back of unit
checkpoint-group | 66fff6f7-e28b-4adf-8527-42fd4d7331a0 |  | section | Ventilation
checkpoint-status | 361c7265-e5ee-4a29-9192-cbe02e18e700 |  | checkpoint | Inspection Date - Comment below
text | 765fb4cd-2e1d-5784-8194-661126645081 |  | textbox | Date of Inspection
checkpoint-status | 7399ff29-1afb-4af9-9bef-c6ef8bb69c3d |  | checkpoint | All Flex has been run to correct location
checkpoint-status | 397f6b71-582e-4851-9394-62be5f9fcc94 |  | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint-status | ccb4d609-2ea5-4922-b7c4-d3f5cfe27c42 |  | checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties
checkpoint-status | 05125b10-e8f3-4e1a-b75b-efd16914a0d3 |  | checkpoint | Filters for return air have been installed at the back of unit
checkpoint-status | 77d6b42d-33b9-4331-b1fc-892ea5264272 |  | checkpoint | PVC sleeves has been installed in wet area walls
checkpoint-status | 2811916c-9265-4983-8e77-062db9905875 |  | checkpoint | Vent boxes are installed in correct location as per RCP and SEALED
checkpoint-status | 0c30611b-f6e1-48e9-8351-411c25ad0b5a |  | checkpoint | PVC ducts have been hung and supported indicidually by using hanging straps
checkpoint-group | 04e2f837-8239-40e6-82fd-52f39626983d |  | section | Access Panels
checkpoint-status | ed081911-7bc7-41c6-ae53-cd9a12a55e10 |  | checkpoint | Inspection Date - Comment below
text | d3507ac4-61f3-5420-a7a2-6e149df7c463 |  | textbox | Date of Inspection
checkpoint-status | b059d3a3-6652-42ce-a9ee-a5c62b65f997 |  | checkpoint | Access Panel location has been marked on floor as per RCP
checkpoint-status | a4a6d775-cd0c-44ce-9c80-d916ae873b85 |  | checkpoint | Access panel location allows sufficient access equipment
checkpoint-status | 60692966-7d5e-4921-a8b9-b91a1e0ca5c5 |  | checkpoint | All other other services do not impede access
checkpoint-group | 8bdbb24d-a9ca-47f1-ba5f-6e027d1643c6 |  | section | Sign Off
checkpoint-status | ca21d6e2-1681-47e3-99ce-ba4353ba30ec |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
boolean | 49390dd0-9271-5f95-80a2-d68f183b1441 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | de131c4d-b500-5095-96c8-137c0871aafb |  | tickbox | Builder Representative Sign Off
holdpoint | 0395137d-9ae7-4230-886d-0c879ca8bc90 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | 4c58b660-bdb8-439a-981c-2fd920ede371 |  | checklist | Electrical Tagging Register |  |  |  |  | Yes | Electrical Tagging Register | e4f4184f-12b0-4adc-8631-b386106d775d
checkpoint-no-status | 715965a6-8f97-4c3b-9f2d-4999fe83f438 |  | checkpoint | Details
text | 0f2b1d84-45d0-58a0-9221-73ebd42822c2 |  | textbox | Company:
text | d0c3fd06-8473-51fe-80da-fc93922afee1 |  | textbox | Date:
checkpoint-no-status | b6e9aae3-e994-4201-8c0a-2c1a494956b8 |  | checkpoint | (1) Register
text | d114b4c4-4924-5de7-a0de-6b30ad756bcb |  | textbox | Number
text | c6c30d9c-1701-5d31-ad26-bfeca11a08c9 |  | textbox | Item
text | 797d8227-6987-57ad-be9a-de1526d70717 |  | textbox | Defections
text | 5c82d759-8c82-5fc6-a49e-4010c42e5cd6 |  | textbox | Date of Inspection
text | 0e3ce84a-b26a-5b7d-b151-6b003526f8fa |  | textbox | Date of next Inspection
text | 157a0ba8-27ff-5a5d-943f-219bab49273d |  | textbox | Inspection by Who: (Qualified Person)
checkpoint-no-status | 8a222cd6-03e0-4eaf-a7c2-d9f3143e24bd |  | checkpoint | (2) Register
text | 60d20e79-cdf1-575f-a8c3-9ef9d0555207 |  | textbox | Number
text | a953265e-fc42-5afd-8615-32ac1c62ea8e |  | textbox | Item
text | b3060e58-3d4e-53d4-a04d-76606e73c6d3 |  | textbox | Defections
text | a8ddad8a-a1cf-5f40-8a6e-3d2da49b4450 |  | textbox | Date of Inspection
text | d836028a-1c4f-5fe3-9048-245a32e424f2 |  | textbox | Date of next Inspection
text | 770cca61-b8f2-5e53-87f9-268d3d090e41 |  | textbox | Inspection by Who: (Qualified Person)
checkpoint-no-status | ed114bf7-018c-4f8b-8043-f4636e735a00 |  | checkpoint | (3) Register
text | 0bc40c3f-1d5e-5955-8990-fc4cb44252ae |  | textbox | Number
text | 1428df8f-8d45-5595-a061-4a64bfb712ce |  | textbox | Item
text | 657113c6-187d-5956-9093-4acdee55076e |  | textbox | Defections
text | a1a695e7-2e42-5a69-b1b4-1467b6c89323 |  | textbox | Date of Inspection
text | 8092724e-58fd-5751-8124-bb8ccc142852 |  | textbox | Date of next Inspection
text | b30213f7-1c80-5df6-8a54-47935935f8c6 |  | textbox | Inspection by Who: (Qualified Person)
checkpoint-no-status | 87ae7759-1347-46f9-a1b1-2501742aa939 |  | checkpoint | (4) Register
text | 10b19167-74e4-5385-aed3-12085fb3abae |  | textbox | Number
text | 4ef23d60-1158-597b-a4da-4b6955d1b8d5 |  | textbox | Item
text | 430d65f4-7f2b-5cdb-b91f-2414fbb245b8 |  | textbox | Defections
text | 6276defb-2c40-5bec-adf7-de8444b832ae |  | textbox | Date of Inspection
text | aae52bb5-53fa-527d-b1b7-cbcb462ebeba |  | textbox | Date of next Inspection
text | 558ae6da-621f-592c-83a4-822fe7568321 |  | textbox | Inspection by Who: (Qualified Person)
checkpoint-no-status | 7822d0c4-c5b1-428c-ac8b-319e865bf23b |  | checkpoint | (5) Register
text | 0f618e9f-efce-5c50-8006-9eb7cc78352b |  | textbox | Number
text | b1be0dfe-9513-5c26-bd05-5f362c9d1197 |  | textbox | Item
text | cf77e696-015c-51dd-b874-28e554b4e90f |  | textbox | Defections
text | d784eb40-8662-5372-b1bf-2ab1090acbd4 |  | textbox | Date of Inspection
text | 55e729f5-cf1c-5523-8698-c12af7c81f88 |  | textbox | Date of next Inspection
text | d6f482ca-ecce-5d93-91b7-65c9ede8637e |  | textbox | Inspection by Who: (Qualified Person)
checklist-flat | 11bad35b-6fc5-494a-ad73-cf53d0bc8225 |  | checklist | Core Hole |  |  |  |  | Yes | Core Hole Checklist | e5ca2542-f05f-4918-ab80-7661be6ebe72
checkpoint-status | 8d267ff7-dc29-4e05-a3da-aa2cfddeb732 |  | checkpoint | Penetration details have been captured
text | b4fc4691-19d1-542d-bdd5-f3d56f1e7160 |  | textbox | Penetration ID #1:
text | 25b14593-fd91-5e91-9fa3-bb1ded725052 |  | textbox | Penetration ID #2:
button | 8421b8ec-b0e0-5b05-8aa8-b49c6e649e9c |  | button | Number of Penetrations | 1, 2, 3, 4, 5
checkpoint-status | 06eaeb7c-c36d-45ba-b6f0-30289f4c47b3 |  | checkpoint | Core hole max 120mm with Firepex sealant filled to a depth of 60mm from either side of wall
checkpoint-status | 50ec4c12-f722-4bd6-9f4c-04cd3c5a77a5 |  | checkpoint | Cables to be tucked between insulation for a minimum of 300mm each side of the penetration
checkpoint-status | f73ca6b8-6c31-410e-befa-29ffd267e1ec |  | checkpoint | The penetration is labelled and photographic evidence is provided
checkpoint-status | 1a19cf92-6a3f-41de-8509-a53eaf2ef788 |  | checkpoint | Maximum services passing the penetration is not exceeding the following
boolean | 2f1f5e2f-bbc4-5264-9564-9beb8d9b6724 |  | tickbox | Two insulated copper pipes with up-to 20mm insulated thickness, with cable up-to 12mm | Pass Fail, N/A
boolean | b15cec5d-3dee-5f71-954d-6c55b72ece91 |  | tickbox | Maximum 1 set of flexible or rigid drain is passing the penetration | Pass Fail, N/A
boolean | 4c8bedf1-9914-58cb-a647-544954f0cde7 |  | tickbox | 20mm. Insulation is FR Amaflex or similar | Pass Fail, N/A
text | a51a5ae4-94f0-521d-b766-512f381aaac1 |  | textbox | Notes/Additional Comments
checkpoint-status | 12f0158f-e480-42ac-a80e-3d66f52065f4 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
boolean | ac9ae731-519d-5c41-98aa-5cccc8688820 |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | f23614ec-826b-5148-9200-cc18aa10cbeb |  | tickbox | Builder Representative Sign Off
holdpoint | 8c6be72a-0787-43b0-bc56-414b9fd13067 |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)
checklist-flat | ffc8a621-47bb-434a-81e2-ae899b74dcc5 |  | checklist | Common Area Rough In - General |  |  |  |  | Yes | Common Area Rough In Checklist - General | e75c9cee-ae38-4c9c-9388-59c9e0ecccbf
checkpoint-status | e0b64397-ab9e-4827-b34b-f901fe45cfe0 |  | checkpoint | Inspection Date - Comment below
text | 86a27d50-e8f5-51ad-ab9b-f7ec7d34cb23 |  | textbox | Date of Inspection
checkpoint-status | a017c073-f652-406e-8404-4d1659cb8b18 |  | checkpoint | Other services installed are not impeding access to fan coil
checkpoint-status | a0c15954-d181-4623-8783-564d41139915 |  | checkpoint | All Ductwork passing block walls are flushed and sealed
checkpoint-status | 3e428d6e-a62a-480b-ba89-51ca2a555deb |  | checkpoint | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed
checkpoint-status | 567d50fe-89cb-40e4-ba61-090e231d7fd2 |  | checkpoint | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed
checkpoint-status | 79c4940f-c94f-4b6c-9950-73838f84b52d |  | checkpoint | Refrigerant pipes passing through fire rarted walls are sealed at wall penetratiobn byu using approved material
checkpoint-status | b0d6f6e1-1b89-4f19-80f9-5b814b1aeda7 |  | checkpoint | Sign-Off Completed as per below (Pass once complete)
boolean | 821374d8-3d2b-55cd-ab60-d5089c40df2f |  | tickbox | Contract/Subcontractor Assessor Sign Off
boolean | 27197f75-da18-595e-8bed-d6f450f86ca8 |  | tickbox | Builder Representative Sign Off
holdpoint | e7584000-f42d-4305-8b72-80860f9d6f5a |  | signoff | Request Sign-Off(s) + Click to Add Signature(s)