## Table 1
WORK AREA: Rawhiti St Morningside |  |  | CONTRACT NAME: Morningside Flood Mitigation Pump Station |  |  | DESCRIPTION OF ACTIVITY: SP1 Pump Station Structural Works |  |  | Rev | Originator |  | Date | Approved |  | Date
[9 empty] | 0 | Casey Aubrey |  | 2025-01-22 | Grant Little
ITP No: 02
Item No. | ITEM | ACTIVITY TASK |  | ACCEPTANCE CRITERIA | FREQUENCY |  | Hold Point | CERTIFYING DOCUMENTATION, RECORD OR CHECKSHEET |  |  | VERIFICATION SIGN OFFS
[11 empty] | INTERNAL VERIFICATION AUTHORITY OR RESPONSIBILITY *Project Manager* |  |  | CRITICAL HOLD POINT AUTHORITY
1 | Footings (1) | Excavation |  | Visual Inspection | Upon completion of excavated footings. Confirm dimensions on IFC drawings |  | W | Survey confirmation
1 | Footings (2) | Subgrade |  | Geotech inspection minimum 100Kpa bearing capacity | Upon completion of excavated footings |  | H | Geotech inspection
2 | Footings | Concrete |  | 10 MPa | Check dispatch docket prior to pouring |  | H | Dispatch docket
3 | Foundation Slab (1) | Hardfill |  | 95% MDD | At finished level |  | H | Geotechnical engineers report
3 | Foundation Slab (2) | Geogrid and Bidum |  | Triaxial Geogrid Tensar TX170 Bidum A19 | Each EQ layer |  | W | As per manufacturers specifications
3 | Foundation Slab (3) | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
4 | Foundation Slab | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill Certs Reinforcing check sheet
5 | Foundation Slab | Concrete |  | 50.0MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
6 | Sloped Floor Slab | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
7 | Sloped Floor Slab | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill Certs Reinforcing check sheet
8 | Sloped Floor Slab | Concrete |  | 50.0 MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
9 | Install precast panels | Lifting/Rigging |  | Approved lift plan | Communicated/signed prior to any lifting |  | H | Implemented Lift Plan
10 | Cast insitu stitch joints (1) | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
10 | Cast insitu stitch joints (2) | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill certs Reinforcing check sheet
10 | Cast insitu stitch joints (3) | Joint seal |  | Visual inspection | Upon installation |  | W | Sikaswell S2 installed in accordance with manufacturers guidelines
10 | Cast insitu stitch joints (4) | Concrete |  | 50.0MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
11 | Cast insitu walls in Discharge basin (1) | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
11 | Cast insitu walls in Discharge basin (2) | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill Certs Reinforcing check sheet
11 | Cast insitu walls in Discharge basin (3) | Joint seal |  | Visual inspection | Upon installation |  | W | Sikaswell S2 installed in accordance with manufacturers guidelines
11 | Cast insitu walls in Discharge basin (4) | Concrete Fixings |  | Visual inspection | Each Fixing/drill hole |  | W | Drill holes cleaned with compressed air Anchors installed in accordance with manufacturers guidelines 8.8 galvanized threaded rod fixed with Hilti HY200 epoxy
11 | Cast insitu walls in Discharge basin (5) | Concrete |  | 50.0MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
12 | Cast insitu retention walls (1) | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
12 | Cast insitu retention walls (2) | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill Certs Reinforcing check sheet
12 | Cast insitu retention walls (3) | Concrete Fixings |  | Visual inspection | Each Fixing/drill hole |  | W | Drill holes cleaned with compressed air Anchors installed in accordance with manufacturers guidelines 8.8 galvanized threaded rod fixed with Hilti HY200 epoxy
12 | Cast insitu retention walls (4) | Concrete |  | 50.0MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
13 | Cast insitu roof slab (1) | Formwork |  | Visual Inspection | Throughout construction |  | W | Formwork check sheet
13 | Cast insitu roof slab (2) | Reinforcing |  | Visual Inspection | Throughout construction |  | W | Mill Certs Reinforcing check sheet
13 | Cast insitu roof slab (3) | Concrete |  | 50.0MPa Visual Inspection Crush test reports | Check dispatch docket prior to pouring |  | H | Concrete Pre-Pour Check sheet Mix from certified plant
INSPECTION & TEST PLAN
INSPECTION & TEST PLAN (ITP)
The ITP defines the required inspections during various stages of fabrication, construction and installation work. It is also a method of communicating these requirements to those doing the work and a verifying record that they have been carried out.
The ITP defines 2 different levels of inspection according to the following criteria:  Internal Verification: This inspection or verification activity is required internally by United Civil. A Designated Internal Authority- Project Manager, Supervisor, Foreman or other authorised person is determined for the given inspection point or verification activity. Where a signature required verification is notified by signing the designated check sheet.  Critical Hold Points: These are ONLY inspections required by the contract. It requires the Foreman/ Supervisor or Subcontractors Representative to notify the United Civil Project Manager that the hold point stage of inspection has been reached. Fabrication shall not proceed past this point unless the inspection has been carried out or approval to proceed is given in writing & signed by the Engineer’s Representative. The Engineer’s Representative shall sign the Check sheet. A Contract Hold Point is a contractual requirement. Where the Engineer’s Rep has not signed or for whatever reason cannot sign the Hold Point off the Project Manager must signify verification by the Engineer by other means such email sign off or other formal correspondence and note as such on the ITP.