## ITP Laydowns
LAYDOWNS ITP
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
United Civil Hold Point
| Survey & Setout | Verification of road alignment and layout | P,F,Attachment
|  | Alignment with approved IFC Drawings | United Civil Hold Point
| Site Clearing | Visual inspection of cleared area | P,F,Attachment
|  | Free from vegetation, debris, and obstructions | United Civil Hold Point
Material Procurement
| Material Approval | Approval of road materials (e.g., aggregates, subbase, basecourses | P,F,Attachment
|  | Compliance with KDC EES2011 specifications and standards and IFC Drawings | CHINT Hold Point
|  | Material Test Certificates - Gradings, CBR, Crushing Resistance | United Civil Hold Point
Construction - Subgrade
| Excavation/Grading | Inspect grading and levelling of subgrade | P,F,Attachment
|  | Uniform surface with proper slope and drainage | United Civil Hold Point
Visual Inspection and Measurements
Every Internal Road
| Compaction | Field density test | P,F,Attachment
|  | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m | United Civil Hold Point
Scalar Penetrometer test check sheet
For each section
Hold Point for United Civil
Subgrade Improvements (Where Required)
| Identify areas of Undercut | Identify areas of undercut and liaise with Client | P,F,Attachment
| Excavate Undercut | Excavate a minimum of 200mm in depth full width of the road | P,F,Attachment
Any free water has a path off the road in a controlled manor
Visual inspection of subgrade with Client
Undercut ITC completed
| Geotextile Installation | Visual inspection of geotextile placement for each section | P,F,Attachment
Correctly installed with proper overlap and anchorage
Delivery Dockets
| Backfill Undercut | Visual inspection of backfilled material | P,F,Attachment
Compaction to be static compaction only
Proof rolled with no obvious weaving or areas of instability
Construction - Base and Subbase
| Material Placement | Inspection of base and subbase layers | P,F,Attachment
Compliance with IFC Drawings and Material Specifications
100mm thickness of Gap40 and 50mm of Gap20
ITC Completed for Laydowns
| Compaction | Proof Roll | P,F,Attachment
|  | Visual Inspection of Compacted Base and Basecourse | United Civil Hold Point
Each Laydown
| Level and Alignment | Visual Inspection of Alignment | P,F,Attachment
|  | Compliance with design tolerances | United Civil Hold Point
Each Laydown
Construction - Surface Layer As Required
| Aggregate Placement | Inspect placement of aggregate layer | P,F,Attachment
Even distribution; meets design thickness of 50mm
ITC Completed for Laydowns
Each Laydown
| Surface Compaction | Proof Roll | P,F,Attachment
|  | Visual Inspection of compacted surface layer | United Civil Hold Point
Each Laydown
| Final Grading | Visual Inspection of final grading and surface finish | P,F,Attachment
|  | Smooth surface with proper slope for drainage | United Civil Hold Point
Each Laydown
Drainage - If Applicable
| Culverts and Drains | Visual Inspection of installation of culverts and drainage channels | P,F,Attachment
Installed as per design; no blockages
Water will flow without deviation
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive Visual Inspection of laydownsn & ensure laydowns are ready for use | P,F,Attachment
|  | Compliance with IFC drawings and specifications | CHINT Hold Point
|  | No defects | United Civil Hold Point
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the laydowns | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | CHINT Hold Point
|  | Drone Survey as-built for alignment and levels | United Civil Hold Point

## ITP Internal Roads
INTERNAL ROADS ITP
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
United Civil Hold Point
| Survey & Setout | Verification of road alignment and layout | P,F,Attachment
|  | Alignment with approved IFC Drawings | United Civil Hold Point
| Site Clearing | Visual inspection of cleared area | P,F,Attachment
|  | Free from vegetation, debris, and obstructions | United Civil Hold Point
Material Procurement
| Material Approval | Approval of road materials (e.g., aggregates, subbase, basecourses | P,F,Attachment
|  | Compliance with KDC EES2011 specifications and standards and IFC Drawings | CHINT Hold Point
|  | Material Test Certificates - Gradings, CBR, Crushing Resistance | United Civil Hold Point
Construction - Subgrade
| Excavation/Grading | Inspect grading and levelling of subgrade | P,F,Attachment
|  | Uniform surface with proper slope and drainage | United Civil Hold Point
Visual Inspection and Measurements
Every Internal Road
| Compaction | Field density test | P,F,Attachment
|  | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m | United Civil Hold Point
Scalar Penetrometer test check sheet
For each section
Hold Point for United Civil
Subgrade Improvements (Where Required)
| Identify areas of Undercut | Identify areas of undercut and liaise with Client | P,F,Attachment
| Excavate Undercut | Excavate a minimum of 200mm in depth full width of the road | P,F,Attachment
Any free water has a path off the road in a controlled manor
Visual inspection of subgrade with Client
Undercut ITC completed
| Geotextile & Geogrid Installation | Visual inspection of geotextile & Geogrids placement for each section | P,F,Attachment
Correctly installed with proper overlap and anchorage
Product Data Sheets
| Backfill Undercut | Visual inspection of backfilled material | P,F,Attachment
Compaction to be static compaction only
Proof rolled with no obvious weaving or areas of instability
Construction - Base and Subbase
| Material Placement | Inspection of base and subbase layers | P,F,Attachment
Compliance with IFC Drawings and Product Data Sheets with Material Specifications
100mm thickness of Gap40 and 50mm of Gap20
ITC Completed for Internal Roads
| Compaction | Proof Roll | P,F,Attachment
|  | Visual Inspection of Compacted Base and Basecourse | United Civil Hold Point
Each Road
| Level and Alignment | Visual Inspection of Alignment | P,F,Attachment
|  | Compliance with design tolerances | United Civil Hold Point
Each Road
Construction - Surface Layer
| Aggregate Placement | Inspect placement of aggregate layer | P,F,Attachment
Even distribution; meets design thickness of 50mm
ITC Completed for Internal Roads
Every section
| Surface Compaction | Proof Roll | P,F,Attachment
|  | Visual Inspection of compacted surface layer | United Civil Hold Point
Each Road
| Final Grading | Visual Inspection of final grading and surface finish | P,F,Attachment
|  | Smooth surface with proper slope for drainage | United Civil Hold Point
Each Road
Drainage
| Culverts and Drains | Visual Inspection of installation of culverts and drainage channels | P,F,Attachment
Installed as per design; no blockages
Water will flow without deviation
Reference Drainage ITP for Culverts
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive Visual Inspection of road construction & ensure roads are ready for use | P,F,Attachment
|  | Compliance with IFC drawings and specifications | CHINT Hold Point
|  | No defects | United Civil Hold Point
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the Internal Roads | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | CHINT Hold Point
|  | Drone Survey as-built for alignment and levels | United Civil Hold Point

## ITP Drainage
DRAINAGE ITP
Location
| Drainage Location | Location of Installed drainage line | Textbox
|  | Project drainage line reference (if applicable) | Textbox
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
Holdpoint United Civil
| Site Preparation | Visual inspection of cleared and levelled area | P,F,Attachment
Site free from debris, vegetation, and unevenness
| Survey and Marking | Verification of layout and drain alignment & grades | P,F,Attachment
Alignment with approved IFC drawings
| Material Approval | Review and approval of pipes, culverts, and other materials | P,F,Attachment
|  | Compliance with IFC drawings, specifications, KDC EES - S06 for accessways, and standards | Holdpoint United Civil
Material Test Certificates / Delivery Dockets attached
Construction - Excavation
| Excavation | Visual inspection and measurement | P,F,Attachment
Depth, dimensions, and cleanliness
Compliance with design drawings
| Soil Stability | Inspection of trench stability and shoring where necessary | P,F,Attachment
Stable and safe for pipe laying
Construction - Installation
| Pipe Placement | Visual Inspection of pipe placement, alignment, and bedding | P,F,Attachment
Compliance with approved IFC Drawings
| Joint Sealing | Inspection of joint sealing materials and application | P,F,Attachment
No leakage; proper sealing per specifications
| Backfilling | Inspection of backfill material and compaction | P,F,Attachment
|  | Proper compaction as per specification | Holdpoint United Civil
ITC for compaction
Construction - Testing
| Hydrostatic Test | Pressure testing of pipes for leakage | P,F,Attachment
|  | Meets pressure standards for type of line being tested | Holdpoint CHINT
|  | Test Report Completed | Holdpoint United Civil
| Flow Test | Visual Inspection to verify water flow through drains | P,F,Attachment
Smooth flow; no blockages
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive Visual Inspection of Stormwater and that it is ready for use | P,F,Attachment
|  | Comply with IFC Drawings / Specifications / KDC EES | Holdpoint CHINT
|  | No misalignment, defects, or debris | Holdpoint United Civil
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the Mechanical works for this Block | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | Holdpoint CHINT
|  | Complete and approved by client | Holdpoint United Civil

## ITP InverterFDNs
INVERTER FOUNDATIONS ITP
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
United Civil Hold Point
| Survey & Setout | Visual Inspection of Inverter Foundation layout | P,F,Attachment
|  | Alignment with approved drawings and site plan | United Civil Hold Point
| Site Clearing | Visual inspection of cleared area | P,F,Attachment
|  | Free from vegetation, debris, and obstructions | CHINT Hold Point
United Civil Hold Point
Material Procurement
| Review of Concrete, and Reinforcement steel | Compliance with IFC Drawings, Specifications and Standards | P,F,Attachment
|  | All reinforcing bars shall be Grade 300E or 500E to AS/NZS 4671 | CHINT Hold Point
|  | All concrete construction shall be in accordance with NZS3109 and IFC Drawings | United Civil Hold Point
Concrete shall be 40MPa Minimum Strength for precast elements or 30MPa for concrete poured insitu
Material Test Certificates / Dockets supplied for each delivery/Pour
Construction - Excavation
| Excavation & Footing Construction | Visual Inspection of each footing location | P,F,Attachment
|  | Check that depth & dimensions comply with IFC Drawings | United Civil Hold Point
Compacted hardfill pad under footing locations
Results Recorded on Clegg Hammer Checksheet for compaction of each footing
Construction - Concrete
| Formwork Installation | Visual inspection of formwork alignment and cleanliness | P,F,Attachment
Compliance with IFC drawings; no gaps or damage
Prepour Inspection completed for each pour
| Reinforcement Installation | Visual Inspection of steel bar placement, cover, and tying | P,F,Attachment
Compliance with bar bending schedule and specifications
Prepour Inspection / Inspection Report for each Pour
| Embedments | Positioning of anchor bolts or inserts | P,F,Attachment
As per approved IFC drawings
Dimensional check
Prepour Inspection / Inspection Report
| Concrete Mixing | Verify Certified Batching Plant is used | P,F,Attachment
Concrete Mix Delivery Records
Prepour Inspection / Inspection Report for each Pour
| Concrete Placement | Visual Inspection during pouring | P,F,Attachment
Proper compaction of poured concrete, no segregation
Each Pour
| Slump Test | Tests Taken in accordance with NZS3112.2 | P,F,Attachment
|  | Slump Test Report | United Civil Hold Point
Per Pour
| Concrete Strength | Compression test on cylinders taken in accordance with NZS3112.2 | P,F,Attachment
|  | Meets required strength of 40MPa for precast element or 30MPa for concrete poured insitu | United Civil Hold Point
Test Report
Post Construction
| Curing | Visual Inspection of curing of concrete | P,F,Attachment
| Foundation Alignment | Check position and alignment of foundation | P,F,Attachment
Dimensional checks & compliance with tolerance in drawings
Larger Block dimensions should be 3338mm x 600mm x 770mm
Small block dimensions should be 3338mm x 500mm x 725mm
| Surface Finish | Visual Inspection of surface for cracks, voids, and finish quality | P,F,Attachment
No visible defects or honeycombing
Every foundation
Inverter Container Installation
| Anchor Bracket Installation | Compliance with IFC Drawings, Specifications and Standards | P,F,Attachment
|  | Material Test Certificates / Dockets supplied for steel and galvanising | CHINT Hold Point
|  | Hold down bolts as per IFC Drawings and specifications | United Civil Hold Point
Epoxy to be as per IFC Drawings and specifications
Grout to be a minimum of 20mm thick under Anchor bracket plate
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive inspection of all elements relating to the Inverter Foundations | P,F,Attachment
|  | Compliance with IFC drawings and specifications | CHINT Hold Point
|  | Verify all Inverter Foundations meet design and functional requirements | United Civil Hold Point
Inverter Foundations ready for subsequent construction activities
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the Inverter Foundations | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | CHINT Hold Point
|  | Complete and approved by client | United Civil Hold Point