## Predrill
Pile Predrilling ITP
Location Details | Site Reference - Block |  | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14, 15, 16, 17, 18, 19
Preconstruction
| Design Review | Verification of Piling Design and Layout | P,F,Attachment
|  | Compliance with approved drawings and geotechnical report | CHINT Hold Point
|  | Design Approval Documentation | United Civil Hold Point
01_Maungaturoto_FS2V-23°-12_DUO_EX
02_Maungaturoto_FS2V-23°-12_DUO_EX
Schletter FS DUO - Fixed-tilt Installation Manual
Schletter Piling Instructions for Maungaturoto Solar Farm
| Material Approval | Approval of drilling fluids or stabilizers (if applicable) | P,F,Attachment
|  | Compliance with specifications | CHINT Hold Point
|  | Material Test Certificates / Delivery Dockets for each delivery | United Civil Hold Point
| Survey & Marking | Visual Inspection of marked drilling points | P,F,Attachment
|  | Visual Inspection of alignment and marking of pile locations | United Civil Hold Point
Alignment with approved layout drawings
| Equipment Verification | Visual Inspection of drilling equipment functionality and calibration | P,F,Attachment
Drilling equipment in good working condition
Visual Inspection of Plant Prestarts
Drilling Operations
| Drilling Alignment | Check verticality and alignment of drilled holes for every hole | P,F,Attachment
Hole should be within 3° of vertical in both North/South and East/West directions
Visual Inspection and Measurement
ITC Record Updated for every table
| Rock Penetration | Confirm penetration into rock (if applicable) | P,F,Attachment
Achieves specified embedment depth
Drilling Logs
| Spoil Removal | Spoil has been removed from each hole | P,F,Attachment
Hole is clean and ready for pile placement
Visual Inspection of the holes drilled
| Drilling Depth and Width | The minimum depth for all holes shall be 1.5m | P,F,Attachment
The minimum width for all holes shall be 300mm
ITC Record Updated for every table
| Predrill Hole Fill Media | Predrill hole media to be Stabilised Sand
Material Test Certificates/Delivery Dockets Attached
Post-Drilling Activities
| Cleaning and Preparation | Visual Inspection of cleanliness and condition of drilled holes | P,F,Attachment
Free from debris and loose material
| Stabilization | Verify stabilization measures (if required) | P,F,Attachment
Free from debris and loose material
| Survey Verification | Visual Inspection of resurvey alignment and location of drilled holes for piling | P,F,Attachment
Compliance with design tolerances
Maintenance and Monitoring
| Equipment Maintenance | Inspect and maintain drilling equipment Daily | P,F,Attachment
Proper functioning and safety compliance
Visual Inspection of daily maintenance records completed
| Drilled Holes | Monitor for collapse or deformation | P,F,Attachment
Holes maintain structural integrity
Post Construction & Handover
| Final Inspection & Walkthrough | Comprehensive Visual Inspection of all drilled holes | P,F,Attachment
|  | Compliance with approved design, function and specification requirements | CHINT Hold Point
|  | Verify readiness of drilled holes for piling | United Civil Hold Point
Area ready for subsequent construction activities
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the Predrilling works for this Block | P,F,Attachment
|  | Supply all documentation on completion of the Piling works for the block | CHINT Hold Point
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point

## Piling
Piling ITP
Location Details | Site Reference - Block |  | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14, 15, 16, 17, 18, 19
Preconstruction
| Design Review | Verification of Piling Design and Layout | P,F,Attachment
|  | Compliance with approved drawings and geotechnical report | CHINT Hold Point
|  | Design Approval Documentation | United Civil Hold Point
01_Maungaturoto_FS2V-23°-12_DUO_EX
02_Maungaturoto_FS2V-23°-12_DUO_EX
Schletter FS DUO - Fixed-tilt Installation Manual
Schletter Piling Instructions for Maungaturoto Solar Farm
In terms of the Piling Operation, in the event that early refusal is not observed, the Pile Testing done by Schletter prior to the construction phase is the extent of the Pile Testing done. Please refer to the Pile Testing Report provided for further details.
| Material Approval | Approval of Piles and Coating | P,F,Attachment
|  | Compliance with specifications (e.g., grade, dimensions, corrosion resistance) | CHINT Hold Point
Material Test Certificates
| Design Verification | Visual Inspection of Design | P,F,Attachment
|  | Client Review of ULS Testing and Geotechnical Reports | CHINT Hold Point
Pile Design Report/Drawings available
| Survey & Marking | Visual Inspection of alignment and marking of pile locations | P,F,Attachment
Alignment with approved IFC Drawings
| Ground Preparation | Visual Inspection of clearing and levelling of the site | P,F,Attachment
Free from debris, vegetation, and obstructions
| Equipment Verification | Inspect equipment and tools for installation | P,F,Attachment
Equipment is functional and calibrated
Equipment Records where applicable
Construction
| Pile Installation | Schletter FS Duo Fixed-tilt Installation Manual Schletter Piling Instructions for Maungaturoto Solar Farm Piles installed in the correct locations as per Schletter drawings and electronics Setout data All piles in every table are installed to the designs and every pile is checked for the following tolerances: North/South +/- 3° East/West +/- 3° Pile Twisting from axis +/- 5° Distance E/W +/- 100mm N/S +/- 50mm Reveal Height +/- 100mm Height difference foundation posts within one row +/- 50mm Piles have no damage deformation and in correct orientation Piling ITCs completed for each table | P,F,Attachment
United Civil Hold Point
| Pile Depth | Drive piles to marked embedment depth or until they reach the point of refusal Pile locations recorded and marked in Piling Maps Record Actual Pile embedment Depth and reveal heights in Data Tracker Pile refusal in accordance with Pile Installation Manual Piles cut and holes drilled and cold galvanising applied as per Schletter Installation Instructions Piles are installed to a minimum driven depth of 1.8m If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN. If Pile refusal is found at shallow depth of <1.5m consider predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with stabilised sands and perform one pile test per area to determine foundation strength. | P,F,Attachment
|  | Piling ITC's completed for each table | United Civil Hold Point
| Pile Predrilling | For every pile predrilled: Predrill pile holes to be drilled and cleaned out to a minimum of 1.5m deep and results recorded Predrill holes are a minimum of 300mm diameter and results recorded Pile Predrill holes are backfilled with an approved material | P,F,Attachment
|  | Predrilling ITC's completed for each table | United Civil Hold Point
| Cold Galvanisation Product Application | Review & approval of galvanisation product | P,F,Attachment
|  | Top 30mm of each pile must be sealed with an appropriate zinc coating as per Schletter FS Duo Installation Manual | United Civil Hold Point
Application of zinc protection follow paint manufacturers recommendations
Post Installation Testing
| Refusal at depth (1.5-1.7m or less) | If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN. If Pile refusal is found at shallow depth of <1.5m predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with an approved material and perform one pile test per area to determine foundation strength. | P,F,Attachment
|  | Hold Point for United Civil | United Civil Hold Point
Post Construction & Handover
| Final Inspection & Walkthrough | Comprehensive Visual Inspection of all installed piles | P,F,Attachment
|  | Compliance with approved design and specifications | CHINT Hold Point
|  | Verify all piles meet design and functional requirements | United Civil Hold Point
Area ready for subsequent construction activities
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the Piling works for this Block | P,F,Attachment
|  | Supply all documentation on completion of the Piling works for the block | CHINT Hold Point
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point

## Racking
Racking Installation ITP
Location Details
| Site Reference - Block |  | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14, 15, 16, 17, 18, 19
Preconstruction
| Design Review | Verification of Racking Design and Layout | P,F,Attachment
|  | Compliance with approved drawings and structural analysis | CHINT Hold Point
Design Approval Documentation
Schletter FS Duo - Fixed Tilt Installation Procedure
01_Maungaturoto_FS2V-23°-12_DUO_EX
02_Maungaturoto_FS2V-23°-12_DUO_EX
| Material Approval | Approval of Racking components (e.g., frames, bolts etc) | P,F,Attachment
|  | Compliance with material specifications & standards | CHINT Hold Point
Material Test Certificates
| Equipment Verification | Inspect equipment and tools for installation | P,F,Attachment
Equipment is functional and calibrated
Equipment Records where applicable
| Survey and Marking | Visually Inspect & Verify alignment and marking of racking locations | P,F,Attachment
Alignment with approved layout drawings
| Ground Preparation | Visual Inspection of clearing and levelling of the site | P,F,Attachment
Free from debris, vegetation, and obstructions
| Foundation Verification | Verify foundation conditions and readiness for racking | P,F,Attachment
|  | Foundation integrity meets specifications | CHINT Hold Point
|  | ITC completed for each table with piles installed | United Civil Hold Point
Racking Installation
| Frame Assembly | Inspect assembly of racking frames | P,F,Attachment
|  | Proper assembly as per Schletter FS Duo Installation Manual specifications | United Civil Hold Point
Visual Inspection of each frame
Post Installation Checks
| Mounting of Girders | Mechanical Installation ITC's are completed for Mounting of Girders Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut Torqued to value of +/- 5% of 56Nm and pass/fail recorded Each bolted connection shall be marked after torquing K&T to check 100%, United Civil to check 15%, CHINT to Check 5% | P,F,Attachment
| Girder to Foundation Post Step Check | Mechanical Installation ITC's are completed for Girder to Post Installation All Angles of the Girders to the horizontal are an angle of 23° +/- 1° K&T to check 100%, United Civil to check 15%, CHINT to check 5% | P,F,Attachment
| Purlin Connector Installation | Mechanical Installation ITC's completed for purlin connector installations Purlin Connector placed under purlin Purlin Connectors are screwed together with Four x M10x25 bolts for LC/LT Purlins Tightened to a torqued value of +/- 5% of 32Nm and pass/fail recorded Each bolted connection shall be marked after torquing K&T to check 100%, United Civil to check 15%, CHINT to check 5% | P,F,Attachment
| Purlin Mounting Checks | Purlins have been placed on top of the girders in correct direction FS Gen3 Girder Purlin connector bottom attached FS Flex Claw Installed K&T to check 100%, United Civil to check 15%, CHINT to check 5% | P,F,Attachment
| Bolted Connection of Girder and Purlin | Mechanical Installation ITC's are completed for each bolted connection M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm K&T to check 100%, United Civil to check 15%, CHINT 5% | P,F,Attachment
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive Visual Inspection of installed racking system | P,F,Attachment
|  | Compliance with approved design and specifications | CHINT Hold Point
United Civil Hold Point
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the Racking works for this Block | P,F,Attachment
|  | Supply all documentation on completion of the Racking works for the block | CHINT Hold Point
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point

## Modules
Module Installation ITP
Location Details
| Site Reference - Block |  | Dropdown, 1,2,3,4,5,6,7,8,9,10,11,12,13,14, 15, 16, 17, 18, 19
Preconstruction
| Design Review | Verification of Module layout and mounting details | P,F,Attachment
|  | Compliance with approved drawings and structural analysis | CHINT Hold Point
Design Approval Documentation
Schletter FS Duo - Fixed Tilt Installation Procedure
01_Maungaturoto_FS2V-23°-12_DUO_EX
02_Maungaturoto_FS2V-23°-12_DUO_EX
| Material Approval | Approval of Solar Module components and hardware | P,F,Attachment
|  | Compliance with material specifications (e.g. certifications & warranties) | CHINT Hold Point
Material Test Certificates
| Racking Inspection | Verify racking system readiness for module installation | P,F,Attachment
|  | Properly installed and inspected as per Racking Installation ITP | CHINT Hold Point
|  | Inspection of all tables | United Civil Hold Point
| Equipment Verification | Inspect equipment and tools for installation | P, F, Attachment
Equipment is functional and calibrated
Equipment Records where applicable
Construction
| Module Handling | Visual inspection of modules for damage during unloading | P,F,Attachment
No visible cracks, chips, or scratches
| Mounting Hardware | Verify assembly ITCs as per Schletter FS Duo - Fixed Tilt Installation Procedure and secure mounting of hardware | P,F,Attachment
As per manufacturer’s specifications within Schletter FS Duo Installation Manual
Visual Inspection
| Module Mounting | Check alignment, tilt angle, and secure attachment | P,F,Attachment
Compliance with approved layout and tolerances within Schletter FS Duo Installation Procedure
| Align Modules and Tighten Clamps | Check alignment and verticality of installed frames and modules Top panel to bottom panel to be between 5-10mm Horizontally between panels with module clamps: 22mm Panel clamps torqued to 15Nm and recorded as pass/fail in ITC's K&T to check 100%, United Civil to check 15%, CHINT to check 5% | P,F,Attachment
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive Visual Inspection of installed modules | P,F,Attachment
|  | Inspect modules for alignment and cleanliness | CHINT Hold Point
|  | No misalignment, defects, or debris | United Civil Hold Point
ITC's Completed for each table
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor | P,F,Attachment
| Documentation | On completion of the Module works for this Block | P,F,Attachment
|  | Supply all documentation on completion of the Module works for the block | CHINT Hold Point
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point