## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
e7811655-4ac8-435c-a2e5-e9a2188b6254 | checklist | ITP No.02 Construction Wiring, Installation, Test and Tag & Removal |  | ITP No.02 Construction Wiring, Installation, Test and Tag & Removal
45541fe7-21e6-4c6c-88f4-1e3b2dbc1ac1 | section | Details
ead7acfe-fad0-40cb-b8be-55a01136b64b | checkpoint | Area accessible & ready
ac095ee5-9616-4521-826e-00fe8bf08106 | checkpoint | Refer to temporary wiring setout plan
7beb53d5-1a6c-501d-aeb0-34055d2ab236 | note | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
f945e6cd-9a3a-4b6e-9931-2b0078a56bec | checkpoint | Fit off plug base and or powerpoint/isolator
e33b1775-81e2-4174-afec-1b587d8dfbdc | checkpoint | Install light fitting, exit/emg, power
7b318e8f-e9a7-404a-9a01-232017aa83c9 | checkpoint | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
0bfc877d-6cf6-473d-b7bd-2dfa94787c00 | checkpoint | Test & commission
d5ba0753-26ee-5429-a283-d34690566716 | note | Lodge non prescribed certificate of electrical safety
8b3305b7-033c-4069-8d49-966387aacd48 | checklist | ITP No.30 Structured Cabling Rough In |  | ITP No.30 Structured Cabling Rough In
2c6b81e2-01b5-41f3-b695-a713c74eaaed | section | Details
eb0c03d2-ec77-4b6f-aeca-1f2630bab400 | checkpoint-no-value | REFER APPROVED DRAWINGS AND SPECIFICATION.
bda9016c-ea6f-4baf-a20e-66de07219ab8 | checkpoint | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
bb64fd7f-c559-4783-bdaa-65e6d318107a | checkpoint | VERIFY CORRECT CABLE TYPE.
7f691069-b861-4277-8e9f-0e8a6caa89ff | checkpoint | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD
63ed6488-a0c7-4a70-9769-6250521cc8dd | checkpoint | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS, ENSURE VELCRO CABLE TIES ARE USED AS PER SPECIFICATION
a25a6f89-924d-45f7-a07e-31e7f97a421b | checkpoint | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
45e34aee-d406-4cf6-9ae8-9a6bb1ea9ad7 | checkpoint | ENSURE AREA IS LEFT CLEAN
0df36e0b-4465-45e6-8ea3-9290506e17e8 | checklist | ITR No.01 Installation of Temporary Power Board |  | ITR No.01 Installation of Temporary Power Board
3ce41de7-614f-4a7f-928b-fa334e68bfb3 | section | Details
55434a75-2365-43b2-89d8-4fb10c76a254 | checkpoint | Area accessible & ready
4d1e18b6-eacf-4c18-bc0a-3242627542f0 | checkpoint | Locate & fix into position, bolt temporary board down with at least 2 fixings
91fb040b-aa0f-4c08-b8fe-6ee385fa58c5 | checkpoint | Install submains cabling as appropriate eg: glands/tray/duct
22fbf98d-12ac-4805-a86e-a6a464fc81b1 | checkpoint | Install lugs and terminate
864fbd2b-988c-437b-aecb-c01845969ad0 | checkpoint | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
8c076dce-c51f-4547-988c-e67d9b8d3bbb | checkpoint | Clearly identify services
7672c7c2-ace6-450a-9103-74d58cf0c3bf | checkpoint | When ready to energise proceed in accordance with energisation procedure
c81901c6-f750-4eb0-8ae3-d37a57cf095e | checkpoint | Energise & record results on Vast RCD test sheet
994d441a-7353-40e8-8fc7-88719bec414c | checkpoint | Install laminated sign on face of temp board with floor plan and where the board is fed from
98a6d52a-2c1c-40da-ae93-13d653161b0e | checkpoint | Update Temporary Power Board register & save to project folder/design control/temp const.
ace7733f-1b34-5396-bbc0-b3abefa46a90 | note | Lodge non prescribed certificate of electrical safety
361da4d0-f745-5f22-a8ee-b3d5ee19904c | note | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
3e44430f-37a2-4ef2-b6fe-433d158b38aa | checklist | ITR No.06 In Slab Conduits |  | ITR No.06 In Slab Conduits
28c04bd6-e1bb-4e34-a2cb-ff46a4adf368 | section | Details
d73d34e9-187c-4095-a702-920ad175d0b8 | checkpoint | Determine origin and destination
4776ddb6-99e8-48b5-9e3f-ea663adecd04 | checkpoint | Mark out positions of junction boxes and penerations when necessary
c316c27b-fbdb-4cd5-9d5e-6bcf875a6aef | checkpoint | Install locating flange/conduit boxes
56c83a7e-ed97-4877-8839-34af1ca07e39 | checkpoint | Install tie down straps on conduit boxes
b76b43ca-782e-4562-b55f-cfd367df2f91 | checkpoint | Tie conduits securely at all joints and midpoints
94a813fd-497f-44f4-927b-54c5c6a5c7a5 | checkpoint | Observe conduits when concrete is being poured
b4ee7f16-a894-487a-b6f2-6fa213167adb | checklist | ITR No.07 Rough in Common areas |  | ITR No.07 Rough in Common areas
a885149f-57b6-4c75-a155-b07ece485d93 | section | Details
1d8e33d3-856b-4665-9672-0a4fc620ec7e | checkpoint | Area clear, tidy and accessible
ab00993e-b93b-4939-8c7a-32bdb8e4d9f8 | checkpoint | Rough in of all lighting circuits- inc Emg/Exits and sensors
27152614-b7a0-408f-bc57-6ef089889f9c | checkpoint | Rough in of all power circuits Fed from demolition Zone
f6865d5c-2349-4c09-a9a2-d286f1fc1fec | checkpoint | Rough in all lighting feeds and label on plan
bad69861-80d9-409c-85a3-7d7a7456554f | checkpoint | Rough in dynalite cabling on dedicated cat wire/donut
3596de37-e725-4da8-96ab-f7d2892fa74a | checkpoint | Rough in all power feeds and label on plan
58701260-505b-4098-942a-ad4acf7b48ed | checkpoint | Check for clashes with other services
4320aa35-845f-4e1b-8c28-a26afa64f91d | checkpoint | Level fire caulked by contractor
cbe0f56a-ccea-4f65-913e-f5c9617f047d | checkpoint | Ensure area is left clean
f4bda715-ca9a-41c1-864e-f5d30c7f6a90 | checklist | ITR No.09 Apartment Rough In of Electrical Services |  | ITR No.09 Apartment Rough In of Electrical Services
307dea51-275c-4cab-864f-d48af6cedbf2 | section | Details
6fe0f8b4-667e-4686-a0e5-8794e13b4ac6 | checkpoint | Area clear, tidy and accessible
ab1c0c1e-3caf-49cf-a5ca-a34232735194 | checkpoint | Rough in Hard Actives to all switches
4ffcfe20-be0d-451f-b221-38bdd0f06567 | checkpoint | Rough in of Switched Actives from switches to lights & Fit off Quick connects whilst on ladder
6033d68f-d86e-48ec-b8f1-143cc5ff6f1a | checkpoint | Rough in GPOs
018c8383-4076-4f1f-a1ca-276552ba5339 | checkpoint | Rough in of all kitchen general power (including island bench) above bench, fridge, microwave, rangehood
ed2e87a6-723b-4c7c-ac49-85dd1a376a4a | checkpoint | Rough in Cooktop and timer
462d96e2-a702-49fa-9ef7-5058ce673294 | checkpoint | Rough in kitchen led strip/figure8 from AP to swb
60493220-ddd8-4aa1-a03a-015574b24691 | checkpoint | Rough in all internal lights and pull through noggins
bbacd977-995c-4089-a5f5-59bf5588426e | checkpoint | Rough in bathroom pod to AP
c5096486-a3c5-4c01-88e0-e954e62d3407 | checkpoint | Rough in Tstat
72519c60-ae18-4d3e-9309-20c3813b6ba7 | checkpoint | Rough in data points to LBNCO hub and TV
360af797-3b7b-559a-acac-53fe2fc542a8 | note | Ensure Sub Mains are at Switchboard Location
60c31d9a-2276-490d-9603-397239069fde | checkpoint | Install switchboard & fit off
8e8aca47-c229-4a8f-a1a0-5a0b55c24343 | checkpoint | Install 150mm stud protecting sub main and earth with nut & bolt
dba3c6e8-c8d6-493a-b32d-b568ce15de62 | checkpoint | Install 2.5mm earth tags
23c1c65d-678e-4e31-9c28-9958cd2f4cd6 | checkpoint | Fire caulk sub main into DB and all cable entries
e4627e31-622b-4d06-9f5d-ee5d8c713d05 | checkpoint | Ensure all Quick Connects and juntions boxes are fit off
e716e11b-c6ad-45ac-b577-ffd2bc4b5514 | checkpoint | Ensure all cables are neat, taped to studs and easily accessible for cut out
ceafda00-be2e-4332-9703-ae6beee79c76 | checkpoint | Ensure all cables are clearly labelled at DB and at party walls
965704cd-fdb3-4146-b438-c68ba47ce2f8 | checkpoint | Ensure area is left clean
e56e1898-3a14-424b-b5f2-8d06ef9ff7e8 | checklist | ITR No.10 Hallway Rough In |  | ITR No.10 Hallway Rough In
76f19db0-c7c9-47e8-933d-c4585cb39052 | section | Details
18392db7-5487-489c-93eb-4f21a3157a03 | checkpoint | Area clear, tidy and accessible
311273d7-8abb-406c-886b-f97a0bb21ea6 | checkpoint | Mark out all public L+P in hallway
99333ea4-727b-4575-a2c2-2988fcd94634 | checkpoint | Rough in lighting, Emg/Exits and sensors
ab9de08a-6cbf-46db-8280-bc88ae69b01a | checkpoint | Rough in general power and cleaners power
36c6889c-4c22-41a7-93d8-2a2a332efff7 | checkpoint | Rough in comms/zigbee
e1a35788-8c70-4d96-8252-b7b829ed2491 | checkpoint | Rough in comms riser power
d131ad10-2ae1-4469-9296-17cbf9907a13 | checkpoint | Rough in dynalite cabling on dedicated cat wire/donut
8a0f1ab0-7362-454c-a9da-013bc59361f1 | checkpoint | Rough in all apartment sub mains from riser to apartment DBs and LABEL
7a2c6203-0357-4062-97b2-adb969d6bafc | checkpoint | Rough in any relevant comms/access control from one floor to another ( Backbone )
bf9cadf9-f07b-48cf-8a97-2c4345fec62f | checkpoint | Check for clashes with other services
280b0f65-f8b0-450f-8709-a5b39af3583a | checkpoint | Level fire caulked by contractor
9ae470fe-11eb-4529-9492-ff329c00fc1d | checkpoint | Fit off plug bases & quick connects
3443a08e-8476-4c0e-b172-f8c2bbe093f8 | checkpoint | Ensure area is left clean
636d8630-8cfa-4be2-97de-73fc74a0d94e | checklist | ITR No.11 Cable Tray Installation |  | ITR No.11 Cable Tray Installation
6fc0ea78-93db-4565-bf52-0e32bcd3fefa | section | Details
f3d09dc4-b56a-4ffe-a5b7-abcad2587ede | checkpoint | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES)
0ca0ca97-4706-4fa6-8ae5-212b0167ef81 | checkpoint | CONFIRM SIZE OF CABLE TRAY
2a08fcf1-f00f-40cf-a3d6-5976f6f0c524 | checkpoint | INSTALL FIXINGS AND SUPPORTS AS NEEDED
84e4baac-551d-4ab3-b2a8-44c8d32ac74e | checkpoint | INSTALL CABLE TRAY
a40f9b54-264f-4d32-bcc2-ceb3f05397ef | checkpoint | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS
480d2705-050f-41d1-857f-a132f91d1e7b | checklist | ITR No.13 Common Areas Cut Out |  | ITR No.13 Common Areas Cut Out
83c244fe-9b85-47f5-be3f-7ed51a6b949f | section | Details
c7bff1a2-2bc6-4127-bc33-5452449defb3 | checkpoint | Confirm sizes of all fittings prior to cut out
f3f6ac41-2257-4fdc-a5bb-bb277855f827 | checkpoint | Cut out all sensors,emg/exits, light fittings
66d39faa-2672-4a9e-b97e-aab1b09346e4 | checkpoint | Cut out all cleaners gpos
65965cc3-55a8-4025-9e18-60c89b814c86 | checkpoint | Cut out any CCTV
2fe3d78f-740d-428c-97b4-dde1c81f705a | checkpoint | Ensure electric strike cable is in press metal frame cut out
15f425fb-7789-4ec2-be3e-5439f1279a53 | checkpoint | Locate all cables
97cb5402-c41a-41d9-a6f6-923375a6d9f9 | checkpoint | Install Fire Boxes and hit all 4 tabs in
15eaf94d-cdbe-45bf-9288-5c4de0c4f755 | checkpoint | Ensure area is left clean
25d909aa-6bc3-4137-9ad9-9b2d905af3ab | checklist | ITR No.13 Hallway Cut Out |  | ITR No.13 Hallway Cut Out
ac150ddb-3e79-43e8-a9d9-93e247893aec | section | Details
0875b6ed-a4dc-4838-bf38-65394be0f2ab | checkpoint | Confirm sizes of all fittings prior to cut out
9fc12430-e611-46a1-aaaa-eb81668a8a06 | checkpoint | Cut out all sensors,emg/exits, light fittings
da4d61dd-2617-4f54-b73c-9dcc486debe5 | checkpoint | Cut out all cleaners gpos
c8174cb4-1fef-47f7-b111-305a814074c1 | checkpoint | Cut out any CCTV
9c63784d-7a61-4484-a61f-9f867bfbeaeb | checkpoint | Ensure electric strike cable is in press metal frame cut out
33a26382-b2e8-4910-b931-f716d78a665f | checkpoint | Locate all cables
7b181918-40a5-4cdf-a22e-42c60f452c0e | checkpoint | Install Fire Boxes and hit all 4 tabs in
18c09278-d7c1-4257-9438-46e530d98fbb | checkpoint | Ensure area is left clean
a748a4c6-40ae-4c57-9f87-7b333510d004 | checklist | ITR No.14 Apartment Cut Out |  | ITR No.14 Apartment Cut Out
9262bf18-1437-4956-9d05-221778110482 | section | Details
aee8a9c9-3520-4c95-97a2-20d7527608a7 | checkpoint | Refer to drawing to determine cable support route and check separation from data/comms services
d010e0e1-6160-4978-ba82-7e9ff42001f5 | checkpoint | Cut out for light fittings
deb889d7-8828-4675-bfc8-c6fc9a22e22b | checkpoint | Cut out kitchen to kitchen plan
295e7476-048b-4348-b7bf-a4a60cf80894 | checkpoint | Cut out switches & GPO’s
8de2214a-238c-48d1-95df-ad47ef29f45a | checkpoint | Ensure Wall light is in correct position
e12923dc-802d-4761-be3f-cc25a964d8cc | checkpoint | Ensure kitchen outlets are in correct position
ade99dca-dbb2-4349-92b2-d86ab7cf9c64 | checkpoint | Install Fire Boxes and hit all 4 tabs in
751484a7-a24f-4419-b294-843681fc6b74 | checkpoint | Ensure Fire caulking is completed by subcontractor
710a47eb-c4fb-4c26-987b-df0f9306b32e | checkpoint | Ensure area is left clean
0fa130ea-c636-45b6-9b9a-d1ffebd17d6a | checklist | ITR No.15 Basement Light & Power Fit Off |  | ITR No.15 Basement Light & Power Fit Off
33500b20-867b-4d7c-a15f-d3729f9d9e32 | section | Bakelite and Power
0750a2e0-1cd5-49dc-81cf-75a166b90c9b | checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
94290585-5194-43c1-b743-22fd3ec64a4e | checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
599a1a8a-d530-4732-821a-5ba068cf9dde | checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
c87e8bce-6aad-483e-9ab0-9075ef0902b8 | checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
e388bd95-23b7-43ec-9e74-ded5311b2fdd | checkpoint | FIT OFF FINAL APPLIANCES
09fe4ea3-7741-4d0c-9cde-ce53dc2a23b3 | checkpoint | COVER PLATES (IF REQUIRED)
201c8b48-d629-4f96-ad19-b4732dc0878e | checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
d200ce7c-990c-464e-8b3b-ffd3d8b8b393 | section | Light Fittings
015c43e3-e641-484c-b9e3-0fa269fe4d97 | checkpoint | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
5f71878e-f12d-4d41-b09f-c4f761af811f | checkpoint | LOCATIONS CO ORDINATE WITH OTHER SERVICES
72aa6ec8-ebb0-4da5-96ce-78eccadf289f | checkpoint | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
85497cb3-feb0-4d4f-83d7-b16e3a487cfc | checkpoint | PLUG IN OR FIT OFF LIGHT / PLUG BASE
35110057-4779-40b2-9b6d-1e7328e10f77 | checkpoint | INSTALL LIGHT FITTING
3d2f62df-b2ca-4c1d-96f6-edf7d81c9349 | checkpoint | INSTALL LAMPS AND DIFFUSER
a544ba07-df15-450e-8712-affe95c9cc5a | checkpoint | CLEAN FITTING, LAMP DIFFUSER
4b279351-e3f9-4d30-b77a-4f8bc62a7f16 | checklist | ITR No.16 Bakelite & Power Fit Off |  | ITR No.16 Bakelite & Power Fit Off
2257de63-9b5e-46ff-b8a2-dad6f6da20fa | section | Details
452313f0-5abd-4e82-981e-95a76768dc61 | checkpoint | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
e0fbc371-d121-4dd2-9cec-8763c6c62bb5 | checkpoint | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
833a0e0c-06f2-4d51-9b2d-40719757f9bc | checkpoint | FIT OFF AND FIX SWITCHES, WHERE MULTI GANG SWITCHES WITH MULTI CIRCUITS ARE INVOLVED USE SHROUDS ON EACH SWITCH. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
03d97bae-f848-4144-8e0f-28c1380cb718 | checkpoint | FITOFF DYNALITE AS PER SPECS WITH CORRECT LABELING/QR CODE ON PLANS
31b8bf8c-2cd3-4fdc-a16a-e494b2e335fa | checkpoint | FIT OFF AND FIX GPO’S, WHERE A GPO IS LOCATED WITHIN 150mm OF A METAL STUD, USE SHROUD. EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
ca960e27-07f3-400a-b92f-cf386233299d | checkpoint | FIT OFF FINAL APPLIANCES
2a0b8b0e-4dc2-4831-bd94-a34f9a73a231 | checkpoint | COVER PLATES (IF REQUIRED)
5eecd81f-8166-4fb8-ab40-507bc0525aaa | checkpoint | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
30c0b305-6563-4fc4-82a9-be2d9613a677 | checklist | ITR No.18 Hallway - Fit Off Electrical |  | ITR No.18 Hallway - Fit Off Electrical
60d6abaa-e6fb-4b02-b485-efc0ca0d97c8 | section | Details
8e789823-3959-47f1-9825-7c46229e9f9a | checkpoint | Area clear, tidy and accessible
a99400a3-7a86-4c94-9252-cdb0f695a319 | checkpoint | Fit off all Lights
b7531213-4f4e-46e1-aa58-a965b6b1dcdf | checkpoint | Fit off all Sensors and SET TIME TO MINIMUM
5084f441-eff9-4e3f-97c9-8193dc34fdc1 | checkpoint | Fit off all EX/EMG’s
5b69daee-54f1-4e16-b734-27f13cfce047 | checkpoint | Label all EX/EMG’s as per plan number
34690583-9872-455c-8240-460730366b53 | checkpoint | Fit off all Cleaners GPOs
3730448b-5da9-4bce-86f8-6400ef345281 | checkpoint | Fit off all Comms Riser GPOs
0ede7f0c-112f-4c2f-b4f6-1b307f3a7adf | checkpoint | Fit off water meter GPOs
0829a505-3535-4cb2-8ddb-f78b3307d0c9 | checkpoint | Ensure area is left clean
de1fe711-6cd9-4fe2-a5e2-56fac2024377 | checklist | ITR No.19 Apartment - Electrical Fit Off |  | ITR No.19 Apartment - Electrical Fit Off
c897ae34-fb87-4084-9b99-7ead339b7ae0 | section | Details
ae9bd504-dfc8-464d-bfec-d32cb29bc5ad | checkpoint | Area clear, tidy and accessible
492f9633-79f3-4479-a86b-c2d4d0e67aaf | checkpoint | Fit Off Wall Lights
7565e543-6ee6-4698-a07d-f1b476e50304 | checkpoint | Fit off joinery GPO's & install cover plates.
bf87063d-da56-460a-aa48-a7a859a817e2 | checkpoint | Fit off all GPOs - Install cover plates & switches where required
52583fc0-499a-4499-8e29-7ff527fa90ea | checkpoint | Fit off light switches
20a804d1-e9fe-4362-ad71-939ab49a08db | checkpoint | Fit Off Data Points
33dd2dd5-050c-49b0-81a9-6ec2a9011d34 | checkpoint | Fit off Tstat
607de866-49aa-444b-b2f0-678117a3258c | checkpoint | Fit Off Kitchen LED Strip
01356903-0099-4bea-8c6f-97e9598ac0b2 | checkpoint | Fire caulk sub main into DB and all cable entries
87bbe912-9b65-4f28-8728-eef64131a96a | checkpoint | Install and fitoff DB
c3f6751c-0025-44e6-af40-67451d06a7a8 | checkpoint | Install Cooktop
ee7f3cf4-4d75-4712-ae5b-cf4be0f85f5c | checkpoint | Ensure area is left clean
37d9e25b-d91c-43b1-8f17-a10a382ffa2c | checklist | ITR No.20 Mains and Sub Mains |  | ITR No.20 Mains and Sub Mains
ad7eb086-328d-4096-817b-ca9e07763a85 | section | Details
af00e744-3fa6-453f-a89a-9c7ff7ca131e | checkpoint | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
316107ed-3869-40ca-b4cd-789d8e9c9a69 | checkpoint | Confirm length of cable
48d1c210-60e0-4ce1-b851-ce5d5c6106ae | checkpoint | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
0fe16316-43bf-5591-b355-21a26b6ecb80 | note | Any cable not terminated immediately must have the end taped covering the bare copper
40f4bf3f-7033-45d5-8d07-8202f8997afe | checkpoint | Trefoil (refer to details on back for all options) cables and tie cables to support system
f2df20af-ccdc-44b2-95ee-38d18f23c30d | checkpoint | Check cable requirements for cable identification and install
b1658f8c-ecff-4705-9177-444a57956403 | checklist | ITR No.25 Commissioning |  | ITR No.25 Commissioning
258bcf81-5601-448a-9792-87f018f799ab | section | Details
7a90a80d-d589-49ca-ade1-cf073b2861af | checkpoint | Prior to energising all personnel involved to be inducted into energisation procedure and all steps undertaken to ensure compliance with this procedure
ae89a176-9e65-56b5-839e-4bfe513d6a69 | note | Obtain fresh copies of current light and power drawings and mark up any changes from the working drawings
aeeba15c-9c3c-5cef-81ec-314688e88e33 | note | Obtain copy of distribution board schedule to mark up any additions or deletions found whilst commissioning
4f1eabaf-faf9-5053-9bdd-46bc7ce58047 | note | Visually Check all items
955cce56-60b7-46cb-a557-083226039dc5 | checkpoint | Dead Testing
6e8088e5-233a-4a3f-97ee-9af290f7594c | checkpoint | Live Test
ad100108-1649-53d2-ad68-cce30d2c8fcb | textbox | Record Metrel Results and log
12931fc5-222b-4986-b38a-186a17c245c0 | checkpoint | Check operation of all sensors (individually on minimum time setting )
f0da7723-6f5a-4c91-9dcc-530bf45a2614 | checkpoint | Check sensors are set to specified time and lux
70359fef-6bbf-4bf9-8086-d772dbad9062 | checkpoint | Fit Cover Plates to GPOs & Switches (take photos)
bf1a35a0-ec9d-4548-a7a6-f43f7a9b4328 | checkpoint | Install switchboard cover / label (take photos)
9097f25f-85de-42dd-b9a8-6b66088c0aed | checkpoint | Ensure area is left clean
b9119765-c107-445e-bd54-7c221337afed | checklist | ITR No.29 Decommission Temporary Power Board |  | ITR No.29 Decommission Temporary Power Board
61d9d962-199c-45b6-80bc-4c3c6c02f07a | section | Details
ad9d3e70-961a-4090-846e-3b10b68568d6 | checkpoint | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
6ffc2ecb-8de1-5867-a5a5-6e0ca119b1cf | note | De-commission form issued to builder, 48 hours notice to be given
bd5de5e0-58de-44cd-982f-da2b93a5f80f | checkpoint | Sign off builders checklist
af873660-4ab9-46e1-85ed-a0d00721e020 | checkpoint | Safety Committee Inspection
f6ecaa57-c852-4938-8307-2d7e1048ecda | checkpoint | Final approval to be given by builder
71dcd36c-418a-4f45-9672-630f5dd3ef79 | checkpoint | Perform voltage test to ensure power supply has been isolated
39ea5004-7558-4cf5-b33a-47b69c915c14 | checkpoint | Disconnect supply cables
46475a49-e9b3-4b0e-a981-3458023fe1cc | checkpoint | Fire sealing of penetrations
9e937294-e63a-4a84-a07b-a6d5ebdc9a99 | checkpoint | Remove temporary board
c7f63da7-1fa7-4622-a7e5-14c32d3c2d59 | checkpoint | Update temporary power board register