## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP-224 Nursecall |  |  |  |  | Yes | ITP-224 Nursecall | 022c927a-a980-4cb8-b65b-e54a30452971
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Please attach marked up drawing
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status |  |  | checkpoint | Prior to installation submit numbered shop drawings for review to the satisfaction of services engineer
checkpoint-group |  |  | section | Cabling Rough-In
checkpoint-status |  |  | checkpoint | Ensure latest services & co-ordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-group |  |  | section | Field End Nurse Call Fit-off
checkpoint-status |  |  | checkpoint | Ensure that all Field End Cabling has been labelled, terminated to manufactures requirements and is level to other services
checkpoint-group |  |  | section | Head End Nurse Call Fit-off
checkpoint-status |  |  | checkpoint | Ensure that cables are dressed neatly and loomed into their final location for termination
checkpoint-status |  |  | checkpoint | Ensure that all Head End Cabling has been labelled, terminated to manufactures requirements and is carried out to Manufactures Shop Drawings
checkpoint-group |  |  | section | Programming
checkpoint-status |  |  | checkpoint | Ensure that all Nurse Call stations are addressed correctly as per latest drawings and Align with the monitor associated to them
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate record
checklist-sectioned |  |  | checklist | ITP-212 Testing and Commissioning |  |  |  |  | Yes | ITP-212 Testing and Commissioning | 0490c0eb-a1f8-4977-9391-02cf0e4a256e
checkpoint-group |  |  | section | Safety
checkpoint-status |  |  | checkpoint | Project Risk identification and management register.
checkpoint-status |  |  | checkpoint | Identify / acknowledge and manage risks involved with this task.
label | cf9ce8ab-657b-507a-979f-cf5a7ebc26e2 |  | note | Review the project risk register.
checkpoint-status |  |  | checkpoint | Ensure that all workers have reviewed appropriate SWMS and have signed onto SWMS
checkpoint-status |  |  | checkpoint | Review Project HSEQ management plan - these works must be fully compliant, site specific safety manual and SWMS have been submitted and accepted by the Principal Contractor
checkpoint-status |  |  | checkpoint | Review Fredon Procedures
label | e3960948-a54c-502b-b937-48df4211f91f |  | note | HSP-055 Testing an Electrical Installation
label | e494163c-7009-58ee-b32a-1c93cd84f4f2 |  | note | HSP-037 Live Work Policy Witness VOC
label | 482e9315-13c1-5ecf-8c8d-4cdaebd4e02a |  | note | VIC Electrical Safety Regulation 2013
checkpoint-status |  |  | checkpoint | All Fredon Electrical personnel undertaking these works are qualified to carry out these works, and are trained, and competent in the use of all equipment and plant required to carry out these works.
checkpoint-status |  |  | checkpoint | Fredon Electrical Testing and Fault Finding Training & VOC in previous 12 months
checkpoint-status |  |  | checkpoint | Ensure workers whom are performing 'energised' testing hold current CPR and switchboard rescue certificate.
label | 033b9c25-ebd9-5de6-abc8-a10e23dfccc3 |  | note | These are to be renewed annually. Witness
checkpoint-group |  |  | section | Project Specific Scope Requirements
checkpoint-status |  |  | checkpoint | Review project specific documentation to ensure all relevant information is available any additional / supplementary testing requirements must be included within this ITP
label | 0098739b-572f-5f0d-afbd-2edc3a12277b |  | note | ITCs for predecessor works complete
label | 3df7f0ce-8c60-5cb6-801d-41d06c2d0957 |  | note | ITC - Switchboard pre-energisation
label | 14151ab8-d17e-58f3-ae46-030f024fa065 |  | note | ITC - Light & Power Fit off
label | 8ada682e-7d76-53da-b1f6-7022a9e1bec3 |  | note | As installed drawings complete Witness
checkpoint-group |  |  | section | Before Starting
checkpoint-status |  |  | checkpoint | Correct test equipment to complete the task
label | 940807dc-3496-5071-aaf6-7fcd2d7378fb |  | note | Insulation resistance tester - Ohmmeter;
label | d31f17c4-3c14-5a75-aa5f-b1e94f159ebe |  | note | Voltage indicator (e.g. lamp, neon, LED device or meter);
label | 95cd3ebc-e6c1-59d5-bf2c-454b252ce1ce |  | note | Suitable probes;
label | b4e99f59-1fb5-59b3-b6fb-c421fe93e28f |  | note | Trailing leads;
label | 1fb77fe0-8d3f-5de4-bf8d-cc1da0c5effe |  | note | A range of resistors of known values;
label | 12df2754-d63c-5534-8e88-2af39243ad1d |  | note | A suitable instrument for measuring fault-loop impedance; and
label | 2aacf255-0e02-5301-8cae-2a6be67f266c |  | note | A suitable instrument or device for checking the operation of a RCD.
label | b4387981-b838-5605-9be5-158809bd40ea |  | note | Phase rotation confirmation instrument Witness
checkpoint-status |  |  | checkpoint | The test equipment / multimeters etc must display current calibration information
checkpoint-status |  |  | checkpoint | Ensure the electrician who is to perform the works has been trained on correct operation of test equipment - multimeters
checkpoint-status |  |  | checkpoint | Ensure the electrician who is performing the works is familiar with the installation - If required walk them through the proposed work zone
checkpoint-status |  |  | checkpoint | Ensure the electrician performing the works has the latest redline marks up available and can easily identify circuit arrangements
label | 73a09a43-c37a-5e30-9773-ea4016d7d6fb |  | note | Complete ITC-212.1 / ITC-212.2 Ensure the electrician who is performing the works understands the requirement to complete the ITC [Inspection & Testing Checklist] associated with these works and that these works must be completed in accordance with Statutory requirements. The electrician must enter their personal electrical licence number and acknowledge compliance via signature on ITC as works are completed. Review ITC-212.1 / ITC-212.2
label | 9ed1a69a-ba15-5a62-b29f-23e5db15ec02 |  | note | Electrical Certificate of Testing and Compliance It is the Project managers responsibility to review complete ITC,s and compile the project testing / commissioning dossier for final review. The project manager shall then complete the certificate of electrical compliance and testing - This document must be presented to Fredon QTP [Qualified Technical Person] for project sign off. Certificate of Compliance
checkpoint-group |  |  | section | De-Energised Testing
checkpoint-status |  |  | checkpoint | Visual Inspection
label | e1a8b442-6157-5414-8c67-1762be317766 |  | note | A visual inspection shall be made when work on an electrical installation has been completed in order to verify that the work complies with the requirements of AS/NZS 3000. The visual inspection shall be carried out before, or in association with testing, and should where practicable be made before the relevant part of the electrical installation is placed in service.
label | 0352e6f3-1472-58ec-9f31-09df827cd8ef |  | note | Where the visual inspection of a part of the electrical installation is not practicable at the completion of the work, e.g. not accessible due to enclosure in the building structure, consideration should be given to inspecting that part during the course of the installation.
label | 1f061e61-6ca4-57bf-93db-308809591f05 |  | note | Refer to AS 3017 section 2 for further detail.
label | 61bff559-b1ed-5a39-9b1a-746c7b13109c |  | note | Complete ITC-212.1 / ITC-212.2
label | b7df7800-2b08-53c5-82cf-bd1c0a788f1c |  | note | AS 3017:2007 Section 2
checkpoint-status |  |  | checkpoint | Earth Continuity Resistance
label | 6885804c-b653-5bc8-a444-9bf6de068f65 |  | note | Earth continuity and resistance tests are necessary to ensure that the earthing system has been installed in an appropriate manner and the resistance of the protective earthing conductor is low enough to permit the passage of sufficient current to cause circuit protective devices to operate if there is a fault between live parts and exposed conductive parts.
label | 5e148d46-9fb3-5def-b3d5-c1cae5b8c593 |  | note | NOTE: This may include cable tray, Stainless kitchens etc
label | 2b3987a6-46c4-553f-921e-ad59df92bbdb |  | note | Refer to AS 3017 section 3.1 for further detail.
label | 9ade59b6-165f-55b9-b58d-c62b5f586249 |  | note | Complete ITC-212.3
label | a4e69da2-ab58-5ddd-80bc-ebee50ada249 |  | note | Earth continuity and resistance tests are required for Communications Cabinets with shielded and sensitive equipment requires to have a clean direct earth.
label | 77d2009c-5916-5870-8599-08e2dab6bccb |  | note | Refer to AS S009 Pass Less than .5Ω
label | ad2fbbe0-0e59-52df-b8c7-a38e13409cce |  | note | Complete ITC-212.3
label | f51d88ec-c671-56ff-9866-8496b8d28335 |  | note | Note: The continuity of protective earthing conductors may also be verified by measuring the earth fault-loop impedance of the circuit.
label | d0e57928-d9d6-58fa-9251-9bac3f619a15 |  | note | See 3.6.4.2 refer table 3.2 for values Complete ITC-212.1 / ITC-212.2
label | cf62b8a2-9491-5315-9170-eba7d23af99e |  | note | AS 3017:2007
label | c3fe9668-0c94-546d-92e1-b8fa1d6db30c |  | note | Section 3.1
label | a490e7f3-8d23-56ec-8494-ec8a96fb5835 |  | note | AS S009
checkpoint-status |  |  | checkpoint | Insulation Resistance
label | b7cb7472-83bd-5095-9c57-dad090ea7db0 |  | note | Insulation resistance tests are necessary to ensure that the insulation resistance between all live conductors and earth or, as the case may be, all live parts and earth is adequate to ensure the integrity of the insulation. This is to prevent:
label | e481aa75-c43e-5198-864f-4885ca1560e2 |  | note | (a) Electric shock hazards from inadvertent contact;
label | 04317df3-4c61-5f55-b8d8-92cf6b4a0b66 |  | note | (b) Fire hazards from short-circuits; and
label | d3b91c97-671a-5339-a651-f8fae9b5cfee |  | note | (c) Equipment damage.
label | e53011c0-1feb-537a-bd1e-deaaeb9d1d5e |  | note | In addition, insulation resistance tests between all conductors are necessary for consumers mains and sub mains to minimise potential for insulation breakdown, injury or property damage due to failure of such conductors. The integrity of the insulation is stressed by applying a direct current at 500 V, or 212 V for equipment described in 3.2.4(e) which cannot be isolated. The insulation resistance between:
label | 160be4aa-08bb-5c1a-82ce-602d56543e7d |  | note | (a) the conductors of consumers mains and sub mains; &
label | 6fcf271d-1207-5fee-b9ff-a77be1a334aa |  | note | (b) live and earthed parts of an electrical installation, or parts thereof, including consumers mains and submains shall be not less than 1 MΩ.
label | 8a74dcda-e201-5dd3-b648-c16596cade8c |  | note | Refer to AS3017 section 3.2 for further detail
label | 70b9ea75-0f00-5125-b619-52ac40d595af |  | note | Complete ITC-212.1 / ITC-212.2
label | 5b32cec3-31ac-5be2-96e9-1bbab15a9593 |  | note | Note - If luminaires have been installed - all switching devices should be 'on' - Test only between 'live' conductors and earth.
label | 28748890-6511-5216-bac4-26bb67063a18 |  | note | Note - If luminaires have not been installed - all switching devices should be 'on' - Test between all conductors and earth.
label | d47a7d31-f3e5-5dfb-a4d2-cb62f4385846 |  | note | AS 3017:2007 Section 3.2
checkpoint-status |  |  | checkpoint | Polarity
label | 7ed0d70a-0406-5dd6-87f3-4bd5340eb11f |  | note | Polarity testing is necessary to ensure that no shock hazard results from the incorrect connection of active, neutral and earthing conductors. This testing is to ensure:
label | 26b80aee-6c24-5631-b725-411d9b7dfd1f |  | note | (a) Active and neutral conductors of the consumers mains or submains are not transposed resulting in the electrical installation earthing system becoming energised;
label | 0373519d-4a34-5d29-8e16-c1cd20909f55 |  | note | (b) There are no combinations of incorrect active, neutral and earthing conductor connections
label | 4033394a-5280-5558-911d-6df16f2ca7dd |  | note | resulting in the exposed conductive parts of the electrical installation becoming energised; and
label | 4bf9716c-bdcd-5b37-9b76-0406e55a6631 |  | note | (c) Switches do not operate in neutral conductors, resulting in parts of appli
label | 0e0676b8-f2e4-5f0a-8da1-e30c588bf146 |  | note | Requirements
label | c0b4164d-f88a-5d35-acc4-fb85d9144d4b |  | note | (a) Every single-pole switch or protective device shall operate in the active conductor of the circuit in which it is connected;
label | 26b92714-df86-5f77-b03e-13b8bcb5a719 |  | note | (b) A switch or protective device of a multi-phase circuit, other than some types of motor overload protective devices, shall operate in all active conductors of the circuit in which it is connected;
label | a8272196-a994-535d-9209-16adb0304705 |  | note | (c) RCDs required to switch all live conductors shall switch the active and neutral conductors of the circuit;
label | af0e2474-cd30-5dd1-84f2-eb4cb40852d8 |  | note | (d) Where multi-phase socket-outlets of the same type form part of an electrical installation the
label | bd7491ca-3698-5460-b6bb-dd78a5851178 |  | note | phase sequence of the socket-outlets shall be the same (see 3.5);
label | bde18076-85ca-5958-aefe-6a7eeeb41a01 |  | note | (e) Socket-outlets which accommodate flat-pin plugs shall be connected so that, when viewed from the front of the socket-outlet, the order of connection commencing from the slot on the radial line shall be earth, active and neutral in a clockwise direction;
label | df720a3b-2c6a-57a0-a8d7-38e9892bee8c |  | note | (f) All neutral conductors shall be connected to the neutral bar of the switchboard; and
label | 9d9a090e-3c88-5f7c-94ff-c87ce706cc6a |  | note | (g) The consumers mains neutral shall be connected to the neutral bar of the main switchboard.
label | af85037d-9f03-5632-b1fd-58263da95d70 |  | note | AS 3017:2007 Section 3.3
checkpoint-status |  |  | checkpoint | Correct Circuit Connections
label | 0118c192-401d-51c6-83ea-73c5080e1619 |  | note | Tests for correct circuit connections are necessary to ensure the following: (a) Protective earthing conductors do not carry current in non-fault conditions; and
label | 8e8e7c13-8c97-5e85-94ff-06dfade6bd48 |  | note | (b) No short-circuit exists, because a short-circuit current flowing between live conductors and through part of the earthing system can cause considerable fire damage or personal injury, particularly in high current locations.
label | b06654c3-12c2-55c0-9643-ae513d99c1a8 |  | note | Refer to AS3017 section 3.4 for further detail.
label | 3ec1bd59-9293-5559-93bc-d3bb8f7bd797 |  | note | Complete ITC-212.1 / ITC-212.2
label | 4297590a-1fbf-5571-a035-1e8a30025e27 |  | note | AS3017;2007 Section 3.4
checkpoint-status |  |  | checkpoint | Earth Fault Loop Impedance
label | b5f6c410-1364-5d8d-bed9-47d4ed6db909 |  | note | 3.6.3.2 Supply not connected
label | 3fef971c-b48b-57ea-a880-4beb930fc981 |  | note | When tested in accordance with 3.6.4.2, the total resistance (Rphe) of the active and protective earthing conductors of an individual circuit which forms part of the earth fault-loop shall not exceed the values shown in table 8.2.
label | 6502aae4-3f8d-5d3f-b697-550c3009994c |  | note | NOTE: The values calculated must be accumulative of sub mains etc.
label | 58da55c9-b10f-59aa-99d4-e86b8c4f7be0 |  | note | The earth fault-loop impedance of a circuit is measured to ensure that, if a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part, sufficient current will flow in the earth fault-loop to cause a protective device to operate within a specified disconnection time.
label | ba44a522-569d-5555-8d08-e9e48a57158b |  | note | Refer to AS3017 section 3.6 for further detail.
label | 82cd426b-7d17-5182-b230-80ab59e08e39 |  | note | Complete ITC-212.1 / ITC-212.2
checkpoint-status |  |  | checkpoint | Dead testing complete
checkpoint-status |  |  | checkpoint | Upon completion of 'dead' testing present all documentation to Site supervisor for approval
checkpoint-status |  |  | checkpoint | Submit test results for review with site management
checkpoint-status |  |  | checkpoint | Site supervisor reviews ITC for completeness.
label | 876e06c4-b8b3-5544-b184-9b3659b9d37d |  | note | Note: Fredon supervisor is not responsible for test result accuracy.
label | 06bfae00-f5d2-54dc-ab61-5d682f5eeae1 |  | note | Review / issue permit energisation Permit (HSF-091)
holdpoint |  |  | signoff | Permit Reviewed
checkpoint-group |  |  | section | Energised Testing
checkpoint-status |  |  | checkpoint | Test For Voltage
label | 32453e5c-4b69-527b-b9fd-64be98842e37 |  | note | Using test lamps / voltmeter
label | 1822542c-ca0f-5030-ade4-20fb06dad37b |  | note | Main switch off
label | 2ca5b057-5d7f-5880-b121-53381ef98968 |  | note | Confirm supply is present at Line side of main switch.
label | bb963c2a-5f79-5f59-b203-359d274796b4 |  | note | Confirm supply is not present at Load side of main switch.
label | 1a18a7cc-87b9-5c75-adf0-b946c99f119b |  | note | Main switch on - sub circuit (CBs) off
label | b9070f8c-c8d7-5df9-aa9e-0a936efe0ae0 |  | note | Confirm supply is present at Load side of main switch.
label | 69da4682-99e0-58d0-b421-9cdb3977f9da |  | note | Confirm supply is present to line side of relative distribution circuit breakers. Complete ITC-212.1 / ITC-212.2
label | b0c449c8-fe8b-54cd-8ed5-be3d5ca5de8a |  | note | AS3017;2007 Section 3.4
checkpoint-status |  |  | checkpoint | Phase rotation
label | 888dd958-63c3-5cc7-b28d-1ba07b42ef90 |  | note | Using test phase rotation meter.
label | 877a9a99-25c1-516e-9c83-6b22bd782ff6 |  | note | Confirm phase rotation sequence.
label | d29ffe64-b40a-5664-b12e-4ceff064cd58 |  | note | Complete ITC-212.1 / ITC-212.2
label | a9fc6f56-a768-51e9-8590-f994e1ca77fe |  | note | AS3017;2007 Section 3.5
checkpoint-status |  |  | checkpoint | Earth Fault Loop Impedance
label | aa8e44e2-a5b1-5d35-831d-d1bcf30df3ef |  | note | 3.6.4.1 Supply connected
label | 0f91aa8e-0df6-55a8-ba75-efb61333d5af |  | note | The earth fault-loop impedance should be measured using an instrument that has a facility for measuring and indicating low values of impedance.
label | 35f868ac-4fa3-58a4-9936-ebdc7b08a4c2 |  | note | (2) Earth continuity and resistance tests should be carried out on protective earthing conductors in accordance with 3.1 before measuring the earth fault-loop impedance.
label | fda90ad3-563f-56d3-9133-b239fd98a288 |  | note | (3) It is preferable to measure the earth fault-loop impedance using the permanent network supply rather than a temporary supply.
label | 54b1b202-7dc6-56dc-ba19-339053b5c1b6 |  | note | (4) The measuring circuit includes the impedance of the flexible test lead, which must be as supplied with the meter. If the meter leads are fused, the fuse resistance must be taken into account. The MEN connection is to be left intact.
label | 835a7d2b-6c88-51ee-bcfa-2821cc6dbcbf |  | note | Maximum values of earth fault-loop impedance shall not exceed the values shown in table 3.1 or the value of Ia for the protective device being used in accordance with the manufacturer’s data. Refer to AS3017 section 3.6 for further detail.
label | 7078e17b-9db0-54bd-b3b7-2e07e8676dff |  | note | Complete ITC-212.1 / ITC-212.2
label | 91740b98-c5ed-5f82-96c4-b22a837ba5d4 |  | note | Note: If an RCD operates during the earth fault-loop impedance test, the test result is considered satisfactory.
checkpoint-status |  |  | checkpoint | Operation of Residual Current Devices
label | 1103b398-c07c-5c44-bda5-8ba40af6b92f |  | note | Testing of an RCD is carried out to ensure that the RCD operates and disconnects the designated circuit.
label | 7bcdae11-d0de-5d09-b38a-da1d59ba306c |  | note | The function of the RCD is verified by the operation of the integral test device, or by the use of special test equipment
label | a9e52b48-463f-5d1d-a1ea-c7ed67a16fa7 |  | note | Operation of the integral test device shall cause the RCD to trip and disconnect the designated circuit.
label | e0cceea7-8cd9-571c-9d81-389367f2087e |  | note | (1) Tripping the RCD by means of the integral test device establishes:
label | 21c5ee9d-e9f0-5211-85e8-3fa8586f8ee4 |  | note | (a) That the RCD is functioning correctly; and
label | 1d3d7c27-c88d-513b-af3f-5c456d038152 |  | note | (b) The integrity of the electrical and mechanical elements of the tripping device.
label | ded66717-9efc-5733-a0f7-ab9aa0280268 |  | note | (2) Operation of the integral test device does not provide a means of checking:
label | 38b8e21b-ea21-5e69-926c-3f2468c5ac7c |  | note | (a) The continuity of the main earthing conductor or the associated circuit protective earthing conductors;
label | 3f80ff0d-7c6c-546e-abe9-19138cb9d337 |  | note | (b) Any earth electrode or other means of earthing; or
label | dd7ef8b6-f56b-59b6-8042-58a1424c8b56 |  | note | (c) Any other part of the associated electrical installation earthing.
label | 0db5ec84-ba99-5c21-9070-78fdee81dd22 |  | note | (3) Tripping the RCD by means of the integral test device, or by special test equipment such as a test plug with a resistor between the active and earth pins, may be used to verify that the circuits required to be protected by the RCD are protected.
label | cb67594b-6246-5adb-bb9b-ee1182e344f8 |  | note | RCD is to be tested using functional trip test and trip times must be recorded. Complete ITC-212.1 / ITC-212.2
label | 0c2d0d99-458b-58c7-9a16-d6a0fd9a2c38 |  | note | AS3017;2007 Section 3.7
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | At works completion confirm all circuit schedules are complete & correct.
checkpoint-status |  |  | checkpoint | All circuit descriptions are clear & worded to be easily understood.
checkpoint-status |  |  | checkpoint | Any circuits not tested remain disconnected from circuit breaker & terminated in BP connected.
checkpoint-status |  |  | checkpoint | All equipment has been labelled in accordance with project requirements, and labelling aligns with as built drawings.
checkpoint-status |  |  | checkpoint | Ensure that any changes made during testing which effect as built documentation are captured via RED pen mark up on drawings.
checkpoint-status |  |  | checkpoint | Compile list of any incomplete works or defects which require rework.
checkpoint-status |  |  | checkpoint | Reinstate all switch board covers, doors and panels. LOCK THE SWITCHBOARD DOOR & CHECK ALL OF THE ABOVE
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Documentation - Once complete:
button | 8402ebff-4395-517c-9426-187a9322921d |  | button | 1. Review documentation for correctness. | Yes, No
button | bf04c7f6-7fae-54ad-8842-6b6132f2a931 |  | button | 2. Submit documentation to site supervisor immediately. | Yes, No
button | 3ebc11b1-b9c3-59ed-8140-943eaa128d8b |  | button | 3. ITC-212 complete & signed | Yes, No
button | 4349c141-d3e9-529e-8dbb-6abd4d316dc4 |  | button | 4. RED pen mark up of zone drawing for as built information. | Yes, No
button | 8f951668-e7ea-5e1e-9ad9-2551fc2e1f79 |  | button | 5. DB schedule information. | Yes, No
button | dd328579-226e-5990-97dd-d3ee3cd0c76a |  | button | 6. Concise list of incomplete or defective works. (DO NOT LEAVE ON SITE) | Yes, No
button | 1c66df73-538f-50a1-badb-eae4933ffdd6 |  | button | 7. Submit | Yes, No
checkpoint-status |  |  | checkpoint | Fredon site supervisor shall review all documentation
label | 8030e509-0910-5004-be9f-1560f0855d7a |  | note | Fredon supervisor is not responsible for test result accuracy
checkpoint-status |  |  | checkpoint | Fredon Project Manager to provide certificate of testing and compliance Certificate of Compliance
checklist-flat |  |  | checklist | ITC-224.1 Nurse Call Installation |  |  |  |  | Yes | ITC-224.1 Nurse Call Installation | 078fd089-3023-4459-a628-bb938e0608b8
checkpoint-status |  |  | checkpoint | Complete details below
text | 1b69ba66-dd7b-5497-83cb-71241c0222be |  | textbox | Source
text | fc7f39c4-b65c-525a-9529-0e0ff22fd0b9 |  | textbox | Destination
boolean | d616c2f6-f7ec-57ab-83de-6a5f6fa51ed4 |  | tickbox | Less than 90m
boolean | 36285f7b-789a-5b3a-a6a3-9648c6f5edb8 |  | tickbox | Bend radius not exceeded
boolean | 6a132be8-5937-58dd-a8e5-15b244e12289 |  | tickbox | Labelled at both ends
boolean | af852343-73f0-5598-bb41-36ef2ed4b832 |  | tickbox | Adequate cable support
boolean | 5e09a080-2d27-5825-8a72-a4c1a8a4d332 |  | tickbox | Service loop / Goose neck
boolean | 49dd9d9f-5098-5f75-a996-d716747e4f0b |  | tickbox | Segregation from other services
text | 32750b0f-bc4b-51e9-8bd7-48be4dda1001 |  | textbox | Installer
text | b3b857b8-f5f5-5764-b4e1-8c5fd001b82f |  | textbox | Registered cabler licence number
text | 0430eb68-7252-5b17-ae2c-a6b81a7ecc01 |  | textbox | Hold Point
checkpoint-status |  |  | checkpoint | Attach signature
checklist-flat |  |  | checklist | ITC-222.1 Horizontal Cabling Installation |  |  |  |  | Yes | ITC-222.1 Horizontal Cabling Installation | 0897af34-bdc0-4ba8-816f-aed7c83397b7
checkpoint-status |  |  | checkpoint | Rack/Patch Panel: PCN
text | 0969e0f1-28ba-55be-9f42-96264c46180f |  | textbox | Cable No.
boolean | d121a76d-8c2f-5195-bf40-a4059a1fb0a7 |  | tickbox | Less than 90m
boolean | 31b36c6a-c3af-5f3f-b33a-48e7f7524e40 |  | tickbox | Bend radius not exceeded
boolean | dd2845d7-dcb8-5895-9fc7-b12b9e98648e |  | tickbox | Labelled at both ends
boolean | 2323ac3c-4b15-5058-b433-388fbd2d4d81 |  | tickbox | Adequate cable support
boolean | 9ec644c5-77bf-5e9e-b389-e8b498e06437 |  | tickbox | Service loop / Gooseneck
boolean | 7d4cc4d4-df60-568c-ad8b-e3208217b861 |  | tickbox | Segregation from other services
text | 5161786c-af86-5482-a460-0bcb8cbea3d9 |  | textbox | Installer
text | 61527925-2beb-520f-b173-aa0f554e7d0c |  | textbox | Registered cabler licence number
checklist-flat |  |  | checklist | ITC-219.1 Fit Off Power, Switches & Accessories |  |  |  |  | Yes | ITC-219.1 Fit Off Power, Switches & Accessories | 0bf5f52b-770c-4d1e-8641-751bee4e079c
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | 0e8a57d6-042c-54ba-a4d7-bef81abadcda |  | textbox | Outlet Number
text | 04e70213-29ba-5ef0-a2ea-93744081bac5 |  | textbox | Equipment Type
text | 4be4eda0-4313-5b08-9d37-a4f24beacc04 |  | textbox | Quantity
text | 74617157-9eae-5b75-affc-9a6b195cde1f |  | textbox | Cable Size
checkpoint-status |  |  | checkpoint | Set Out Comms Services Plan
checkpoint-status |  |  | checkpoint | Set Out Architectural / Other Serices Plan
checkpoint-status |  |  | checkpoint | Mounting Arrangement
boolean | 8918f641-6af4-5525-ac83-c8a13357f104 |  | tickbox | Plaster Clip
boolean | bdf9e022-dd5a-58ac-8b12-b3b0a5748b7e |  | tickbox | Recessed Fire Box
boolean | ce9950bf-bb8a-5814-8110-547da1c6cbb6 |  | tickbox | Acoustic
boolean | bd02ab35-2ff2-5c75-acd1-1f316f26d2c4 |  | tickbox | Surface Mounted
checkpoint-status |  |  | checkpoint | Ready for use
text | 1981d76c-af2b-51c2-a073-128c58f1ccfd |  | textbox | Label Installed
checklist-flat |  |  | checklist | ITC-227.1 Backbone Copper Cable |  |  |  |  | Yes | ITC-227.1 Backbone Copper Cable | 0e067ef9-8911-4c32-96b9-25d7ee2bd910
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
label | 2aac48ac-8d50-5adb-a9f8-a70e11df9eb7 |  | note | Cable identification drawing outlet number
text | 994fd083-4dd5-599f-9346-2292dbae2593 |  | textbox | From
text | 01a722d0-308f-58da-b684-023217736756 |  | textbox | To
text | e592dc8c-ea6f-5c57-829a-40997636ccb4 |  | textbox | Cable Type
text | ad8fc664-e558-5377-b0e5-da6596cd7711 |  | textbox | Core
checkpoint-status |  |  | checkpoint | Materials conform to specification
checkpoint-status |  |  | checkpoint | Cable terminated and labelled
checkpoint-status |  |  | checkpoint | Cable Tested
checkpoint-status |  |  | checkpoint | Drawings marked up to reflect as-installed
checkpoint-status |  |  | checkpoint | Final Acceptance - attach Fredon representative & client signature
checklist-flat |  |  | checklist | ITC-222.2 Fit-Off Horizontal Cabling |  |  |  |  | Yes | ITC-222.2 Fit-Off Horizontal Cabling | 132efa2a-ae26-49e1-b280-007d12f6fe87
checkpoint-status |  |  | checkpoint | Rack/Patch Panel: PCN
text | 4d0836f4-8db8-5c2b-81e6-0614765c7e89 |  | textbox | Cable No.
label | dea853ac-94b9-5910-8fab-3db3a5e0925e |  | note | Field End
boolean | 0cf1eb46-d22b-5adb-85c6-55eb5074e2a5 |  | tickbox | Labelled
boolean | d4ea0100-c577-55ad-8fa2-3631100c1a09 |  | tickbox | Level to other services
boolean | 324272f2-80af-5bd0-a492-bd8562592c77 |  | tickbox | Terminated
boolean | d7546cb8-482d-5f4d-8fb3-9fe31f1c56bc |  | tickbox | Labelled
label | 3f65ec1b-6b94-5534-98fa-2b41d9433152 |  | note | Communication
boolean | 0f2b85ca-839b-5ad7-881c-4addaecaf541 |  | tickbox | Labelled
boolean | 929e1997-151a-5bbd-a05f-b1d8e1adddee |  | tickbox | Service Loop
boolean | fe23bb8d-cd47-54ab-98fe-62c1f9b58a3d |  | tickbox | Terminated
text | d2a52846-afcc-5973-b970-a1ec52c7bdf7 |  | textbox | Installer
text | ed34e2d3-9f95-53d0-931d-93d3b0effe8f |  | textbox | Registered cabler licence number
checkpoint-status |  |  | checkpoint | Construction drawing is latest revision
checkpoint-status |  |  | checkpoint | Cabinet positioning marked
checkpoint-status |  |  | checkpoint | Cabinet conforms to specification
checkpoint-status |  |  | checkpoint | Cabinet & accessories installed & earthed
checkpoint-status |  |  | checkpoint | Cabinet & accessories labelled
checkpoint-status |  |  | checkpoint | Drawings marked up to reflect as-installed
checklist-flat |  |  | checklist | ITC-218.1 Fit Off - Lighting |  |  |  |  | Yes | ITC-218.1 Fit Off - Lighting | 187d2e92-eef2-49b7-a7f5-9064cd3270a2
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | 094e6039-76c9-5301-bd69-fdd7b38bb7a8 |  | textbox | Circuit Number
text | 52e12bf1-45e0-5eb1-bf45-32bc3c321e7c |  | textbox | Fitting Type
text | df57a50b-daf4-5924-9491-12b42c3e1fca |  | textbox | Quantity
checkpoint-status |  |  | checkpoint | Check fitting for damage
checkpoint-status |  |  | checkpoint | Check fitting has correct lamps / type
checkpoint-status |  |  | checkpoint | Set Out Electrical Services Plan
checkpoint-status |  |  | checkpoint | Set Out Architectural / Other Services Plan
checkpoint-status |  |  | checkpoint | Mounting
text | d115fd7d-6a19-5e8a-a92d-7370f99faf50 |  | textbox | Recessed cut out size
text | a57c2d3f-5dd0-5c91-8023-da21c7db7ffc |  | textbox | Support system - Direct fixed, Tbar, Chain etc.
checkpoint-status |  |  | checkpoint | EM Lights
text | 701c01e3-be22-5111-9fda-3f08052f2097 |  | textbox | ID Sticker Fitting
text | e5c6ee03-6b92-5392-8c37-3b82e7bc8eea |  | textbox | ID Label Register
checkpoint-status |  |  | checkpoint | Connection
text | f620014c-2cfc-5100-b601-e04b5232d715 |  | textbox | Plug Top
text | eeb0c9e4-f238-5622-b650-54bf288de0da |  | textbox | Hard Wired
text | 85b2b7a6-ceb9-5d47-b75d-564f416654b5 |  | textbox | LT CTRL Connected
checklist-flat |  |  | checklist | ITC-215.1 Cable Tray / Ladder |  |  |  |  | Yes | ITC-215.1 Cable Tray / Ladder | 1a9ed759-3384-4962-9d82-53d3b9ea8a86
checkpoint-status |  |  | checkpoint | Area / Location - Plan Reference
label | 186b7c44-e2c2-5372-bb5e-d159e51ec8ad |  | note | Grid Ref
text | 52011a43-435a-52cf-9022-335e43cd1502 |  | textbox | Drawing #
text | 08b8ada5-8882-5ada-b450-897fa6aba461 |  | textbox | Cable Support Size
text | a28a5eef-b6e5-5290-9a28-5266b5664252 |  | textbox | Cable Tray Material (HP Gal, Zinc, Galvanized etc.)
text | 4a66ff05-cb54-539d-9196-807c7b1b8674 |  | textbox | Spare Capacity
text | 4ca3e4f8-9804-5c03-9492-0f1e22185625 |  | textbox | Tray type ( T - Tray, FR - Fire Rated, B - Basket, L - Ladder)
text | 492dba29-e751-530a-8501-66454a7a8ffe |  | textbox | Spacing for Fixing
checkpoint-status |  |  | checkpoint | Support system suitability sized for expected load
text | 3d5790f3-b00e-5b46-97ac-623951863bde |  | textbox | Expected Load
text | 251317ec-6a56-55cb-be74-968fc542aa10 |  | textbox | Seismic Restrained
text | 42849f2a-135f-58a9-8c4c-4a9df35c9d5b |  | textbox | Support Bracket is Suitable
checkpoint-status |  |  | checkpoint | Coordination & clearance from other services has been complete
checkpoint-status |  |  | checkpoint | Approx Meterage
checkpoint-status |  |  | checkpoint | Cable support system require equipotential bonding
checklist-sectioned |  |  | checklist | ITP-218 Fit Off - Light Fittings |  |  |  |  | Yes | ITP-218 Fit Off - Light Fittings | 217af654-93e0-44bd-9703-c0c3d94569b5
checkpoint-group |  |  | section | Light Fitting Installation
checkpoint-status |  |  | checkpoint | Ensure that the correct fitting is being installed for each location as per drawings
checkpoint-status |  |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status |  |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status |  |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status |  |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status |  |  | checkpoint | Ensure that all terminations are correct including lighting control terminations and are as per manufacturer's requirements
checkpoint-status |  |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
label | 443bfad4-3f58-5352-bc92-a80c0491593c |  | note | AS 3000, Sec 4
label | ce1a89ce-9b70-5bd0-ad24-f0b83f25c1bf |  | note | SDC-KNX-ELE-EPS-401-D Electrical project specification SDC-NSD-ELE-GSS-401-8.1-AU Electrical general specification
checkpoint-group |  |  | section | Installation of Exit & Emergency Lighting
checkpoint-status |  |  | checkpoint | Install fittings as per manufacturer's recommendations
label | e33f36d1-0da8-5424-aed3-ec3f516fb08b |  | note | Ensure that the correct fitting is being installed for each location as per drawings and visibility of escape lighting meets AS 2293. NOTE: Directional arrows show correct path of egress and the luminaire has the Emergency label attached
checkpoint-status |  |  | checkpoint | Ensure that the correct mounting method is being used i.e. surface, chain suspended, recessed etc. Check all drawings prior to installation
checkpoint-status |  |  | checkpoint | Ensure fittings are installed using the correct fixing type
checkpoint-status |  |  | checkpoint | Ensure that any required ceiling grid removal has been carried out by ceiling fixers only. UNDER NO CIRCUMSTANCE IS CEILING GRID / CHANNEL TO BE CUT BY FREDON ELECTRICAL PERSONNEL
checkpoint-status |  |  | checkpoint | Ensure that all terminations are correct including monitoring terminations and are as per manufacturer's requirements
checkpoint-status |  |  | checkpoint | Ensure that ceiling mounted fittings are adequately supported according to their weight. Additional supports added to the ceiling where necessary
checkpoint-status |  |  | checkpoint | All light fittings have been installed in a tradesman like manner (Straight & level etc)
checkpoint-group |  |  | section | Record Luminaire Information
checkpoint-status |  |  | checkpoint | Ensure all emergency lighting information is kept on As Built information. Fitting number. Circuit supplying fitting. Fitting serial numbers etc.
checkpoint-group |  |  | section | Installation of Fittings with ELV Control i.e. DALI
checkpoint-status |  |  | checkpoint | Ensure that the lighting control philosophy is understood. Cable requirements. Cable polarity. Cable connections. Refer to Lighting Control ITP & ITC
checkpoint-status |  |  | checkpoint | Ensure all fitting information is kept on as built information. Fitting number. Circuit supplying fitting. Fitting serial number etc.
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Visually inspect entire circuit for completeness
checkpoint-status |  |  | checkpoint | Ensure fittings are protected if required
checkpoint-status |  |  | checkpoint | Remove all rubbish - empty boxes etc.
checkpoint-status |  |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-flat |  |  | checklist | ITC-216.1 In-Slab Works |  |  |  |  | Yes | ITC-216.1 In-Slab Works | 227b33a4-6c06-4c4b-9122-a25eb57cfe4f
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | 19af1d46-c1f1-5e04-9424-7b47bec5bd0a |  | textbox | CCT Ref
text | 43d836cd-f054-54f7-bc0c-2e9e9f418540 |  | textbox | Pour Location (e.g. Document Gridlines)
text | dbdc2344-5dc5-5f0f-b9c3-15293e65a4a4 |  | textbox | Fredon Drawing Reference & Revision
checkpoint-status |  |  | checkpoint | No Structural Implications
checkpoint-status |  |  | checkpoint | Marked Out Correctly
checkpoint-status |  |  | checkpoint | Glued & Tied Securely
text | 2d7314dd-e955-5c26-a3a4-c91673707ed3 |  | textbox | Conduit Size
checkpoint-status |  |  | checkpoint | As Installed Drawing Attached
checkpoint-status |  |  | checkpoint | Conduit Ends Capped
checkpoint-status |  |  | checkpoint | Signed By Installing Tradesman
text | e773393b-95de-5e7f-80a6-8dc11be0d919 |  | textbox | Approx Lengths of Conduit
checkpoint-status |  |  | checkpoint | Ensure photos are taken
checklist-sectioned |  |  | checklist | ITP-213 Switchboard Inspections |  |  |  |  | Yes | ITP-213 Switchboard Inspections | 2437c430-5230-4d0b-9be3-66f5b493598c
checkpoint-group |  |  | section | On-Site Coordination
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | Ensure all new installations have been coordinated with other services, both new and existing.
checkpoint-status |  |  | checkpoint | Location & position of switchboard
checkpoint-status |  |  | checkpoint | Supply authority access requirements
checkpoint-status |  |  | checkpoint | Physical clearances in and around switchboard area
checkpoint-status |  |  | checkpoint | Ensure proposed switchboard location is secure
checkpoint-status |  |  | checkpoint | Doors on rooms / cupboards etc.
checkpoint-status |  |  | checkpoint | Signage is installed
checkpoint-status |  |  | checkpoint | Structural supports in place
checkpoint-group |  |  | section | Off-Site Coordination
checkpoint-status |  |  | checkpoint | Carry out pre-delivery inspection at workshop
checkpoint-status |  |  | checkpoint | Inspect workmanship
checkpoint-status |  |  | checkpoint | Quality control - Please take photos
checkpoint-status |  |  | checkpoint | Get weight and lifting information
text | a57ced59-d349-5bda-a2b7-a2443f4da4f8 |  | textbox | Confirm:
checkpoint-status |  |  | checkpoint | Has the manufacturer supplied workshop QA documentation
checkpoint-status |  |  | checkpoint | Has the manufacturer supplied workshop FAT documentation
checkpoint-group |  |  | section | Delivery Acceptance Inspection
checkpoint-status |  |  | checkpoint | VISUAL Check for obvious signs of damage DO NOT ACCEPT DELIVERY IF DAMAGED
checkpoint-status |  |  | checkpoint | Check for delivery of quality control and quality checklist completed from factory DO NOT ACCEPT DELIVERY IF NO DOCUMENTS
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Plan and resource installation task appropriately
label | f42b465d-90aa-58f0-8765-57d9cafbc9bb |  | note | Use only proprietary lifting and rolling equipment
label | 6977199a-d96d-507e-8bbf-bfdac70fa7f8 |  | note | Clear route to switchboard installation location
label | 613febc2-18c5-56fb-8570-c5b45b0ee9d0 |  | note | Clear installation area completely of any obstacles, rubbish, personnel etc.
checkpoint-status |  |  | checkpoint | Switchboard mounted using correct fixings with additional structural support added where required
checkpoint-status |  |  | checkpoint | Switchboard mounted in a position to allow all correct clearances around the switchboard to satisfy all standards, specs and regulations
checkpoint-group |  |  | section | Post-Installation Inspection: General
checkpoint-status |  |  | checkpoint | Remove all covers and inspection panels from board
checkpoint-status |  |  | checkpoint | Carry out the following checks and inspections;
checkpoint-status |  |  | checkpoint | Visually inspect for damage
checkpoint-status |  |  | checkpoint | Visually inspect for cleanliness within boards
checkpoint-status |  |  | checkpoint | Visually inspect for loose cables & bars
checkpoint-status |  |  | checkpoint | Visually inspect for loose breakers, fuses and switches
checkpoint-status |  |  | checkpoint | Visually inspect all metering and control equipment
checkpoint-group |  |  | section | Post-Installation Inspection: Terminations & Connections
checkpoint-status |  |  | checkpoint | Using appropriate tension tools and equipment, physically check tension of switchboard connections (switches, circuit breakers, control components etc.)
checkpoint-status |  |  | checkpoint | Complete ITC-213.1, Section 4
label | e8e148a7-c380-5059-a16c-6bee5ec3cc7d |  | note | NOTE: Switchboard connections may have come loose during transit
checkpoint-group |  |  | section | Post-Installation Inspection: Functional Devices
checkpoint-status |  |  | checkpoint | Using a calibrated tester physically confirm functionality of ALL isolation devices
checkpoint-status |  |  | checkpoint | Confirm "OFF" is off (open state) by phisical operation
checkpoint-status |  |  | checkpoint | Confirm "ON" is on (closed state) by physical operation
checkpoint-status |  |  | checkpoint | Complete ITC-213.1, Section 5
checkpoint-status |  |  | checkpoint | Review all protective device trip settings in accordance with engineers design, discrimination and cascade reports
checkpoint-status |  |  | checkpoint | Review all metering, fuses and control equipment wiring
checkpoint-group |  |  | section | Post-Installation Inspection: Drawing Confirmation
checkpoint-status |  |  | checkpoint | Using as built / as constructed documentation confirm general arrangement, SLD and schematics are correct
checkpoint-status |  |  | checkpoint | Confirm signage and labels on board are correct
checkpoint-status |  |  | checkpoint | Confirm schedule is updated and inside board
checkpoint-group |  |  | section | Post-Installation Inspection: Insulation Resistance
checkpoint-status |  |  | checkpoint | Carry out insulation resistance test to confirm integrity of switchboard insulation between all active conductors and all neutrals AND earths
checkpoint-group |  |  | section | Final Completion
checkpoint-status |  |  | checkpoint | Reinstate ALL cover panels, close doors and lock etc.
checklist-flat |  |  | checklist | ITC-220.1 In-Ground Works |  |  |  |  | Yes | ITC-220.1 In-Ground Works | 27591576-620f-43cc-8678-1ab48f7754b3
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | f83ae7e1-c2df-511a-8cc2-e0bbfe60c3e3 |  | textbox | Conduit Run / Grid No
checkpoint-status |  |  | checkpoint | Survey and set out was correct at time of survey Surveyor to complete (& reference set out info)
checkpoint-status |  |  | checkpoint | Permit to dig
checkpoint-status |  |  | checkpoint | Alignment correct width / depth suitability of base
checkpoint-status |  |  | checkpoint | Conduit Installation Size / Type / Quantity
checkpoint-status |  |  | checkpoint | Conduit Installation, correct spacers used
checkpoint-status |  |  | checkpoint | Photograph, Trench Detail & Depth
checkpoint-status |  |  | checkpoint | GFIS detail for as build data base - Surveyor to complete
checkpoint-status |  |  | checkpoint | Confirm backfill is suitable - Check compaction & frequency requirements
holdpoint |  |  | signoff | Hold point prior to backfill
checkpoint-status |  |  | checkpoint | Geo to confirm
checkpoint-status |  |  | checkpoint | Suitability of proposed backfill
checkpoint-status |  |  | checkpoint | Test 1 per 2 layers per 40m
checkpoint-status |  |  | checkpoint | Confirm layers being replaced i.e. geo - fab, road base & general fill
checkpoint-status |  |  | checkpoint | GEOTECH Cardno - NB layer thickness is 250mm max loose
checkpoint-status |  |  | checkpoint | Trench Markers
checkpoint-status |  |  | checkpoint | Geo tech results reviewed
checklist-flat |  |  | checklist | ITC-212.2 Single & Three Phase Sub-Circuit Test Sheet |  |  |  |  | Yes | ITC-212.2 Single & Three Phase Sub-Circuit Test Sheet | 3d109445-8764-4cf8-9307-10161d0e4987
checkpoint-status |  |  | checkpoint | De-Energised Tests
text | 3a7f668d-e550-534f-ab11-e16e3c456484 |  | textbox | Distribution Board No.:
text | 60eda2ae-ef40-5702-ac7c-ccb64e861250 |  | textbox | CB No.
text | 02c19f8d-2714-53b2-b50d-a603cf586fca |  | textbox | Neutral No.
text | bbddb9c5-597c-56ac-bb17-dc988856a679 |  | textbox | Circruit No.
text | 9f3e91ca-d2ca-5846-b549-7a643a092bc8 |  | textbox | Cable Size
text | 0b0c0549-29e0-5927-8343-88ab8fd7817e |  | textbox | Destination
text | df427cc5-5d59-5c9b-8121-f8beea7b660a |  | textbox | No. Pts
boolean | 9586a45b-6924-53cc-854b-131bde165ec5 |  | tickbox | Visual Check
text | bc976656-5a36-5aee-a7ab-93da266b7772 |  | textbox | CB Size (Amps) & Type (A,B,C,D)
text | 373f9b64-b4ab-528c-9021-8527975a47f6 |  | textbox | Earth Continuity (Ω)
label | 4c22a512-2c01-57f7-bf68-6eab01d8345b |  | note | Insulation Resistance (MΩ)
text | 9cf9bd6c-85ea-50bf-8f83-5675a33e597c |  | textbox | Red to White
text | d5ddafc3-55f4-5e42-b368-1b3e31441044 |  | textbox | White to Blue
text | a8508644-a2bc-5549-a839-a1f51e888378 |  | textbox | Blue to Red
text | 35426ac4-f61e-599f-8364-74c0c802c15a |  | textbox | A Phase to Neutral
text | 574ce2af-fdd0-5552-af79-ff9bed4cd47b |  | textbox | B Phase to Neutral
text | 7cb6c231-30a7-5458-8224-82294df0c046 |  | textbox | C Phase to Neutral
text | 65e10adf-1452-5894-8b58-1c8437d5e2d4 |  | textbox | Phases to Earth
text | 88bec526-7059-52c0-b9ca-0d489c8d7ba1 |  | textbox | Neutral to Earth
boolean | f7f74b3b-ae01-5a0f-b6b7-c91c92278118 |  | tickbox | Polarity Pass
boolean | f3906394-bcc3-5155-9e64-0599ea8b82a9 |  | tickbox | Correct circuit connections
checkpoint-status |  |  | checkpoint | Safe to Energise
holdpoint |  |  | signoff | Ensure safe to energise
checkpoint-status |  |  | checkpoint | Energised Tests
text | 4f3b0b94-8688-5faf-b048-4d381f9c53c4 |  | textbox | Voltage (V)
text | 3fbd13e2-6591-542a-bd5f-82f0feb29a9a |  | textbox | Phase Sequence
text | e03dbaa4-c7c5-5f78-8e16-452613088d89 |  | textbox | Fault Loop Impedance
label | e30575b1-2bbc-5dfd-bd2b-c26afdd040b5 |  | note | RCD Timed Test (mS)
label | 3afd57b0-1335-5560-b948-2a91f99d42c4 |  | note | 30mA / 10mA
text | aa5a9ccb-e0b3-514b-8467-609a6cbad875 |  | textbox | 0
text | 5e6a26e5-c398-51dc-877e-17337d633cc3 |  | textbox | 180
checkpoint-status |  |  | checkpoint | Label Installed
checkpoint-status |  |  | checkpoint | Test Signed Off
checklist-flat |  |  | checklist | ITC-212.1 Consumer Mains, Sub Main or Bus Bar Test Sheet |  |  |  |  | Yes | ITC-212.1 Consumer Mains, Sub Main or Bus Bar Test Sheet | 41be8bdb-c497-4ab5-a866-416d8ceb4e75
checkpoint-status |  |  | checkpoint | Test between phases / neutral & earth
checkpoint-status |  |  | checkpoint | Install danger tag if required. Should be zero volts.
label | 82c886f7-d889-5aca-94b3-67c7ae75ada4 |  | note | POWER IS TO BE OFF / DB ISOLATOR TURNED OFF
text | c1ac2aa3-68d4-59f7-8d5a-5676e81c1d83 |  | textbox | R-W
text | 82677891-a804-5d13-9267-16f0a95e1e39 |  | textbox | R-B
text | b5afa6f9-e80a-5f97-93df-4bb383bed436 |  | textbox | W-B
text | c1cbd805-4959-5fc6-9d97-fc2082bf04dd |  | textbox | R-E
text | a0f4e86e-d87d-5d10-ae45-d859c6f432d4 |  | textbox | W-E
text | 36dca5e1-993c-51df-9e10-befe47219cd6 |  | textbox | B-E
text | 9496db46-1dcb-584c-be17-cbe0137a8d5e |  | textbox | R-N
text | 28bc9c22-f1f4-5df1-bb7f-0b614baf15f6 |  | textbox | W-N
text | 048204c7-b786-5ffc-8b80-68bf9179e6d4 |  | textbox | B-N
text | f2e26128-85c3-55cb-82c6-7e50c86bf180 |  | textbox | Power Off
checkpoint-status |  |  | checkpoint | Disconnect M.E.N
checkpoint-status |  |  | checkpoint | Remove earth from neutral bar
checkpoint-status |  |  | checkpoint | Disconnect for all tests
checkpoint-status |  |  | checkpoint | Resistance of main earth. Do a resistance test on the cable from one end to the other.
label | c59826b1-1782-5db0-ba14-a1463e94a5cc |  | note | Make sure M.E.N is disconnected.
label | 0467fd81-0c00-59f7-bf89-5eb54f3fd2ae |  | note | (Shall Not Exceed .5 Ohms)
text | 562d7141-55f6-55da-81e3-212c3d1f4639 |  | textbox | Size of active conductor
text | fed105f6-2fea-5803-a4df-f663556773ce |  | textbox | Size of Main Earth
text | 18d35c44-17cb-5072-9243-8ce4699fc3b8 |  | textbox | Resistance of main earth Ω
checkpoint-status |  |  | checkpoint | Insulation Resistance
label | 46cd1b2b-83ae-589b-8bfc-88da86b379bf |  | note | Connect earth and isolate cable both ends. Test with Mega set to 500V/1000V between phases / neutral and earth.
label | 34721ea7-9293-593c-829a-0b0e0bc1e090 |  | note | Should exceed 1M Ohm.
text | 8c158de0-c923-5dd4-8222-c13a32bfb245 |  | textbox | R-W Ω
text | ba53a108-902b-53fa-a44b-5a386625a8ff |  | textbox | R-B Ω
text | ecf84d7b-9237-55f9-b2f3-7e4f983c6595 |  | textbox | W-B Ω
text | 3be08ade-5c8c-5e64-a378-0084ec1b90eb |  | textbox | R-E Ω
text | a5989765-78fa-5927-b80a-651d4450c698 |  | textbox | W-E Ω
text | 8fdeac05-fc76-516c-8462-5fe676fdb061 |  | textbox | B-E Ω
text | e8b6e2e6-9b6e-5807-abb8-9787c279c888 |  | textbox | R-N Ω
text | 858d5c3e-0fe2-51df-85c8-2bbe1d5b5a4c |  | textbox | W-N Ω
text | 5253e4e1-8156-5975-b120-c235a6f2e76c |  | textbox | B-N Ω
checkpoint-status |  |  | checkpoint | Polarity Of Consumer Mains / Submains
label | 3575774f-88f1-5519-b8a6-43773f5b8f41 |  | note | Using the main earth or a trailing lead as a reference conductor short a phase one end & test with meter set to ohms across other end. If you get no reading on the meter the polarity is incorrect.
text | 1cb4e3c2-b7a8-5823-8b23-d0722a347efb |  | textbox | E-R Ohms
text | 3f15ede1-3db1-5852-a9fd-a51d10d5a9ef |  | textbox | E-W Ohms
text | 4ca46e7c-759d-5711-a111-ccf5d17dcc17 |  | textbox | E-B Ohms
text | ab456d03-0a1d-556a-8bac-7132f35e0384 |  | textbox | E-N Ohms
checkpoint-status |  |  | checkpoint | This service is safe to energise
holdpoint |  |  | signoff | HOLD POINT - Complete Energisation permit HSF-091
checkpoint-status |  |  | checkpoint | Phase Rotation Test
label | 91659100-43ee-5af8-bca7-000cfff17dc9 |  | note | On satisfactory completion of above tests, and power is energised, connect phase rotation tester Red, White, Blue leads to respective phase colours and check rotation. Must be clockwise.
checkpoint-status |  |  | checkpoint | Fault Loop Impedance
label | 7ee795ab-6cc1-5272-b1f8-3095585d6253 |  | note | If Energised, Confirm less than AS3000 table 8.1 (Zs)
label | fdf76cd1-acb3-5159-94bb-c5df5db55759 |  | note | If De-energised,Confirm less than AS3000 table 8.2 (Rphe)
text | cbf8311a-3e61-5b66-b9ff-a73b3269ecde |  | textbox | Reading Ω
text | f514791b-408e-5af5-aa50-6918128037ae |  | textbox | AS 3000 Table Requirement
checkpoint-status |  |  | checkpoint | Pre-switchboard Energisation ITC-251 has been completed
checkpoint-status |  |  | checkpoint | Check all necessary drawings available and latest issue.
checkpoint-status |  |  | checkpoint | Check cables of correct size, type & voltage rating is used for wiring.
checkpoint-status |  |  | checkpoint | Ensure correct main switch rating and cabling terminated
checkpoint-status |  |  | checkpoint | Ensure equipment fixed at the correct height. (2000mm switch height max)
checkpoint-status |  |  | checkpoint | Check cable gland is secure and tight on cable
checkpoint-status |  |  | checkpoint | Check cable bending radius is correct
checkpoint-status |  |  | checkpoint | Identification & labelling
checkpoint-status |  |  | checkpoint | Check for cleanliness & for visible damage
checklist-flat |  |  | checklist | ITC-224.2 Fit-Off Nurse Call |  |  |  |  | Yes | ITC-224.2 Fit-Off Nurse Call | 4450f60b-6d1a-4b52-bcad-06716e8d838c
checkpoint-status |  |  | checkpoint | Complete details below
text | 5ef8dda3-4d9b-5c00-a57f-362f22bee45e |  | textbox | Room #
text | 1adcb0b7-a867-5119-aac5-2a7d5ba1f9eb |  | textbox | Device
boolean | ad9ab4ee-c2e3-5994-965a-af2a0f301af3 |  | tickbox | Field End labelled
boolean | ad2998e8-7ebb-5059-9b6d-b3a6777836d3 |  | tickbox | Field End level to other services
boolean | 9df8ff01-cc65-521b-86ea-b0591462cd4d |  | tickbox | Field End terminated
boolean | 3fcb73ae-7c21-547d-8d8e-50e60cfbc2eb |  | tickbox | Comms Room labelled
boolean | 15d60110-26c1-51c3-a8fa-2dbab2ae2d8f |  | tickbox | Comms Room Service Loop
boolean | 148df634-cbb4-5581-b7d0-361f6056f398 |  | tickbox | Comms Room terminated
text | 16655dc2-cb82-52b2-9586-b62ed468e6e6 |  | textbox | Installer
text | 46981849-2fdf-51a0-8513-52e350686475 |  | textbox | Registered cabler licence number
checklist-sectioned |  |  | checklist | ITP-226 Fibre Optic Cable |  |  |  |  | Yes | ITP-226 Fibre Optic Cable | 47be5f1f-a4bc-4046-9fe3-78256c29419d
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure pit and underground piping are clear of obstructions and have the appropriate access and barricading
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status |  |  | checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Ensure that the latest services and coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable pulling strength is not exceeded as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
label | 2913fe11-13f8-5b70-9f4e-5e4410693c22 |  | note | Fredon Shop Drawings AS S2009:2013 Manufactures Requirements
label | 55989568-7c69-52c9-9a31-418fd943d8f0 |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Termination
checkpoint-status |  |  | checkpoint | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
checkpoint-status |  |  | checkpoint | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
checkpoint-status |  |  | checkpoint | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
checkpoint-status |  |  | checkpoint | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
checkpoint-status |  |  | checkpoint | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
checkpoint-status |  |  | checkpoint | Ensure fobot is securely placed inside enclosure and dust caps installed
label | 3732ff78-b5a9-5fd3-8013-240014221e44 |  | note | Fredon Shop Drawings AS S2009:2013 AS 3080 Manufactures Requirements
label | 02c9a603-710f-5319-8f16-475adccb0942 |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status |  |  | checkpoint | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
label | 4c4e03ec-a516-5cd4-a63b-c33a4da942f5 |  | note | Fredon Shop Drawings AS S2009:2013 AS 3080 Manufactures Requirements
label | 1bb51022-474e-5fdc-a0cc-b2ad950c2c44 |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Test Results Recording
checkpoint-status |  |  | checkpoint | Ensure all test results are downloaded and stored in both their native format and as PDF's or safe keeping
label | 7529fa16-6d8f-5bd9-8b81-3ffbf576ef2e |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
label | e622894a-89e8-5dcc-a15c-21b86e1c6a47 |  | note | AS S2009:2013 AS 3080
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records
checklist-sectioned |  |  | checklist | ITP-214 Mains & Sub Mains Installation |  |  |  |  | Yes | ITP-214 Mains & Sub Mains Installation | 48ad84cb-84af-4867-9bc9-28c4c58ddcae
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | For sub main installation information follow Fredon sub main installation check sheet. The check sheet will have all necessary information such as; cable size, origin and destination. This sheet is to be followed and filled out to verify correct installation. COMPLETE ITC-214.1
checkpoint-status |  |  | checkpoint | All submains dressed in the formation specified on Fredon sub main installation check sheet.
label | d08a2447-e953-552a-a658-492e415aef49 |  | note | When using a winch, maximum cable pulling tensions are not to be exceeded, refer to cable manufacturers technical data for maximum pulling tension
label | eda96e00-13c2-5041-bc33-63a817cb4e4b |  | note | All parallel submains dressed on cable tray/ ladder have been spaced correctly to minimise derating and satisfy all standards specs and regulations NOTE: AS3008 Table 23 & Table 24
label | 509d44f4-12c6-5686-bbea-bcb81ab59538 |  | note | All fire rated submains have been dressed with steel cable ties NOTE: Essential Safety Services require their own Fire Rated Support and cable pathway
checkpoint-status |  |  | checkpoint | Mechanical protection installed where required.
checkpoint-status |  |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status |  |  | checkpoint | All submains have been kept clear of sharp edges during installation to avoid damage to insulation.
checkpoint-group |  |  | section | Visual Inspection of Rough In
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for
label | 17cb4c75-e598-535d-ae7a-dced4df93886 |  | note | Hauling of cables ITC-214.1
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned |  |  | checklist | ITP-216 In-Slab Works Installation |  |  |  |  | Yes | ITP-216 In-Slab Works Installation | 502384cb-58b1-48aa-8580-e583cd78ea52
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Prior to installation submit conduit shop drawing for review to the satisfaction of structural engineer
checkpoint-group |  |  | section | Metering / Setting Out
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status |  |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-group |  |  | section | Conduit Selection
checkpoint-status |  |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-group |  |  | section | Conduit Installation (General)
checkpoint-status |  |  | checkpoint | Conduit to be measured and cut using correct tools
checkpoint-status |  |  | checkpoint | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
checkpoint-status |  |  | checkpoint | All joins to be glued using PVC jointing cement
checkpoint-status |  |  | checkpoint | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3 way T, 4way
label | c336aca2-10e7-5995-84cb-7e6c569a22cf |  | note | Do not use corrugated conduit in decks
checkpoint-group |  |  | section | Conduit Installation (Fixing)
checkpoint-status |  |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
checkpoint-status |  |  | checkpoint | Conduit should be tied to bottom mat of steel
checkpoint-status |  |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | 5ffc636e-6ab3-52d8-b55e-5af231d9c525 |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-group |  |  | section | Cast In Items
checkpoint-status |  |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls Floor Boxes & Cast in Light's etc
checkpoint-group |  |  | section | Conduit Installation (Covering)
checkpoint-status |  |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-group |  |  | section | Earthing
checkpoint-status |  |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-group |  |  | section | Concrete Pour
checkpoint-status |  |  | checkpoint | Observe concrete pour with particular attention to critical area
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-sectioned |  |  | checklist | ITP-219 Fit Off Power, Switches and Accessories |  |  |  |  | Yes | ITP-219 Fit Off Power, Switches and Accessories | 53c0606d-23a7-42c8-b4b5-cc6f5ac470eb
checkpoint-group |  |  | section | Marking / Setting Out
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure all required distances are kept from other services as per AS 3000, e.g. in damp situations
checkpoint-group |  |  | section | Installation of Devices
checkpoint-status |  |  | checkpoint | Ensure the fitting is compliant with Australian standards
checkpoint-status |  |  | checkpoint | Install devices as per manufacturers recommendations
checkpoint-status |  |  | checkpoint | Ensure all devices are installed using the correct fixings and brackets
checkpoint-status |  |  | checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
checkpoint-status |  |  | checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
checkpoint-status |  |  | checkpoint | Ensure correct weather proof fittings are used where required
checkpoint-status |  |  | checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level.
checkpoint-group |  |  | section | Record Changes to Drawings
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built Drawings.
checkpoint-group |  |  | section | Visual Check Against Amended Drawings & Schedule
checkpoint-status |  |  | checkpoint | Visually inspect entire circuit for completeness.
checkpoint-status |  |  | checkpoint | Ensure fittings are protected if required
checkpoint-group |  |  | section | Visual Checks
checkpoint-status |  |  | checkpoint | Remove all rubbish - empty boxes etc.
checkpoint-status |  |  | checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the As built Drawings are Complete and Correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-flat |  |  | checklist | ITC-217.1 Light & Power Rough In |  |  |  |  | Yes | ITC-217.1 Light & Power Rough In | 602e523f-bcf6-4302-b624-c000f38e9949
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | 62c0e9c5-f6e0-5a3b-8c8c-bd254bbbd02c |  | textbox | Distribution Board No:
text | 24ed5e06-dbc8-5de7-a418-bd97f4b70671 |  | textbox | Circuit Description
text | 86d77a47-37c7-5139-b33e-105380584759 |  | textbox | Circuit No.
text | c285bb09-a32f-59ed-93f7-4e35839a8511 |  | textbox | Cable Size (mm2) & Type
text | 2eef3934-7a93-5f54-970c-28f9489b2afa |  | textbox | Feed Installed
text | 39cb3915-218e-5115-8fe6-c9d2d521a188 |  | textbox | Circuit Type (e.g GPO's, busduct lighting)
text | e2a741b1-a747-5c68-8147-e2ec26b8e7b4 |  | textbox | Number of points
text | 44085593-3bb6-5363-81ab-cddfa9cc3c4c |  | textbox | Circuit Length
boolean | dc4abb6f-08a4-552f-9b55-c361cd0f8f97 |  | tickbox | Twist & Tape / Lts Fit Off
boolean | 8d8e4317-e37c-5445-ae73-eb3c6659edc5 |  | tickbox | Cable ID both ends
boolean | 0d94bb7e-ea9f-556d-8a3f-50122aae77bd |  | tickbox | Adequate Support
boolean | b9d1ce4b-b2f4-51c5-9bfe-6c7a2e14fac3 |  | tickbox | Segregation Maintained
boolean | b1c0d87d-2b6b-53ac-a5b8-87a9a837b8f0 |  | tickbox | Drawing Markup
checkpoint-status |  |  | checkpoint | Signed Off
checklist-flat |  |  | checklist | ITC-226.1 Fibre Optic Cable |  |  |  |  | Yes | ITC-226.1 Fibre Optic Cable | 6c2cf9d4-6cf2-4a0f-b372-5e7a66692ac6
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | ce953ff2-66fc-580f-94fe-3e8cc009e286 |  | textbox | Cable No.
label | 95c50bcb-68d9-582f-a199-a3260b838203 |  | note | Cable identification drawing outlet number
text | f08e21ad-7f58-5000-b84f-ce5135cb63cc |  | textbox | From
text | 2ec08111-5c57-5fcb-9fb9-e79aa261c4aa |  | textbox | To
text | da174c71-4d05-5031-821d-e75e94440e5c |  | textbox | Cable Type
text | 5181d7bc-f10f-51b3-b82e-a5e84e902114 |  | textbox | Core
checkpoint-status |  |  | checkpoint | Materials conform to specification
checkpoint-status |  |  | checkpoint | Cable terminated and labelled
checkpoint-status |  |  | checkpoint | Cable Tested
text | 29c947c4-dc1e-5b2a-ad8d-9ac2f9d25807 |  | textbox | Light Source Testing
text | 85516d0a-358e-51c1-a488-204256b59f9b |  | textbox | OTDR
checkpoint-status |  |  | checkpoint | Drawings marked up to reflect as-installed
checklist-flat |  |  | checklist | ITC-224.2 Fit-Off Nurse Call |  |  |  |  | Yes | ITC-224.2 Fit-Off Nurse Call | 76a93c87-587c-4727-839c-d791afc7d8d8
checkpoint-status |  |  | checkpoint | Complete details below
text | 4e7dc7e1-1702-5ac5-8345-7ff33e7b63bf |  | textbox | Room #
text | 2d65ec75-3c56-573c-8690-1043a1bf9512 |  | textbox | Device
boolean | 81c65fe3-c483-535c-a961-bf7e40fda31a |  | tickbox | Field End labelled
boolean | 7fde23dc-4269-58be-8bd5-31a634012f55 |  | tickbox | Field End level to other services
boolean | fefc36bb-0b86-55ec-b991-29e53c99dedb |  | tickbox | Field End terminated
boolean | 53fd387d-f21a-526b-a530-126bed191cd2 |  | tickbox | Comms Room labelled
boolean | 639c9109-e252-51f1-81f0-9891de93ebe7 |  | tickbox | Comms Room Service Loop
boolean | c35d06f4-09a2-5e7f-b878-2761088c0784 |  | tickbox | Comms Room terminated
text | 6ec06d7b-d0ae-5727-81a4-34cfd07e7176 |  | textbox | Installer
text | 631ce1ab-115a-5801-afd3-7d37158c2e22 |  | textbox | Registered cabler licence number
checklist-flat |  |  | checklist | Testing and Commissioning |  |  |  |  | Yes | Testing and Commissioning | 883e638e-ca68-4e99-b45d-65863596744c
checkpoint-status |  |  | checkpoint | Attach testing & commissioning documents
checklist-sectioned |  |  | checklist | ITC-213.1 Switchboard Delivery & Pre Energisation Inspections |  |  |  |  | Yes | ITC-213.1 Switchboard Delivery & Pre Energisation Inspections | 8c5b0984-9033-44a3-b2ba-e26b076c7f03
checkpoint-group |  |  | section | 1. Workshop Pre-Delivery Inspection
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-group |  |  | section | 2. Installation
checkpoint-status |  |  | checkpoint | Fixed Correctly into Position ¦ Fixing Type
text | 5078f3e5-bf06-574b-9c7a-a5685063fb9b |  | textbox | Seismic Restrained
text | 10f474a0-e50e-53dc-8f3d-68d7eba87c58 |  | textbox | Type
text | cdfdc562-b24d-5efc-8760-cd8022b08ea3 |  | textbox | Clearances - AS 3000 - 2.10.2
checkpoint-group |  |  | section | 3. Visual Checks
checkpoint-status |  |  | checkpoint | Take photos of any damage
checkpoint-status |  |  | checkpoint | Internal Clean
checkpoint-status |  |  | checkpoint | Internal Fixtures, Meter's, CB's etc. Secure
checkpoint-group |  |  | section | 4. Tension Checks
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Circuit Breakers
checkpoint-status |  |  | checkpoint | Control
checkpoint-group |  |  | section | 5. Isolation Checks Completed
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Circuit Breakers
checkpoint-group |  |  | section | 6. Check Trip Settings & Protective Device Ratings
checkpoint-status |  |  | checkpoint | Review switchboard as built SLD & engineers discrimination study
checkpoint-group |  |  | section | 7. Correct Labelling Has Been Fixed
checkpoint-status |  |  | checkpoint | Review switchboard as built general arrangement and engineers reports
checkpoint-group |  |  | section | 8. Signage
checkpoint-status |  |  | checkpoint | External Doors, Trench Covers & Schedules
checkpoint-group |  |  | section | 9. Insulation & Continuity Test
checkpoint-status |  |  | checkpoint | Insulation & Continuity Test completed
checkpoint-group |  |  | section | 10. Reinstate All Covers / Panels
checkpoint-status |  |  | checkpoint | Switchboard Covers Secured
checkpoint-status |  |  | checkpoint | Ready to Energise
checklist-flat |  |  | checklist | ITC-214.1 Hauling of Cables |  |  |  |  | Yes | ITC-214.1 Hauling of Cables | 90b2ca9c-e91a-426d-a7cc-a252581a82c0
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | 41d0ccfe-59bf-5952-81ad-7d2ce1d54d7e |  | textbox | Cable Number
text | a062127f-9932-5b15-94ea-bfde02d81a9d |  | textbox | Plan Reference Info
checkpoint-status |  |  | checkpoint | Cable Description
text | 76d42f19-ea2c-58e1-a834-779a1ddee7de |  | textbox | Cable Name
checkpoint-status |  |  | checkpoint | New Cable
checkpoint-status |  |  | checkpoint | Reticulation System has been checked for structural integrity & spatial adequacy
checkpoint-status |  |  | checkpoint | Confirm Cable Size
text | 18b38fe2-c11a-5505-8760-0a827503dadc |  | textbox | Active
text | 22836306-4523-53e0-8b0f-aeae152c8c77 |  | textbox | Neutral
text | 1bb0b406-7054-5929-84e4-08f03680806f |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Confirm number of conductors / phase
text | 5a11d3c3-3e6e-5ec0-a54d-730083d3c564 |  | textbox | Active
text | d28d37a9-69f6-554d-9825-dfbd0ede07a1 |  | textbox | Neutral
text | 362aca79-3c88-50b4-afdc-613b09f35e21 |  | textbox | Earth
checkpoint-status |  |  | checkpoint | Hauling Method
text | 2cd331ac-3ec1-5dc6-8920-e23feb04369e |  | textbox | Manual
text | 27c2d1a4-e301-54c3-9817-b1a7133b6eaf |  | textbox | Winch
checkpoint-status |  |  | checkpoint | Cable Tie Type
text | 8580b0b4-347a-5b7c-b9da-6c95262d480e |  | textbox | Nylon
text | 99bd9ccb-718f-5b4e-be91-0e10812e6c88 |  | textbox | Steel
checkpoint-status |  |  | checkpoint | Confirm cable installation configuration
text | 1bbb440d-75cd-564e-8061-3cfd842d54ff |  | textbox | Trefoil Grouped
text | 0caa8257-1021-569c-a472-4a483d7c8fcd |  | textbox | 4C&E Circuit
text | c33d4994-07c8-571e-8fab-11a6f63635fb |  | textbox | Single Phase
checkpoint-status |  |  | checkpoint | Cable Labeled at both ends
text | ff41a9f1-8bf3-5968-a70e-dc764a743324 |  | textbox | Approx. Route Length (m)
checklist-sectioned |  |  | checklist | ITP-217 Light and Power Rough In |  |  |  |  | Yes | ITP-217 Light and Power Rough In | 94738ce5-dbf9-4953-a38b-33d880a0de32
checkpoint-group |  |  | section | Marking / Set Out
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced Not Required
checkpoint-status |  |  | checkpoint | Cable locations marked on floors and walls, if required
checkpoint-status |  |  | checkpoint | Cable locations marked on drawings for ease of locating where required
checkpoint-group |  |  | section | Installation of any required surface conduit
checkpoint-status |  |  | checkpoint | Surface conduit correct size to house required number and size of cables
checkpoint-status |  |  | checkpoint | Surface conduit fixed correctly and all required draw boxes installed
checkpoint-status |  |  | checkpoint | Ensure that no PVC Conduit has been installed passing through fire rated walls, breaking the integrity of the fire rating.
checkpoint-status |  |  | checkpoint | Ensure that steel conduit has been installed in areas where mechanical protection is required or where called for by the project documentation.
checkpoint-status |  |  | checkpoint | All surface conduit installed in a tradesman like manner.
label | 980646ab-a298-518e-8ca1-45e4e01021f3 |  | note | AS 3000:2018
checkpoint-group |  |  | section | Drilled Penetrations In Steel Structure
checkpoint-status |  |  | checkpoint | All penetrations are sized correctly
checkpoint-status |  |  | checkpoint | All penetrations are sprayed or painted with galvanising paint
checkpoint-status |  |  | checkpoint | All penetrations are bushed to prevent damage to cables passing through them
checkpoint-status |  |  | checkpoint | All penetrations are sealed to prevent the ingress of insects or vermin
label | 05afcf1e-97f4-57a2-b288-abd2b2992d47 |  | note | AS 3000:2018
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | All cable sizes selected correctly to suit the size of the supply required and to satisfy all standards, specs and regulations.
checkpoint-status |  |  | checkpoint | All cable sizes selected correctly to allow for Voltage Drop due to excessive cable run lengths to satisfy all standards, specs and regulations.
checkpoint-status |  |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status |  |  | checkpoint | All cables installed on cable ladder/tray are dressed and spaced correctly to minimise derating and satisfy all standards, specifications and regulations.
checkpoint-status |  |  | checkpoint | Do not leave any cable ends exposed / bare. Fredon Policy TWIST-PREPARE-TAPE
checkpoint-group |  |  | section | Visual Inspection
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-group |  |  | section | Record Changes to Drawings
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as as built drawings.
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct.
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records.
checklist-sectioned |  |  | checklist | ITP-227 Backbone Copper Cabling |  |  |  |  | Yes | ITP-227 Backbone Copper Cabling | 9bf46a7c-677c-488e-9a38-a754964a8388
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status |  |  | checkpoint | Ensure the cable is suitable for the environment (Gel filled, screened ect)
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Ensure that the latest drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable has adequate support and does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
label | 8f17448d-988a-5cb7-a523-ff869343126a |  | note | Fredon Shop Drawings AS S2009:2013 Manufactures Requirements
label | c89d46b2-b290-5161-b546-817ed4d857da |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Installation of Distribution Boards
checkpoint-status |  |  | checkpoint | Ensure the distribution frame is fastened securely and at appropriate height for future maintenance and expansion
label | fb64b5fd-65e5-571d-8e50-e886bad63916 |  | note | Fredon Shop Drawings AS S2009:2013 Manufactures Requirements
label | e93b7b53-1692-58fb-ae78-5195eea3c258 |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Termination
checkpoint-status |  |  | checkpoint | Ensure that all cores are punched down with the manufactures punch down tool and in the correct colour Sequence
label | a9b2cb1a-e6a1-5fed-b373-e0f033936b30 |  | note | Fredon Shop Drawings AS S2009:2013 Manufactures Requirements
label | 3cd5652e-6f2c-597d-a2b6-3ce80181e543 |  | note | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Test each pair on the disconnect module for correct wire mapping
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Ensure that the record book is updated and installed within the Distribution Frame
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned |  |  | checklist | ITP-222 Horizontal Cabling |  |  |  |  | Yes | ITP-222 Horizontal Cabling | 9c116e6f-1a91-4b4a-9ab5-86940d328def
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status |  |  | checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status |  |  | checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-group |  |  | section | Horizontal Cabling Rough-in
checkpoint-status |  |  | checkpoint | Ensure that the latest services and coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
checkpoint-group |  |  | section | Visual Inspection of Rough In
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-group |  |  | section | Cabinet
checkpoint-status |  |  | checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
checkpoint-status |  |  | checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
checkpoint-status |  |  | checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
checkpoint-group |  |  | section | Horizontal Cabling Fit-off (Field)
checkpoint-status |  |  | checkpoint | Ensure that all Field End Cabling has been labelled, terminated and is level to other services
checkpoint-group |  |  | section | Horizontal Cabling Fit-off (Communications Room)
checkpoint-status |  |  | checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated has been labelled
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Ensure that Fluke DSX Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their correct label on cabinet and latest revision drawings
checkpoint-group |  |  | section | Test Results Recording
checkpoint-status |  |  | checkpoint | Ensure all test results are downloaded and stored in both their native format and as PDF's or safe keeping
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records
checklist-flat |  |  | checklist | ITC-212.3 Earthing |  |  |  |  | Yes | ITC-212.3 Earthing | 9f383cbf-01dd-432b-89cc-7bd7ed83ca36
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | e33003ef-c73f-5e36-96ca-1b699a958e86 |  | textbox | Distribution Board No:
text | 64150151-cc88-54a6-81e2-68d76c452a74 |  | textbox | Earth Point Origin
text | 825fae0a-f4e9-5d60-8258-876dbb2db0c8 |  | textbox | Destination
text | a588b8e7-7f94-585d-9a95-bbfd361f4b2a |  | textbox | Correct Location to Drawing
text | 30d699c9-4778-5c58-9e51-2f692b384938 |  | textbox | Protective Earth Size
text | 69cdd7d5-9f7d-5447-b521-52c024be30fd |  | textbox | Earth Joint Secured
text | 3a61bfed-d170-5b03-bb51-cb87e41a7da8 |  | textbox | Continuity
label | 554f75fa-7e1f-5335-8bb3-2e9c8fd8d0fe |  | note | Equipotential = <.5Ω
label | 407f0d4d-8360-55c6-8562-1469aa0b0300 |  | note | General Earthing = <1Ω
checklist-sectioned |  |  | checklist | ITP-220 In-Ground Works |  |  |  |  | Yes | ITP-220 In-Ground Works | b3e9fa67-5df6-429e-8626-d3b7a44d896f
checkpoint-group |  |  | section | Mark out route
checkpoint-status |  |  | checkpoint | Criteria as per Electrical Services Specification issued by (insert consultant name) COMPLETE ITC-220.1 Section 1
label | 37b53ad2-7024-5cba-93a6-5e73f2b10779 |  | note | AS 3000:2018
checkpoint-group |  |  | section | Pothole / Service Location
checkpoint-status |  |  | checkpoint | Mark up all documentation identifying any service clashes
checkpoint-status |  |  | checkpoint | Coordinate with others
checkpoint-status |  |  | checkpoint | Survey level documents
checkpoint-status |  |  | checkpoint | Ensure proposed trench route is clearly identified and all existing and proposed new buried services have been exposed / considered.
holdpoint |  |  | signoff | Approval to dig from Builder (get permit)
checkpoint-group |  |  | section | Dig Permit
checkpoint-status |  |  | checkpoint | Ensure Builder issues permit to dig.
checkpoint-group |  |  | section | Trenching Correct Size / Alignment / Depth (Use Datum Points)
checkpoint-status |  |  | checkpoint | COMPLETE ITC-220.1 Section 4
checkpoint-group |  |  | section | Correct Conduit Size / Alignment / Spacing
checkpoint-status |  |  | checkpoint | COMPLETE ITC-220.1 Sections 5 & 6
holdpoint |  |  | signoff | Check ITC-220.1 has been completed to this point
checkpoint-group |  |  | section | Trenching detail & identification for as built documentation
checkpoint-status |  |  | checkpoint | Photograph trench detail showing correct installation method.
checkpoint-status |  |  | checkpoint | Photograph trench detail showing correct depth.
holdpoint |  |  | signoff | COMPLETE ITC-220.1 Section 7
checkpoint-group |  |  | section | Rag Bolts & Light Footings
checkpoint-status |  |  | checkpoint | Ensure Augered hole meets minimum engineered requirements
checkpoint-status |  |  | checkpoint | Ensure the rag bolt and footing is completely filled with concrete and finished with FFL
checkpoint-group |  |  | section | Pit Installation
checkpoint-status |  |  | checkpoint | Ensure pit is installed adjacent to path/building and to FFL using surveyors markers
checkpoint-status |  |  | checkpoint | Smoothen edges of conduit penetrations or installed manufactured bell mouths to allow cables to be neatly pulled through pits safely
checkpoint-group |  |  | section | GFIS Trenching Detail for as built
checkpoint-status |  |  | checkpoint | Engage surveyors to carry out these works.
checkpoint-status |  |  | checkpoint | COMPLETE ITC-220.1 Section 8
checkpoint-group |  |  | section | Backfilling / Compaction
checkpoint-status |  |  | checkpoint | COMPLETE ITC-220.1 Section 9
checkpoint-group |  |  | section | Trench Identification Marker Plates
checkpoint-status |  |  | checkpoint | As Built Drawings
checkpoint-status |  |  | checkpoint | COMPLETE ITC-220.1 Section 10
checkpoint-group |  |  | section | Hand Over Submission & Documentation
checkpoint-status |  |  | checkpoint | O&M Manual
checklist-flat |  |  | checklist | ITC-213.2 Switchboard Inspections: Continuity & Isolation Functional Checks, Insulation Resistance Checks |  |  |  |  | Yes | ITC-213.2 Switchboard Inspections: Continuity & Isolation Functional Checks, Insulation Resistance Checks | b739cbf2-7750-433c-b5a5-c46b067e2234
checkpoint-status |  |  | checkpoint | Attach any relevant photos & documents
text | af092149-ee2c-526b-a0df-febeba14bd43 |  | textbox | Item
text | 6340e41f-8e1f-5b06-a039-30e142a9f79c |  | textbox | CB#
text | 7ff23ce8-ccb4-5096-b17f-5b1060d041b1 |  | textbox | CB Size
checkpoint-status |  |  | checkpoint | Open Continuity (MΩ)
text | a40a3173-4ff3-54ea-823f-52a0f9fa0874 |  | textbox | Red to Red
text | ac522bab-538a-5321-8fe5-dd181ea5386b |  | textbox | White to White
text | 46a50e6c-5e42-530c-90f4-0cec0d270ab2 |  | textbox | Blue to Blue
checkpoint-status |  |  | checkpoint | Closed Continuity (MΩ)
text | a8a0c823-d0da-51b1-ba18-3fb9f97ba65d |  | textbox | Red to Red
text | 5bf4f52f-ec20-5dec-9c6e-94cf9556166f |  | textbox | White to White
text | 6348d72e-7ce5-5a88-903d-9ba72acd4d3b |  | textbox | Blue to Blue
checkpoint-status |  |  | checkpoint | Open Continuity (MΩ)
text | 24e4742d-b44e-5889-ba6c-17aa8da02697 |  | textbox | Red to Red
text | b06764be-58a7-5b67-83cb-6b81b7a3c97b |  | textbox | White to White
text | a07b33b4-1394-5d1d-b766-14d7cd2127d9 |  | textbox | Blue to Blue
checkpoint-status |  |  | checkpoint | Insulation Resistance Pre-Energisation Switchboard Internal (MΩ)
text | e1bbec5d-03f3-50dc-a08b-2a9d08c7a40a |  | textbox | Red to Blue
text | 186f882d-fa79-58ea-9dd7-062f04e83b09 |  | textbox | White to Red
text | 26958462-a5f1-5385-8723-14a001ce1eef |  | textbox | Blue to White
text | b2b771ce-c2db-584d-a98b-cc9a9127d4ef |  | textbox | Red to Earth
text | c398f0f4-24ab-50ef-ae41-4710daf23225 |  | textbox | White to Earth
text | f276614e-767b-5097-a63f-fa8c7178e6b4 |  | textbox | Blue to Earth
text | b940bf29-d39f-569f-badb-50b55de57722 |  | textbox | Neutral to Earth
checklist-sectioned |  |  | checklist | ITP-215 Cable Tray / Ladder |  |  |  |  | Yes | ITP-215 Cable Tray / Ladder | bc9e1d88-58fe-452f-b2df-73117e3dc77e
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-group |  |  | section | Metering / Setting Out
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status |  |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-group |  |  | section | Cable Tray / Ladder Installation
checkpoint-status |  |  | checkpoint | Correct fixings have been used for the installation of support rods e.g. HKDs, Drop In Anchors. Fixings have been knocked in correctly with appropriate punch tool.
checkpoint-status |  |  | checkpoint | Load bearing capacity has been calculated and confirmed - PM to have cable support technical submission to confirm.
checkpoint-status |  |  | checkpoint | Cable tray / ladder has been supported at intervals not exceeding manufacturers specifications.
checkpoint-status |  |  | checkpoint | Seismic restraints have been installed in accordance with engineered approvals.
checkpoint-status |  |  | checkpoint | Cable tray / ladder has been installed at the correct height in order to coordinate with other services and ceiling heights.
checkpoint-status |  |  | checkpoint | Cable tray / ladder, which will be carrying fire rated submains, has had fire rated ladder and supports installed to manufacturers specifications
checkpoint-status |  |  | checkpoint | All threaded rods have been cut to a maximum of 30 mm below the fixing nut on completion of installation
checkpoint-status |  |  | checkpoint | All cuts to cable/tray ladder and supports have been galvanised to prevent corrosion
label | 933f2bbd-ee8a-5e6a-a27a-c54a694901ee |  | note | Ensure the Cable tray has been bonded to earth securely NOTE: Any continuity readings to be completed on ITC-250.3
checkpoint-group |  |  | section | Visual inspection
checkpoint-status |  |  | checkpoint | Visually inspect the cable tray/ladder run to ensure all above requirements have been fulfilled
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built drawings.
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checklist-flat |  |  | checklist | ITC-222.3 Cabinets |  |  |  |  | Yes | ITC-222.3 Cabinets | dfc9a2f6-642a-4a95-82a5-d20c9e4d7060
checkpoint-status |  |  | checkpoint | Construction drawing is latest revision
checkpoint-status |  |  | checkpoint | Cabinet positioning marked
checkpoint-status |  |  | checkpoint | Cabinet conforms to specification
checkpoint-status |  |  | checkpoint | Cabinet & accessories installed & earthed
checkpoint-status |  |  | checkpoint | Cabinet & accessories labelled
checkpoint-status |  |  | checkpoint | Drawings marked up to reflect as-installed
checkpoint-status |  |  | checkpoint | Final Acceptance - attach Fredon representative & client signature