## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | ITC-219.1 Fit Off Power, Switches & Accessories |  |  |  |  | Yes | ITC-219.1 Fit Off Power, Switches & Accessories | 0bf5f52b-770c-4d1e-8641-751bee4e079c
checkpoint | Attach any relevant photos & documents
text | Outlet Number
text | Equipment Type
text | Quantity
text | Cable Size
checkpoint | Set Out Comms Services Plan
checkpoint | Set Out Architectural / Other Serices Plan
checkpoint | Mounting Arrangement
bool | Plaster Clip
bool | Recessed Fire Box
bool | Acoustic
bool | Surface Mounted
checkpoint | Ready for use
text | Label Installed
checklist-sectioned | ITP-219 Fit Off Power, Switches and Accessories |  |  |  |  | Yes | ITP-219 Fit Off Power, Switches and Accessories | 53c0606d-23a7-42c8-b4b5-cc6f5ac470eb
section | Marking / Setting Out
checkpoint | Ensure that the latest service drawings are being referenced
checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint | Ensure all required distances are kept from other services as per AS 3000, e.g. in damp situations
section | Installation of Devices
checkpoint | Ensure the fitting is compliant with Australian standards
checkpoint | Install devices as per manufacturers recommendations
checkpoint | Ensure all devices are installed using the correct fixings and brackets
checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
checkpoint | Ensure correct weather proof fittings are used where required
checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level.
section | Record Changes to Drawings
checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As built Drawings.
section | Visual Check Against Amended Drawings & Schedule
checkpoint | Visually inspect entire circuit for completeness.
checkpoint | Ensure fittings are protected if required
section | Visual Checks
checkpoint | Remove all rubbish - empty boxes etc.
checkpoint | Check that all ceilings, walls and floors are left neat and tidy and without any damage. IF DAMAGE OCCURS ADVISE FREDON SITE MANAGER IMMEDIATELY
section | Final Inspection
checkpoint | Cross check and verify that the As built Drawings are Complete and Correct.
checkpoint | Verify all inspections are complete and collate records.
checklist-sectioned | ITP-224 Nursecall |  |  |  |  | Yes | ITP-224 Nursecall | 022c927a-a980-4cb8-b65b-e54a30452971
checkpoint-group | Coordination
checkpoint-status | Please attach marked up drawing
checkpoint-status | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status | Prior to installation submit numbered shop drawings for review to the satisfaction of services engineer
checkpoint-group | Cabling Rough-In
checkpoint-status | Ensure latest services & co-ordinated drawings are being referenced
checkpoint-status | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status | Visual inspection of rough in carried out to ensure completion.
checkpoint-status | All relevant drawings checked to ensure that all services have been allowed for.
checkpoint-group | Field End Nurse Call Fit-off
checkpoint-status | Ensure that all Field End Cabling has been labelled, terminated to manufactures requirements and is level to other services
checkpoint-group | Head End Nurse Call Fit-off
checkpoint-status | Ensure that cables are dressed neatly and loomed into their final location for termination
checkpoint-status | Ensure that all Head End Cabling has been labelled, terminated to manufactures requirements and is carried out to Manufactures Shop Drawings
checkpoint-group | Programming
checkpoint-status | Ensure that all Nurse Call stations are addressed correctly as per latest drawings and Align with the monitor associated to them
checkpoint-group | Final Inspection
checkpoint-status | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status | Verify all inspections are complete and collate record
checklist-flat | ITC-224.1 Nurse Call Installation |  |  |  |  | Yes | ITC-224.1 Nurse Call Installation | 078fd089-3023-4459-a628-bb938e0608b8
checkpoint | Complete details below
text | Source
text | Destination
bool | Less than 90m
bool | Bend radius not exceeded
bool | Labelled at both ends
bool | Adequate cable support
bool | Service loop / Goose neck
bool | Segregation from other services
text | Installer
text | Registered cabler licence number
text | Hold Point
checkpoint | Attach signature
checklist-flat | ITC-224.2 Fit-Off Nurse Call
checkpoint | Complete details below
text | Room #
text | Device
bool | Field End labelled
bool | Field End level to other services
bool | Field End terminated
bool | Comms Room labelled
bool | Comms Room Service Loop
bool | Comms Room terminated
text | Installer
text | Registered cabler licence number
checklist-sectioned | ITP-226 Fibre Optic Cable |  |  |  |  | Yes | ITP-226 Fibre Optic Cable | 47be5f1f-a4bc-4046-9fe3-78256c29419d
checkpoint-group | Coordination
checkpoint-status | Please attach marked up drawing - Please take photo of title block
checkpoint-status | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-status | Ensure pit and underground piping are clear of obstructions and have the appropriate access and barricading
checkpoint-status | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint-status | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
checkpoint-group | Cable Installation
checkpoint-status | Ensure that the latest services and coordinated drawings are being referenced
checkpoint-status | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status | Ensure the cable pulling strength is not exceeded as per manufacturer's recommendations
checkpoint-status | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
label | Fredon Shop Drawings AS S2009:2013 Manufactures Requirements
label | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group | Termination
checkpoint-status | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
checkpoint-status | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
checkpoint-status | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
checkpoint-status | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
checkpoint-status | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
checkpoint-status | Ensure fobot is securely placed inside enclosure and dust caps installed
label | Fredon Shop Drawings AS S2009:2013 AS 3080 Manufactures Requirements
label | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group | Testing
checkpoint-status | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
label | Fredon Shop Drawings AS S2009:2013 AS 3080 Manufactures Requirements
label | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
checkpoint-group | Test Results Recording
checkpoint-status | Ensure all test results are downloaded and stored in both their native format and as PDF's or safe keeping
label | SDC-NSD-COM-GSS-401-1.4-AU Communications general specification
label | AS S2009:2013 AS 3080
checkpoint-group | Final Inspection
checkpoint-status | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint-status | Cross check and verify that the as built drawings are complete and correct
checkpoint-status | Verify all testing are complete and collate records
checklist | ITP-222 Horizontal Cabling |  |  |  |  | Yes | ITP-222 Horizontal Cabling | 9c116e6f-1a91-4b4a-9ab5-86940d328def
section | Coordination
checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint | Ensure that all new installations numbering and labelling systems meet specification and have been approved by the client
checkpoint | Prior to installation submit numbered Communications shop drawings for review to the satisfaction of services engineer
section | Horizontal Cabling Rough-in
checkpoint | Ensure that the latest services and coordinated drawings are being referenced
checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
section | Visual Inspection of Rough In
checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint | All relevant drawings checked to ensure that all services have been allowed for.
section | Cabinet
checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
section | Horizontal Cabling Fit-off (Field)
checkpoint | Ensure that all Field End Cabling has been labelled, terminated and is level to other services
section | Horizontal Cabling Fit-off (Communications Room)
checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
checkpoint | Ensure that all cabling is terminated has been labelled
section | Testing
checkpoint | Ensure that Fluke DSX Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their correct label on cabinet and latest revision drawings
section | Test Results Recording
checkpoint | Ensure all test results are downloaded and stored in both their native format and as PDF's or safe keeping
section | Final Inspection
checkpoint | Ensure that all changes made to the original drawing have been marked and noted on the Working Drawing located in the Site Office. These drawings MUST be kept updated for use as As Built Drawings.
checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint | Verify all inspections are complete and collate records
checkpoint | Verify all testing are complete and collate records