## Proj Resources - Syfon
type | name | values | prefix | postfix | Template Name | Template Id
checklist | A9681-ITC-01 - Syfon Drainage
section | Installation
checkpoint | Spec. Ref: HY-SP-002
text | Drawing Ref & Revision #
tickbox | Stormwater/Syfonic
text | Other:
checkpoint | Fabricated Pipework
note | Acceptance Criteria / Reference: In accordance with 6.4 of Syfon Systems CMP
note | Inspection Type: Normal Inspection
checkpoint | Installation of Pipework
note | Acceptance Criteria / Reference: Approved shop drawings
note | Inspection Type: Normal Inspection
checkpoint | Railing System
note | Acceptance Criteria / Reference: Bracket spacing in accordance with 6.4 of Syfon Systems CMP
note | Inspection Type: Normal Inspection
note | Refer to syfon shop drawings
checkpoint | Pipe Material Correct
note | Acceptance Criteria / Reference: As per approved shop drawings
tickbox | HDPE
note | Inspection Type: Normal Inspection
checkpoint | Testing & Commissioning
note | Acceptance Criteria / Reference: AS3500-3
note | Test Type:
tickbox | Hydrostatic Test as per AS-NZS 3500-3 (2018) Stormwater Drainage System
tickbox | Air Test as per AS-NZS 3500-3 (2018) Stormwater Drainage System
note | Inspection Type: Hold Point, Test, Witness
note | REF TEST CRITERIA; Hydrostatic Test - Fill with water and must show no leaks Air Test - To hold at 30kPa for a minimum of 3 minutes
checkpoint | Pipework Labelling
note | Acceptance Criteria / Reference: As per AS1345
note | Inspection Type: Normal Inspection
checkpoint | Acoustic Lagging
note | Acceptance Criteria / Reference: Secure and full coverage
note | Inspection Type: Normal Inspection
checkpoint | As Built Information Recorded
note | Recorded on shop drawings as required prior to concealment
note | Inspection Type: Shop Drawings
checkpoint | Sign-Off Completed
note | Inspections carried out by
text | Name
text | Organisation
note | Signature(s) attached below

## ITP 005 Changes
type | name | values | prefix | postfix | Template Name | Template Id
checklist | ITP 005 - Fit-Off, Fixtures & Fittings (NFH)
section | Installation
checkpoint | Spec. Ref: HY-SP-002
text | Drawing Ref & Revision #
text | Service & Fitting Types:
checkpoint | Set Out and Alignment of Rough-ins
note | Acceptance Criteria / Reference: Approved installation drawings
note | Inspection Type: Hold Point
checkpoint | Correct Items Installed
note | Acceptance Criteria / Reference: As per approved shop drawings
note | Inspection Type: Hold Point
checkpoint | Items are of High Quality
note | Acceptance Criteria / Reference: No apparent damage - free of cracks, chips, crazing or other defects
note | Inspection Type: Normal Inspection
checkpoint | Sealant
note | Acceptance Criteria / Reference: Sealant is neat, correct type, colour and volume
note | Inspection Type: Normal Inspection
checkpoint | Fittings Installed Straight
note | Acceptance Criteria / Reference: Visual inspection
note | Inspection Type: Normal Inspection
checkpoint | Access Panels are Installed
note | Acceptance Criteria / Reference: As per approved installation drawings
note | Inspection Type: Normal Inspection
checkpoint | WC's
note | Acceptance Criteria / Reference: Fixed with levelling brackets after floor installation, seat lid is secure
note | Inspection Type: Normal Inspection
checkpoint | Items all Operate Correctly
note | Acceptance Criteria / Reference: Check each item for operation – hot and cold if applicable and have no leaks
note | Inspection Type: Testing
note | Refer commissioning plan for disinfection and flushing of mains, TMV commissioning and cross connections potable & recycled water
checkpoint | Sign-Off Completed
note | Inspections carried out by
text | Name
text | Organisation
note | Signature(s) attached below