## res_1630-P200-SYM-QAC-ITP-0021.
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CC0394 - ITP-009 - Fire Service Installation & Commissioning | itp |  |  |  |  | CC0394 - ITP-009 - Fire Service Installation & Commissioning REV1
section | Lot Conformance.
checkpoint | Lot Conformance
select | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | Lot opened date:
text | Lot opened by:
text | Date lot closed:
button | NCR raised? | Yes, No
text | NCR Raised Date:
button | NCR closed? | Yes, No
text | NCR Closed Date:
text | NCR Number:
text | Comments
holdpoint | AUTHORITY HOLDPOINT
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine Lot Size
label | Ref docs - AS3500
label | Acceptance criteria -
textbox | Pipe / lot length:
button | Acceptance | Yes,No,N/A
label | See Work Lot Map
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Work Lot Map
checkpoint | 1.2 - Survey Set-out
label | Ref docs - IFC Drawings
label | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all fire lines including hydrants and risers.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
checkpoint | 1.3 - Approved Material Type
label | Ref docs - IFC Drawings AS3500
label | Acceptance criteria - All materials selected in accordance with AS4130 and RJE civil specification and drawings.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
section | 2.0 In Process Works
checkpoint | 2.1 - Excavation
label | Ref docs - IFC Drawings AS3500, Excavation permit
label | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | ○ Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 2.2 - Removal of Obstructions
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Remove obstructions including roots, stumps, boulders, and the like which may, in the opinion of Symal, interfere with the proper functioning of the service.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 2.3 - Bedding
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Pipes should be bedded and supported by class 3 quarry material with a minimum thickness of 75mm.
label | ○ 5-10mm crushed rock or sand shall be used as the haunching material.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
section | 3.0 Installation of pipes
checkpoint | 3.1 - Pipe Installation
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Work shall be carried out by and under the direct supervision of appropriately licenced personnel.
label | ○ During construction, temporarily seal open ends of pipes and valves to prevent the entry of foreign matter into pipe systems.
label | ○ Install piping in straight lines at uniform grades without sags.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 3.2 - Electrofusion Weld fittings/pipe/couplings
label | Ref docs - as per manufacturers recommendations
label | Acceptance criteria - Ensure pipe is cleaned and scraped prior to welding.
label | ○ Ensure pipe is fixed firmly in position.
label | ○ Allow curing time as per specific fittings recommendations, Visually check all fittings have been welded.
label | Acceptance - Prior to Backfilling
label | Key - W
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Electrofusion welder calibration certificate.
checkpoint | 3.3 - Cover
label | Ref docs - IFC Drawings and specifications AS3500.1
label | Acceptance criteria - Minimum depth of cover for buried pipes: 600mm to finished surface.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As-Built Attached
section | 4.0 Backfill
checkpoint | 4.1 - Backfill Material
label | Ref docs - IFC Drawings and specifications AS3500
label | Acceptance criteria - After pipes & fittings have been set in the correct position and jointed, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
label | ○ Trench backfilled with selected clean excavated material, or the purchased material bought to site.
label | ○ 5mm Dust Compliant for bedding
label | ○ BACKFILL Overlay WITH 20mm nominal size class 3 crushed rock
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material dockets
checkpoint | 4.2 - Layer Thickness
label | Ref docs - IFC Drawings AS3500
label | Acceptance criteria - Backfill material must be placed and compacted in layers not exceeding 300mm.
label | ○ Backfill trenches as soon as possible after approval of laid and bedded service.
label | ○ Allow adequate cover over pipe (minimum 600mm)
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
checkpoint | 4.3 - Compaction
label | Ref docs - IFC Drawings AS1289
label | Acceptance criteria - Compaction to be undertaken using hand methods only for first 300mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 4.4 - Preliminary Pressure testing
label | Ref docs - IFC Drawings RJE NOE AS3500.1
label | Acceptance criteria - Sign-off items 1.0 – 4.3.
label | ○ RJE NOE
label | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa. Pressure deviation to be not more than +/- 35Kpa.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | RJE Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | RJE NOE
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 Fire Hydrant Install
checkpoint | 5.1 - Survey set-out
label | Ref docs - IFC Drawings
label | Acceptance criteria - Prior to the commencement of works, the contractor shall engage a suitably qualified surveyor to set out the works and clearly mark its limits.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
checkpoint | 5.2 - Approved Material Type
label | Ref docs - IFC Drawings AS3500
label | Acceptance criteria - Materials used for the installation of Hydrants to be in accordance with AS3500
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
checkpoint | 5.3 - Fire Hydrant Install
label | Ref docs - IFC Drawings
label | Acceptance criteria - Ensure fire hydrants are located such that they do not impact vehicle access.
label | ○ Bollards are to be installed for physical protection.
label | ○ Confirm valve operability.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
section | 6.0 Conformance Check
checkpoint | 6.1 - Clean & Finish
label | Ref docs - IFC Drawings
label | Acceptance criteria - On completion, each line shall be free from dirt, debris, or other impediments.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 6.2 - Testing
label | Ref docs - AS3500.1
label | Acceptance criteria - All pipe and hydrants to be pressure tested in accordance with AS3500.1
label | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | RJE Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test certification
bool | Calibration certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.3 - As-Builts
label | Ref docs - IFC Drawings
label | Acceptance criteria - Accurately record the routes of all underground pipes before backfilling.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As-Built Attached