## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | CS-4072 - ITS Pit Inspection Record | [5 empty] | CS-4072 - ITS Pit Inspection Record
checkpoint-no-status | ITS Pit Inspection Record
textbox | Project No.
textbox | Drawing No (& Rev No):
textbox | Pit #:
checkpoint | Pull Pit/ Joint chamber set out by surveyor
textbox | Initials:
date | Date:
label | Comments: Survey Receipt
checkpoint | All existing services exposed and identified before trenching
textbox | Initials:
date | Date:
checkpoint | Depth shall be determined prior to excavating
textbox | Initials:
date | Date:
label | Comments: Grass/Concrete/Asphalt areas – Lid must be flush to FL
label | ○ Planted areas – Lid must be 100mm above ground level with a sloping concrete apron
checkpoint | Slopes >30 lid shall be 100mm above GL on the upper side. Slopes 10-30 lid shall be flush with the GL on the upper side.
textbox | Initials:
date | Date:
checkpoint | Bedding shall be 150mm of GAP65 compacted
textbox | Initials:
date | Date:
checkpoint | Ducts shall be connected perpendicular to the chamber wall.
textbox | Initials:
date | Date:
label | Comments: Ducts must not protrude more than 100mm into the chamber
checkpoint | Seal ducts using suitable epoxy resin (outside) to ensure water tight
textbox | Initials:
date | Date:
label | Comments: All joints must be smoothed off to form a fillet between the duct & chamber wall
checkpoint | Ensure all ducts are capped inside the chambers to keep water tight
textbox | Initials:
date | Date:
checkpoint | Ensure backfill material is correct and compacted
textbox | Initials:
date | Date:
label | Comments: Berm – sand/excavated material 200mm lifts CIV of 8
label | ○ Carriageway – GAP65 200mm lifts 95% MDD
checkpoint | Top 300mm of the chamber shall be concreted to a width of 150mm around the lid
textbox | Initials:
date | Date:
checkpoint | Roof, collar & lid installed to manufacturer’s requirements
textbox | Initials:
date | Date:
checkpoint | Clean out jointing chambers at completion.
textbox | Initials:
date | Date:
label | Comments: Remove any construction materials or contaminates from Pit
checkpoint | The above works have been inspected and are considered compliant with the drawings, specifications and instructions
textbox | Name:
textbox | Position:
date | Date:
holdpoint | Sign: