## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | CS-4105 - Road Lighting & Cable Installation Record | [5 empty] | CS-4105 - Road Lighting & Cable Installation Record
checkpoint-no-status | Road Lighting Trench & Cable Installation Record
textbox | Project No.
textbox | Drg No:
textbox | Rev No:
textbox | Chainage/Road Light No.:
checkpoint | Road Light Locations set out by Surveyor.
textbox | Initials:
date | Date:
label | Comments: Consistency with Construction Drawing, Details and Notes.
checkpoint | Pothole existing services that cross the line of the trench.
textbox | Initials:
date | Date:
checkpoint | Permit to dig obtained and underground services marked out.
textbox | Initials:
date | Date:
checkpoint | Trench location marked out with offset pegs and checked that it clears other services.
textbox | Initials:
date | Date:
checkpoint | Inspect trench and ensure it is required depth below Ground level and free from obstruction.
textbox | Initials:
date | Date:
label | Comments: 600mm below open areas and under footpaths, 900m under roadways and free from obstruction
checkpoint | Ensure the correct cable is being placed in the trench and check if direct buried or duct required.
textbox | Initials:
date | Date:
label | Comments: Ducting is required under roadways, within bridges and when entering concrete foundations
checkpoint | Ensure cable ducts (where required) are clear of obstructions, fitted with Draw Wires and are easily accessible for cable drawing.
textbox | Initials:
date | Date:
checkpoint | Ensure cables are laid without sharp kinks and loops for connection are provided at Pole locations.
textbox | Initials:
date | Date:
label | Comments: 3m loop on continuous cable, 1.5m loop at cable ends
checkpoint | As built survey Cable in the trench. Ensure the As Built information includes the number and the type of cables and circuit numbers
textbox | Initials:
date | Date:
checkpoint | Cables buried directly into the ground shall be enclosed.
textbox | Initials:
date | Date:
label | Comments: Min. 50mm of Sand on all sides of the cables or Soil which passed through sieve no greater than 10mm
checkpoint | Ensure trench is backfilled and compacted by hand ramming for the first two layers, followed by power consolidation.
textbox | Initials:
date | Date:
label | Comments: Depth of cover:
label | ○ Open areas or under footpaths = 600mm Under roadways = 900mm
label | ○ Check compaction with Clegg hammer every 20m
checkpoint | Ensure 100mm Wide Orange Polythene Warning Tape is installed.
textbox | Initials:
date | Date:
label | Comments: 150mm below finished surface of trench.
checkpoint | The above works have been inspected and are considered compliant with the drawings, specifications and instructions
label | Position: Site Engineer
textbox | Site Engineer - Name:
date | Site Engineer - Date:
label | Position: CPS Engineer
textbox | CPS Engineer - Name:
date | CPS Engineer - Date:
holdpoint | Sign: