## Project Structure
EXAMPLE SHEET
Site QA | Building Zones (if applicable) | List site levels here (delete as required) | List sections required here | Checklists - List what ITPs need to be added here. Use tab Master''
|  | Level 7 | Lights | ITP007 Lighting Wiring Rough In
1 - Refer to drawing to determine cable support route and check separation from data/comms services
2 - Determine cable size
3 - Cable sizes max length
4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
5 - Install cable support system
6 - Check cable size/type/colour
7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
9 - Fix cables to support system
10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
12 - All lighting points and switches have been wired as per drawings
13 - All lighting points and switches have been marked on the site as built drawing
14 - Height and location have been confirmed for each lighting points and switches
ITP010 Lighting Installation and Fit Off
1 - Check drawings for quantity, brand, type and colour
2 - Each circuit is terminated at the db and protected by the correct protective device
3 - Location/compliance wet areas, hazards etc. Mounting heights,
4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
5 - Fit off final light fittings
6 - Functional test carried out on each outlet
7 - Cover plates (if required)
8 - Install label (if a specified requirement)
9 - All lights and switches marked on the site as build’s
|  |  | Power | ITP006 Power Wiring Rough In
1 - Refer to drawing to determine cable support route and check separation from data/comms services
2 - Determine cable size
3 - Cable sizes max length
4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
5 - Install cable support system
6 - Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
9 - Fix cables to support system
10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
12 - All outlets have been wired as per drawings
13 - All outlets have been marked on the site as built drawing
14 - Height and location have been confirmed for each outlet
ITP009 Power Installation and Fit Off
1 - Check drawings for quantity, brand, type and colour
2 - Each circuit is terminated at the db and protected by the correct protective device
3 - Location/compliance wet areas, hazards etc. Mounting heights,
4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
5 - Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use shroud. Each circuit must be fitted off completely.
6 - Fit off final appliances
7 - Functional test carried out on each outlet
8 - Cover plates (if required)
9 - Install label (if a specified requirement)
10 - All outlets & appliances marked on the site as build’s
|  |  | Data | ITP008 Data Wiring Rough In
1 - Refer to drawing to determine cable support route and check separation from power services
2 - Determine cable type
3 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
4 - Install cable support system
5 - Install and identify cables.
6 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
7 - Fix cables to support system
8 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
9 - All outlets have been wired as per drawings
10 - All outlets have been marked on the site as built drawing
11 - Height and location have been confirmed for each outlet
ITP011 Data Installation and Fit Off
1 - Check drawings for quantity, brand, type and colour
2 - Fit off and fix outlets, terminations have been checked and all terminations are correct and secure in all outlets
3 - Outlets have all been secured in place and levelled
4 - All cabling has been tested using the fluke data tester
5 - Each cable has been correctly installed and terminated in the patch panel
6 - Cover plates (if required)
7 - Install label (if a specified requirement)
8 - All outlets & appliances marked on the site as build’s
|  |  | Emergency Lights | ITP0012 Exit & Emergency Light Installation
1 - Delivery check for damage and correct quantities
2 - Locations coordinate with other services
3 - Marking out (if required) - refer to reflected ceiling plan for locations
4 - Plug in or fit off light fit-off data cable if applicable
5 - Number and install light fitting and as built drawing
6 - Install lamp & diffuser and clean fitting
7 - Mark up lighting drawing, data loop included, numbering all exit and emergency lights (if applicable)
8 - Complete log book and record results if applicable
|  |  | Switchboards | ITP013 Install Distribution Boards -Terminate Cables
1 - Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
2 - Locate & fix into position
3 - Install submains cabling as appropriate eg. Glands, tray, duct
4 - Install lugs and terminate
5 - Install sub circuit cabling and terminate. If circuit not complete at the other end, it must not be terminated.
6 - Clean & vacuum
7 - Record results
8 - Organise inspection by inspector. Lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
9 - Clearly identify services
10 - Energize
11 - Check phase rotation
12 - Check switchboard as installed matches shop drawing. If necessary modify shop drawing to match installed & return to office
13 - Check typed schedule for accuracy and install in schedule holder
14 - Clean switchboard cupboard
ITP014 Distribution Board Test Results
Distribution Board Test Results - Complete and Test Sheet attached
ITP015 Submains Test Results
Submains Test Results - Complete and Test Sheet attached
|  |  | Temps | ITP017 Temp DBs
1 - RCD
2 - Date of testing
3 - Next test due
4 - Results and/or trip current (less 30ma) for earth leakage device
5 - Has a new tag been installed on the db - please take a photo
6 - Has the front cover been updated
7 - Please take a photo of DB - pass once attached
8 - Compliance certificate completed and attached
9 - License no.
ITP018 Temp Lighting
1 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
2 - Install cable support system
3 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
4 - Fix cables to support system
5 - Temporary construction tape has been installed along cabling
6 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
7 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
8 - Location/compliance
9 - Fit off light fittings
10 - Functional test carried out on each fitting

## Master
New Checklists 3.3.23
ITP001 Underground Conduits
ITP002 In-Deck/Slab Conduits
ITP003 Main Switchboard & Termination of Cables
ITP004 Conduit & Cable Tray
ITP005 Mains, Submains Cable in Conduits or on Trays
ITP006 Power Wiring Rough In
ITP007 Lighting Wiring Rough In
ITP008 Data Wiring Rough In
ITP009 Power Installation and Fit Off
ITP010 Lighting Installation and Fit Off
ITP011 Data Installation and Fit Off
ITP0012 Exit & Emergency Light Installation
ITP013 Install Distribution Boards -Terminate Cables
ITP014 Distribution Board Test Results
ITP015 Submains Test Results
ITP016 Earth Grids / Lighting Protection
ITP017 Temp DBs
ITP018 Temp Lighting
OLD CHECKLISTS: - Account Library 1.3.23
Data cabling and outlets
Power cabling and outlets
Emergency Lighting Testing Evidence
Cable Support System
Install Distribution Boards - Terminate Cables
Lighting cabling and outlets
Toolbox Safety Talks Meeting Minutes
Temp Board Install Checklist
Electrical Installation Testing
Test and Tag Register
Temporary DB Monthly Testing
Switchboard and Sub Main Terminations

## New Checklists - 3.3.23
type | name | values
checklist | ITP001 Underground Conduits
section | Preparation
checkpoint | 1 - Determine origin & destination
checkpoint | 2 - Confirm area of work is accessible & acceptable to commence
text | 3 - Drawing & revision number
checkpoint | 4 - Check clear of other services N.B. the clearance for gas pipes is 300mm & other services 100mm
checkpoint | 5 - Check cable size to verify conduit size & determining size of trench
checkpoint | 6 - Organise barricades, webbing, plates, warning lights if applicable prior to excavation
checkpoint | 7 - Determine spoil removal, back fill material, compaction, cable marking & protection & re-instatement requirements
section | Installation
checkpoint | 8 - Mark out trench route arrange saw cutting if required
checkpoint | 9 - Excavate trench & install barricades as required check depth, taking into account final ground levels
checkpoint | 10 - Determine which way cable will be installed and lay couplings in no friction direction, install conduit, glue
checkpoint | 11 - Install draw wire if required
checkpoint | 12 - Inspect trench by supply authority if applicable
checkpoint | 13 - Inspect & back fill trench
checkpoint | 14 - Re-instate & clean area
checkpoint | 15 - Install direction marker if applicable
checkpoint | 16 - Do sketch or mark up drg for future as builts
checklist-flat | ITP002 In-Deck/Slab Conduits
checkpoint | 1 - Confirm that the selected conduit is of adequate size for purpose
checkpoint | 2 - It has been confirmed that all outlets/fittings in slab have been captured
checkpoint | 3 - Conduit has been securely fixed
checkpoint | 4 - Conduit has been securely fixed to the box or volcano
checkpoint | 5 - Conduit box has temporarily been secured and tied down in place for pour
checkpoint | 6 - Alternative route has been supplied in case main route is damaged
checkpoint | 7 - Conduit runs have all been marked on as builts
checklist-flat | ITP003 Main Switchboard & Termination of Cables
checkpoint | 1 - Locate and fix switchboard into position
checkpoint | 2 - Determine cable sizes for cable glands, mark out gland plate (if not previously determined at planning meeting)
checkpoint | 3 - Install cable glands and cables
checkpoint | 4 - Install lugs & terminate
checkpoint | 5 - Clean and vacuum out board
checkpoint | 6 - Check all circuits are terminated & safe at the other end or disconnect.
checkpoint | 7 - Visual inspection
text | 8 - Test earth continuity and resistance
text | 9 - Test insulation resistance
text | 10 - Test polarity
text | 11 - Test phase rotation
checkpoint | 12 - Lodge prescribed certificate of electrical safety. Organise inspection by inspector.
checkpoint | 13 - Isolate / lock off / danger tag all outgoing circuits.
checkpoint | 14 - Ensure all labelling is complete and accurate.
checkpoint | 15 - Energize
checkpoint | 16 - Check phase rotation
checkpoint | 17 - Check switchboard as installed matches shop drawing
checkpoint | 18 - Modify shop drawing to match existing & return to office
checkpoint | 19 - Clean switchroom
checkpoint | 20 - Check if requirement for spare fuse
checkpoint | 21 - Check requirements for laminated drawing to be installed
checklist | ITP004 Conduit & Cable Tray
section | Conduit Installation
checkpoint | 1 - Coordinate with other services ensure segregation from comms / data services
checkpoint | 2 - Size and type of conduit
checkpoint | 3 - Install conduit
checkpoint | 4 - Fixings
section | Cable Tray Installation
checkpoint | 5 - Coordinate with other services
checkpoint | 6 - Size of cable tray each cable support has sufficient room for future expansion
checkpoint | 7 - Cable support system has been selected to correctly hold the required weight
checkpoint | 8 - Install fixings
checkpoint | 9 - Install cable tray cable support system has been correctly installed and is secure in place
checkpoint | 10 - Height of cable support system has been confirmed and installed to that height in all areas
checkpoint | 11 - Cable support system is as per shop drawings and not impacting any other services
checkpoint | 12 - All threaded rods have been cut off to correct size
checkpoint | 13 - All nuts/bolts/channel nuts have been tightened
checkpoint | 14 - Do sketch or mark up drawing for future as builts
checklist-flat | ITP005 Mains, Submains Cable in Conduits or on Trays
checkpoint | 1 - Measure cable runs with appropriate accurate measuring instrument eg tape measure, wheel
checkpoint | 2 - Check cable sizes. Resistance of protective earth conductor shall be low enough to permit passage of current necessary to operate protective device.
checkpoint | 3 - Confirm length of cable
checkpoint | 4 - Install cable in applicable method eg. Cable stands, electric winch, pulleys etc. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint | 5 - Tri-foil (refer to details on back for all options) cables and tie cables to support system
checkpoint | 6 - Check requirements for cable identification and install
checklist-flat | ITP006 Power Wiring Rough In
checkpoint | 1 - Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint | 2 - Determine cable size
checkpoint | 3 - Cable sizes max length
checkpoint | 4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint | 5 - Install cable support system
checkpoint | 6 - Check cable size/type, black sheath for power, white sheath for light: 4mm to be used for runs over 90 metres (unless specified differently)
checkpoint | 7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint | 8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | 9 - Fix cables to support system
checkpoint | 10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | 11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint | 12 - All outlets have been wired as per drawings
checkpoint | 13 - All outlets have been marked on the site as built drawing
checkpoint | 14 - Height and location have been confirmed for each outlet
checklist-flat | ITP007 Lighting Wiring Rough In
checkpoint | 1 - Refer to drawing to determine cable support route and check separation from data/comms services
checkpoint | 2 - Determine cable size
checkpoint | 3 - Cable sizes max length
checkpoint | 4 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint | 5 - Install cable support system
checkpoint | 6 - Check cable size/type/colour
checkpoint | 7 - Install and identify cables. Any cable not terminated immediately must have the ends taped covering the bare copper.
checkpoint | 8 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | 9 - Fix cables to support system
checkpoint | 10 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | 11 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint | 12 - All lighting points and switches have been wired as per drawings
checkpoint | 13 - All lighting points and switches have been marked on the site as built drawing
checkpoint | 14 - Height and location have been confirmed for each lighting points and switches
checklist-flat | ITP008 Data Wiring Rough In
checkpoint | 1 - Refer to drawing to determine cable support route and check separation from power services
checkpoint | 2 - Determine cable type
checkpoint | 3 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint | 4 - Install cable support system
checkpoint | 5 - Install and identify cables.
checkpoint | 6 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | 7 - Fix cables to support system
checkpoint | 8 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | 9 - All outlets have been wired as per drawings
checkpoint | 10 - All outlets have been marked on the site as built drawing
checkpoint | 11 - Height and location have been confirmed for each outlet
checklist-flat | ITP009 Power Installation and Fit Off
checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint | 2 - Each circuit is terminated at the db and protected by the correct protective device
checkpoint | 3 - Location/compliance wet areas, hazards etc. Mounting heights,
checkpoint | 4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
checkpoint | 5 - Fit off and fix gpo’s, where a gpo is located within 150mm of a metal stud, use shroud. Each circuit must be fitted off completely.
checkpoint | 6 - Fit off final appliances
checkpoint | 7 - Functional test carried out on each outlet
checkpoint | 8 - Cover plates (if required)
checkpoint | 9 - Install label (if a specified requirement)
checkpoint | 10 - All outlets & appliances marked on the site as build’s
checklist-flat | ITP010 Lighting Installation and Fit Off
checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint | 2 - Each circuit is terminated at the db and protected by the correct protective device
checkpoint | 3 - Location/compliance wet areas, hazards etc. Mounting heights,
checkpoint | 4 - Fit off and fix switches, where multi gang switches with multi circuits are involved use shrouds on each switch. Each circuit must be fitted off completely.
checkpoint | 5 - Fit off final light fittings
checkpoint | 6 - Functional test carried out on each outlet
checkpoint | 7 - Cover plates (if required)
checkpoint | 8 - Install label (if a specified requirement)
checkpoint | 9 - All lights and switches marked on the site as build’s
checklist-flat | ITP011 Data Installation and Fit Off
checkpoint | 1 - Check drawings for quantity, brand, type and colour
checkpoint | 2 - Fit off and fix outlets, terminations have been checked and all terminations are correct and secure in all outlets
checkpoint | 3 - Outlets have all been secured in place and levelled
checkpoint | 4 - All cabling has been tested using the fluke data tester
checkpoint | 5 - Each cable has been correctly installed and terminated in the patch panel
checkpoint | 6 - Cover plates (if required)
checkpoint | 7 - Install label (if a specified requirement)
checkpoint | 8 - All outlets & appliances marked on the site as build’s
checklist-flat | ITP0012 Exit & Emergency Light Installation
checkpoint | 1 - Delivery check for damage and correct quantities
checkpoint | 2 - Locations coordinate with other services
checkpoint | 3 - Marking out (if required) - refer to reflected ceiling plan for locations
checkpoint | 4 - Plug in or fit off light fit-off data cable if applicable
checkpoint | 5 - Number and install light fitting and as built drawing
checkpoint | 6 - Install lamp & diffuser and clean fitting
checkpoint | 7 - Mark up lighting drawing, data loop included, numbering all exit and emergency lights (if applicable)
checkpoint | 8 - Complete log book and record results if applicable
checklist-flat | ITP013 Install Distribution Boards -Terminate Cables
checkpoint | 1 - Delivery check for damage, paint finish, dimensions and doors against approved shop drawing
checkpoint | 2 - Locate & fix into position
checkpoint | 3 - Install submains cabling as appropriate eg. Glands, tray, duct
checkpoint | 4 - Install lugs and terminate
checkpoint | 5 - Install sub circuit cabling and terminate. If circuit not complete at the other end, it must not be terminated.
checkpoint | 6 - Clean & vacuum
checkpoint | 7 - Record results
checkpoint | 8 - Organise inspection by inspector. Lodge prescribed / non prescribed (as applicable) certificate of electrical safety (if required).
checkpoint | 9 - Clearly identify services
checkpoint | 10 - Energize
checkpoint | 11 - Check phase rotation
checkpoint | 12 - Check switchboard as installed matches shop drawing. If necessary modify shop drawing to match installed & return to office
checkpoint | 13 - Check typed schedule for accuracy and install in schedule holder
checkpoint | 14 - Clean switchboard cupboard
checklist-flat | ITP014 Distribution Board Test Results
checkpoint | Distribution Board Test Results - Complete and Test Sheet attached
checklist-flat | ITP015 Submains Test Results
checkpoint | Submains Test Results - Complete and Test Sheet attached
checklist-flat | ITP016 Earth Grids / Lighting Protection
checkpoint | 1 - Refer to drawings to determine size of grid.
checkpoint | 2 - Check size of cable and earth electrode.
checkpoint | 3 - Check specification for resistance level.
checkpoint | 4 - Drive earth electrode into ground.
checkpoint | 5 - Earth test electrode or grid.
text | Earth tester number
checkpoint | 6 - If insufficient reading, add other electrodes 2 metres apart and link up with initial electrode with earth cable.
checkpoint | 7 - Terminate cable from first electrode to frame or earth bar and label.
checkpoint | 8 - Test sheet completed and attached
checklist-flat | ITP017 Temp DBs
checkpoint | 1 - RCD
checkpoint | 2 - Date of testing
checkpoint | 3 - Next test due
checkpoint | 4 - Results and/or trip current (less 30ma) for earth leakage device
checkpoint | 5 - Has a new tag been installed on the db - please take a photo
checkpoint | 6 - Has the front cover been updated
checkpoint | 7 - Please take a photo of DB - pass once attached
checkpoint | 8 - Compliance certificate completed and attached
checkpoint | 9 - License no.
checklist-flat | ITP018 Temp Lighting
checkpoint | 1 - Determine cable support system ie. Catinary, cable tray, fix to structure, ducting
checkpoint | 2 - Install cable support system
checkpoint | 3 - Mechanical protection has been provided to minimise the likelihood of physical damage to cabling
checkpoint | 4 - Fix cables to support system
checkpoint | 5 - Temporary construction tape has been installed along cabling
checkpoint | 6 - Cabling has been concealed where possible in ceiling spaces, wall cavities or risers
checkpoint | 7 - Fit-off outlets, plug bases etc. (if necessary), each circuit to be fitted off completely & clean up area
checkpoint | 8 - Location/compliance
checkpoint | 9 - Fit off light fittings
checkpoint | 10 - Functional test carried out on each fitting
Checklist | Main Switchboard & Termination of Cables ITP019
section | Preparation
checkpoint | Locate & fix switchboard into position - check for clearances fix correctly
checkpoint | Determine cable sizes for cable glands & mark out gland plate (check cable O.D's for cable size glands)
button | Install cable glands & cables | Yes, No, N/A
button | Install lugs & terminate | Yes, No, N/A
checkpoint | Clean & vacuum out board - please take a photo
checkpoint | Check all circuits are terminated & safe at the other end or disconnect
checkpoint | Final visual inspection of board - please take a photo
section | Installation
checkpoint | Test earth continuity & resistance
button | Test insulation resistance | Yes, No, N/A
button | Test polarity | Yes, No, N/A
button | Test phase rotation | Yes, No, N/A
checkpoint | Attach prescribed certificate of electrical safety. Organise inspection by inspector (Add photo or attached certification
checkpoint | Isolate / lock off/ dange tag all outgoing circuits - please take a photo
button | Ensure labelling is complete & accurate | Yes, No, N/A
checkpoint | Energise system
button | Check phase rotation | Yes, No, N/A
button | Check switchboard as installed as per drawings | Yes, No, N/A
text | Drawing & revision number(s)
checkpoint | Ensure any modifications to shop drawings are matched to existing & returned to office / attach drawings
checkpoint | Ensure switch room is left clean - please take a photo
checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)