## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
c144afde-555c-5528-9daf-3e37c758849c | checklist | FH-ZU2-QU-ITP001 - Demolition of Existing Pavements - Rev 0 | itp | ITP001 - Demolition of Existing Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
de6ba418-2f03-5955-aff5-5e2c470d39b5 | note | Frequency - Prior to works
bb451165-5268-54e3-b4b3-8cbe6e9d37fa | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
6ed2bb77-45d4-5333-a0a1-cce4e1527cc8 | note | ○ Using the correct and complete set of drawings.
cff6e110-a38b-51b6-a6e5-0e28d19fe499 | note | ○ All drawings are the latest revision
33fc753a-477a-5f83-a6b1-be5cbddefd25 | note | Reference Documents - Aconex
869252e6-5f03-5a03-a27c-06d6aa13de5b | note | Inspection/Test Method - Visual inspection
e10801c6-67d0-59d2-a960-52a5b2a6237d | note | Record of conformity - This ITP signed
98e00363-1acd-579f-aa9e-b465cfc1d60d | note | IP
2e60b1e9-7e3d-5aca-850f-c29ad54093ee | note | Responsibility - Project/Site Engineer
a181c36b-ae14-5c86-a20a-ba915d3c521c | date | Date Completed:
652fe225-451a-5ff1-9c3e-5cb20fa77399 | checkpoint | 1.2 - Demolition Work Plan
bb0d47e1-b70f-5be4-86bc-6d0d37693a4d | note | Frequency - 2-weeks prior to start of works
e1c9a3bf-226c-5123-9338-2edf778f750e | note | Acceptance Criteria - Prepared and submit Demolition Work Plan in accordance with AS 2601 to Contract Administrator two weeks prior to start of works.
c758a3bb-d8ed-5e95-a947-289dfedf1fac | note | Reference Documents - Spec cl. 8.4 AS2601 WMS-001
4ca45db9-8b0c-593f-854a-70f9c91cca6c | note | Inspection/Test Method - Verify
c8cd80e1-5dc0-5e39-a4bd-8395ab627af1 | note | Record of conformity - This ITP signed
e2077523-4d37-50e2-a1f7-236a89c4a6fb | note | HP
7d84c665-a967-530f-8433-c484bfb0d278 | note | Responsibility - Project/Site Engineer, Principal’s Representative
5db4d83c-29fd-5cdf-960c-ed9c12482e50 | date | Date Completed:
43ecc5c0-58a0-53a5-aafc-38fb21ddebd8 | signoff | AUTHORITY HOLDPOINT
af19260b-7d35-5f5b-8ddb-fb72e51d7659 | checkpoint | 1.3 - Dilapidation Report
7bd5b0c6-ba17-5187-adc3-e6a326a32eb2 | note | Frequency - Prior to works
35695348-166d-5426-94a1-37f22be6a12e | note | Acceptance Criteria - A dilapidation report is to be completed and submitted prior to works on site. Dilapidation report to include photos and recordings of the condition of the pavement prior to demolition works.
218d6988-09da-5982-a2e4-909d172da817 | note | Reference Documents - Dilapidation Report
0b41a501-7016-5af3-988e-a6311d817726 | note | Inspection/Test Method - Visual inspection & Verify
405be92c-0e43-50e6-8944-d5e211f5759f | note | Record of conformity - Aconex & This ITP signed
74a7bfa7-7423-5826-abb8-adebfeae7f9a | note | HP*
023533ff-1616-5d33-a2b8-30bef7b7486b | note | Responsibility - Project/Site Engineer
c2e3814f-1ccd-534b-a013-4d4f743f21dd | date | Date Completed:
56a333f6-6275-5ad8-a545-852b0bef9497 | checkpoint | 1.4 - Existing Service Identification & Protection
45f1702d-5b43-575b-9667-75048355810b | note | Frequency - Prior to works
4522f48d-9bdf-5866-8d04-f661277673a2 | note | Acceptance Criteria - Existing services information gathered from APAM prior to works. Area to be demolished has current BYD plans, service scanned, and existing services has been proved. Services have been identified and protected prior to demolition.
58dd54e3-03e1-5fb7-849e-d8f22fa07fbe | note | Reference Documents - Spec cl. 8.5.1 Drawings, BYDA, Survey Maps
97297616-c88e-5eb6-99ed-b539126ae022 | note | Inspection/Test Method - Verify
e5c985f5-f458-58aa-a10f-f5e7346a67d4 | note | Record of conformity - This ITP signed
f276c259-8c21-5cca-a78f-49100e7c9402 | note | IP
5907faef-fe05-5530-81d6-24ed30a1b715 | note | Responsibility - Surveyor, Project/Site Engineer
4f9c2daa-fa7b-5ede-9e45-eefa43fd675d | date | Date Completed:
3d5540f9-8951-5202-993d-61e164319ff8 | checkpoint | 1.5 - Execution of Demolition works
b9f49108-0177-5ea0-a0db-0e2301b5389a | note | Frequency - 2-weeks prior to start of works
e6729bde-b9d0-5217-9282-8cc785387ff1 | note | Acceptance Criteria - If working within the existing vicinity of AGL services, Fulton Hogan to give APAM a two-week written notice to work in the vicinity of existing AGL cables and transformers, to provide notice for APAM to assist in isolating services.
8c4ca2a2-bc2a-51a5-89eb-197856cb2a8e | note | Reference Documents - Spec cl. 8.5.1
2705b2d5-423f-5299-9b17-ff18479d6236 | note | Inspection/Test Method - Verify
f6a5a2d9-aa00-55c5-af5b-02517ffb42e5 | note | Record of conformity - This ITP signed
9b05a6b9-21b7-5a6d-94f2-aac152dfdcfe | note | IP
6769e4c8-2210-5634-bd56-691fabf8e714 | note | Responsibility - Project/Site Engineer
2ec735ad-f8dd-51ad-a7d0-bdab91a4efac | date | Date Completed:
d5e7c061-a358-5f3c-acdf-8cdcdba2ba43 | checkpoint | 1.6 - Implementation of all measures and controls
0288d473-5da7-580d-bb77-dd34ac13a7f6 | note | Frequency - Prior to works
5b133118-4d35-573b-806b-23778d780fd9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, ECP, TMP, SWMS and WP. Existing areas that are not part of the demolition will be delineated with bollards or similar to ensure that it is not disturbed during demolition.
34224c36-7f04-5aef-8886-f22b446426a1 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
f22f7a72-5027-5553-b48d-c50f459710fb | note | Inspection/Test Method - Visual Inspection
00819a04-f5a1-5f8f-a38e-4a4f6fa7092b | note | Record of conformity - This ITP signed
a3cd1da0-3c74-5829-81b8-79d9cb39a0f3 | note | IP
b88747a5-0950-5069-8d91-33c9885de087 | note | Responsibility - Project/Site Engineer
05a68ad6-76b3-58df-93c1-dd9252a94a11 | date | Date Completed:
b92327ca-5de2-55c0-95cf-bd10482bf603 | checkpoint | 1.7 - Testing of Demolition Materials
d7fd890f-720a-5d4d-9d5e-fff65772b3c3 | note | Frequency - Prior to works
eb55cd7b-dcfa-5434-8639-c55e87603b0a | note | Acceptance Criteria - Ensure PFAS testing has been completed. The results of the testing will be used to determine the appropriate disposal or re-use of the demolished materials. Offsite disposal of material has been approved by APAM and comply with regulatory requirements.
e07c9c66-19b8-53e8-ae70-ef8968bfec0a | note | Reference Documents - Spec cl. 8.5.5
50f7461a-2b7e-5d7d-9c84-ffedd2400d90 | note | Inspection/Test Method - Verify
8bdecf34-d91f-5805-b803-d4e50f3f66b2 | note | Record of conformity - This ITP signed
de5775e5-cd56-550e-8333-79a2f2215f3f | note | HP*
c9bfbcd4-75a8-59e6-8fe8-974782b93305 | note | Responsibility - Project/Site Engineer
9f4b5e74-2c21-5070-a5c6-40e28d21b6bd | date | Date Completed:
661b1258-317b-55df-91af-3bd2da089919 | checkpoint | 1.8 - Excavation Permits
be982e0d-451d-5990-b371-14bd6a185547 | note | Frequency - Prior to works
31b23bba-6ec6-56fd-a149-0b62d29a0b33 | note | Acceptance Criteria - Prior to works, check that excavation permit has been gathered from APAM prior to any demolition works. Internal Fulton Hogan permit has been issues to excavation works and plant operators.
b7c27170-a1ca-5d0d-b0b8-cb64a43d841e | note | Reference Documents - APAM Excavation permit, FH Permit, Go- Cards
10f5a5af-1690-5b5a-9bda-dee7d4bdb2d8 | note | Inspection/Test Method - Verify
1b9c1d85-945d-5cd5-87df-b56aa0eeb97e | note | Record of conformity - Excavation Permit
2e86c833-d897-5663-8392-742befa2a4f6 | note | HP*
08f2e4dd-49c9-5a1d-b705-b46fe3ed0ad2 | note | Responsibility - Project/Site Engineer
f80a5894-3af3-507f-a3c4-605e3111fde8 | date | Date Completed:
a5e70c95-ebf5-5449-920c-b3ca49bac0f8 | section | 2.0 - Demolition of Existing Pavement Works
53302c01-4ad4-5657-937a-dc89dcc79ddc | checkpoint | 2.1 - Definition of a works area (survey)
aae52969-45d2-503e-adc2-d30ba1dd9d2d | note | Frequency - Each Lot
b4adfc7f-599d-5b8d-8cd3-e661d18ab14f | note | Acceptance Criteria - Work area has been cleaned and surveyed (marked on site). Limits of demolition are clearly marked.
ef12fdfe-1564-5ea2-b5f6-2d7d56fe5e0c | note | Reference Documents - Drawings
e867c56c-9d76-5a56-bb23-b85897312423 | note | Inspection/Test Method - Verify
17d31cd7-172a-5a27-b550-5cef99ad77ce | note | Record of conformity - This ITP signed
4d590bf8-5081-5894-a2b4-5b161ed967fb | note | IP
53d97e94-87e1-5ed2-b6ab-66f519b380ae | note | Responsibility - Project/Site Engineer, Surveyor
9dfd43f7-e8ef-503e-bd0b-4685d0cc6190 | date | Date Completed:
51012452-a66f-5350-9652-8079c72d73f7 | checkpoint | 2.2 - Temporary Supports
284bf415-c66d-52fc-87f8-f1d3317cd3e5 | note | Frequency - Each Lot
c5a0bfd9-acef-5e79-9960-d1bba05f5585 | note | Acceptance Criteria - Check demolition will not affect any structural or service supports, if so, temporary supports will be provided until it is no longer required.
25fd1501-6624-532a-8618-4460e259eb3a | note | Reference Documents - Spec cl. 8.5.3
4527299f-b244-5799-ba2a-31ec22a6e6f8 | note | Inspection/Test Method - Verify
bff6d09d-e026-51bf-8796-48ecd81b755d | note | Record of conformity - This ITP signed
26408a23-98a8-529a-8c69-e60a9c256fc1 | note | IP
9cb94ee1-978c-577c-a441-c9a96ac698b7 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
c6fd8ad7-c9a7-519e-bb7f-7215c1ca0594 | date | Date Completed:
cb2d8e84-991f-5559-a72a-59370f524404 | checkpoint | 2.3 - Disposal of Material
edeeb9de-8f1d-5408-948d-f170556aefb9 | note | Frequency - Each Lot
62348367-a089-5ff2-965a-d5b97f1490d5 | note | Acceptance Criteria - Demolished clean concrete material will be taken to Vic Civils at Gate 8, for concrete recycling. Contaminated or PFAS material are to be taken to Gate 11 to be stockpiled into their dedicated category and contaminant. Any discovered contaminated material found on site, that are not already known, will be notified to the client immediately.
d51bfb7b-fb2b-5e85-bb31-102f96a844ab | note | Reference Documents - Spec cl. 8.5.5
628bdfa2-776a-56b3-ad7f-2c6f15db31a7 | note | Inspection/Test Method - Verify
34eb3d96-c6e2-5c48-a27e-e66ecd8623f7 | note | Record of conformity - This ITP signed
eab19740-24a5-5057-b0a7-4656c968481d | note | IP
6ef59242-739d-584c-9780-6332e3011149 | note | Responsibility - Project/Site Engineer, Foreman
4d348c96-f5be-5a9b-a86f-4c97db7f50b6 | date | Date Completed:
7c53d2ae-eb69-5762-99e4-f9eb16eb80bc | checkpoint | 2.4 - Asbestos Materials
4973ee8e-e824-5621-8769-1660434f041c | note | Frequency - Each Lot
50401d4f-5850-55fc-867d-33e4e17c44a6 | note | Acceptance Criteria - If asbestos material is identified, works are to be stopped until test is conducted to verify the asbestos. If asbestos is confirmed, licensed subcontractors are to remove and dispose the asbestos out of site.
c8338bbf-c5cd-5c6d-8560-17ec9a11dcf2 | note | Reference Documents - Spec cl. 8.5.6
63eac01c-1285-511f-9009-807a05066da4 | note | Inspection/Test Method - Verify
deb03700-7275-57e9-8b52-ec1baaf14c47 | note | Record of conformity - This ITP signed
1919a9ee-a3fc-5a1d-a43f-206f21f2ed84 | note | HP*
2660f46f-ffde-5d8d-ba2b-1fe0c70f3c7f | note | Responsibility - Project/Site Engineer, Foreman
f9a21230-85e8-5c8a-8766-654ec65b288f | date | Date Completed:
8656f687-014e-5488-a5ea-5ac5f08f4f8a | checkpoint | 2.5 - Made Good
2e649beb-1249-56e7-bdf6-b2a3358aed94 | note | Frequency - Each Lot
72cb9da6-7592-566c-a0c5-7bad14187df7 | note | Acceptance Criteria - Removed and demolished pits and/or cavities are backfilled and compacted. Backfilled areas match adjacent existing surfaces.
a122d8df-a5a6-5039-abe3-45ddf042b566 | note | Reference Documents - Spec Cl. 8.5.7
032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f | note | Inspection/Test Method - Verify
de1d9087-ec08-57fa-9c3b-a8e2f082dd8a | note | Record of conformity - This ITP signed
753bd93d-d588-5243-bb18-80ffc50e8cb1 | note | HP*
95172b46-6943-5d2b-b5b9-60aef6f9cecb | note | Responsibility - Project/Site Engineer, Foreman
0d69e2a8-438f-5fbd-be52-ebd47e1cc6e7 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2e649beb-1249-56e7-bdf6-b2a3358aed94 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
72cb9da6-7592-566c-a0c5-7bad14187df7 | textbox | Print Name:
a122d8df-a5a6-5039-abe3-45ddf042b566 | textbox | Position:
032378c0-9e5f-5fe6-9c7c-a7a25c0cc35f | date | Work Completed On:
de1d9087-ec08-57fa-9c3b-a8e2f082dd8a | date | Date:
c16a7dd0-c687-5cd6-887d-70efd49b6468 | checklist | FH-ZU2-QU-ITP002 - Site Establishment - Rev 0 | itp | ITP002 - Site Establishment
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3cfc1515-1fe7-5182-8110-095e2a556c32 | note | Frequency - Prior to works
5f979054-727e-54aa-8645-fb79302086c9 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
7a7b835a-87b9-5819-b24a-054c8dcd3994 | note | – Using the correct and complete set of drawings.
f8079544-3881-5620-98b8-59beb27370c3 | note | – All drawings are the latest revision
a8475448-f144-5495-b5fc-6993900571fa | note | Reference Documents - Work Pack
bf8a3dd4-0e62-571f-98da-683c260cb359 | note | Inspection/Test Method - Verify
958ce004-234e-5e71-88fd-6fa4b18a21bd | note | Record of conformity - This ITP signed
90469bb2-d27a-536c-acea-5544ec8976bb | note | IP
8ce14f19-a51e-55f3-81ea-0f8a06940dd7 | note | Responsibility - Project/Site Engineer
0f7b1605-06d9-53a7-9a06-c33e112dd6ee | date | Date Completed:
4bd1d280-8d7f-5dfb-abc2-9c57770ba8c2 | checkpoint | 1.2 - Dilapidation Report
c2bcdd88-d14e-5d6b-a936-b84cdcbd0466 | note | Frequency - Prior to works
c26ff740-c231-52ba-b06c-8c6efda807a6 | note | Acceptance Criteria - A dilapidation report is to be completed and submitted prior to works on site. Dilapidation report to include photos and recordings of the condition of the site compounds areas prior to start.
e5b19e94-a206-5ae9-b7b5-3bebbc124d70 | note | Reference Documents - Dilapidation Report
abf9fb6f-e6bd-5b84-9c6c-bbb1fc04293c | note | Inspection/Test Method - Verify
61cbd3d1-e908-5933-b041-d38e71e0f6e0 | note | Record of conformity - Aconex & This ITP signed
ec2200f5-4a02-51e7-88e8-2ba60278d73c | note | HP*
87eb43cf-d3bc-5448-a56b-f2b3d9588de5 | note | Responsibility - Project/Site Engineer
8170464f-1e89-5ae7-a7f9-ea5bf1cb95d9 | date | Date Completed:
1345e494-308d-59f2-9734-1b56d70c486c | checkpoint | 1.3 - Existing Service Identification & Protection
c91f897a-bbb9-557f-b0d6-b68cad614832 | note | Frequency - Prior to works
a5f8e5b3-8e44-5306-a72b-ed5465d53ee9 | note | Acceptance Criteria - Hardstand area has current BYD plans, service scanned, and existing services has been proved. Services have been identified and protected prior to demolition.
dabcbcc8-a24c-5a75-8c79-37a520ffe796 | note | Reference Documents - BYDA, Survey Maps
db005276-8c78-56db-84ad-8194afcea8e2 | note | Inspection/Test Method - Verify
1f97c349-d1c4-5349-ab1c-9fbb364f8e06 | note | Record of conformity - This ITP signed
761d0319-0a04-56dc-82fc-3e7a37a2af9a | note | IP
4d9a8f6a-9164-5dfa-9de7-9b1576639340 | note | Responsibility - Surveyor, Project/Site Engineer
3a1c9c80-0467-5605-9459-fd9cf9a7a741 | date | Date Completed:
2b2d509f-644c-513b-8429-dc08b6bd0803 | checkpoint | 1.4 - Implementation of control measures
2102382c-98b4-55ec-b64f-c362f5d93de1 | note | Frequency - Prior to works
82f3d642-92cf-5365-a9d8-ac7a7ad9079a | note | Acceptance Criteria - All necessary control measures are being implemented, which include PSP, ECP, TMP, SWMS and WP
1106c405-6435-545f-8e0c-fbce99609408 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
c8f203b8-de9d-538c-9fa8-de265c221722 | note | Inspection/Test Method - Verify
2e4e799e-1a58-58cc-8183-e0c31531b986 | note | Record of conformity - This ITP signed
ad65f495-a215-5c46-b32d-c93fd03a6710 | note | IP
9624af7e-36c8-5a93-8425-4efbc949557c | note | Responsibility - Project/Site Engineer
b6171726-97ec-5f08-9180-4fb7cb54bb40 | date | Date Completed:
940df89a-8186-56ea-b5c3-4645a58a692b | checkpoint | 1.5 - Testing
56b0609c-3136-5adb-99e7-6dcebb30eb90 | note | Frequency - Prior to works
0fa57451-1e5c-5b06-ab1c-28c81e6b2bc7 | note | Acceptance Criteria - Ensure PFAS testing has been completed. The results of the testing will be used to determine the appropriate disposal or re-use of the demolished materials.
1ccf6cf2-b3af-5025-8e17-a48c645c1d2a | note | Reference Documents - Aconex
efded1df-a4f6-5702-8cfc-40a516be814f | note | Inspection/Test Method - Verify
875c58e8-5650-55dd-98e5-667a9fad9d8d | note | Record of conformity - This ITP signed and test report
88f43a90-dbaa-55a4-813d-f7e661c27c40 | note | HP*
121c1f21-fd9f-58f7-bf2a-77c8dcf0392c | note | Responsibility - Project/Site Engineer
ede39bc6-21e6-5577-89e6-4f486939a620 | date | Date Completed:
b7e81dec-e470-5248-a10c-e95e95f63636 | checkpoint | 1.6 - Excavation Permits
438f0943-5177-502b-8329-f1c93846ee19 | note | Frequency - Prior to works
626de8fa-07e5-5ee3-8890-a365da489a19 | note | Acceptance Criteria - Prior to works, check that excavation permit has been obtained from APAM prior to any ground penetrating works. Internal Fulton Hogan permit has been issued for excavation works and plant operators have a Go-Card.
a54e3c31-8e56-52bd-bb6a-6e561a515ea8 | note | Reference Documents - APAM Excavation permit, FH Permit, Go-Cards
acb02066-1e9f-5d4e-a02b-3524ecf65518 | note | Inspection/Test Method - Verify
8e9c8bd5-f7ac-5969-a618-e51bcce70ad7 | note | Record of conformity - Excavation Permit
3f36bc56-a1ae-5524-a1b5-203eb3437f1b | note | HP*
2ea25830-60bd-5a21-9281-8bb933f3dddb | note | Responsibility - Project/Site Engineer
53bb5044-b0c6-587d-96c6-ef4f3c40ef13 | date | Date Completed:
e66747cf-dea2-51eb-b3ec-1b89f3bf0b5d | checkpoint | 1.7 - Geotechnical Testing
a4717674-a002-501b-becd-3542952ad92d | note | Frequency - Prior to works
1a27f139-cfa4-5855-b846-c7ceca0c45fc | note | Acceptance Criteria - Ensure testing is carried out to obtain a Hardstand design that meets the requirements and suitable for use.
aa6eaba6-6550-5320-bc28-5704f826047b | note | Reference Documents - APAM Excavation permit, FH Permit, Go-Cards, FH spec
d1e480aa-8ca8-59b1-b0d9-8911b71b7fb2 | note | Inspection/Test Method - Verify
7a3e9e1d-e818-5582-a74a-5742912a6702 | note | Record of conformity - Excavation Permit
55237742-d7d0-5ba3-aae7-197b754af9e0 | note | HP*
f6691999-63d4-5007-a230-0e782e5acee6 | note | Responsibility - Project/Site Engineer
7bea0aba-af66-5129-8dfa-567546d0a78d | date | Date Completed:
68d4b750-18d0-5bb8-97d3-fe4e562f8dc0 | section | 2.0 - Building Hardstands
53302c01-4ad4-5657-937a-dc89dcc79ddc | checkpoint | 2.1 - Definition of a works area (survey)
1495f105-79ac-5ae6-958c-b8af2f0917fd | note | Frequency - Each Hardstand
01e59542-55ff-56a7-aa8c-3bd66f93bf12 | note | Acceptance Criteria - Work area has been cleaned and surveyed (marked on site). Limits of hardstands are clearly marked.
d24c548c-733b-5b2f-abf7-fb8acbda0a0a | note | Reference Documents - Site Markups, Survey layouts
b3aeb841-330e-5fb0-bc8f-0c972c71cd39 | note | Inspection/Test Method - Verify
6a1d4755-e820-59c7-877f-a8267b2a731b | note | Record of conformity - This ITP signed
8b048cc1-d142-5981-852a-346e271051c3 | note | IP
263c11bc-6929-5a56-9e2b-d67036efd2c1 | note | Responsibility - Project/Site Engineer, Surveyor
f2fb3fe2-53a4-5a0c-a34d-21a5c29f3c5d | date | Date Completed:
25acb849-3109-53dc-b0ef-d853cbf5237d | checkpoint | 2.2 - Preparing subgrade
0500d3f1-331d-53cf-92e7-71e3c5882841 | note | Frequency - Each Hardstand
2056ded0-8e4b-5e8a-97af-bb9d5e1849f8 | note | Acceptance Criteria - Ensure topsoil stripped as per hardstand temp design and subgrade compacted to meet design requirements from Geotechnical Engineer.
b9d6dd20-7633-5fc9-934b-2e738cabf5b7 | note | Reference Documents - Geotechnical temp design
cff19e40-fcb9-544a-94e4-101c985beb63 | note | Inspection/Test Method - Verify
4ef23d7c-8ee6-5f4f-93d3-276683bfb7d0 | note | Record of conformity - This ITP signed
7ca16b4b-c013-5661-866b-649b18a4799c | note | IP
adf3bda5-8f3a-5328-aa10-88d2359ad0e5 | note | Responsibility - Project/Site Engineer, Foreman
2ed9a8c6-51e9-55d1-ab26-0b8d28996d2a | date | Date Completed:
cb2d8e84-991f-5559-a72a-59370f524404 | checkpoint | 2.3 - Disposal of Material
5a4695fc-fed9-5d39-993b-510f73c26ba4 | note | Frequency - As Required
3647b628-1080-5ac0-b783-d8115721a752 | note | Acceptance Criteria - Contaminated or PFAS materials are to be taken to Gate 11 to be stockpiled into their dedicated category and contaminant.
663f3cad-596d-5600-ac40-ce55a7eb5859 | note | Reference Documents - Negri PFAS Permit
21926fa3-6a6b-5ba1-b5a7-04ec5295ffab | note | Inspection/Test Method - Verify
1051b69c-784e-5baa-821a-685cf463f56f | note | Record of conformity - This ITP signed and Negri Permit
14b22d9f-12b9-54c5-baf2-d886cd44341f | note | IP
8c75014e-8b2e-599f-8b71-9df089d86128 | note | Responsibility - Project/Site Engineer, Foreman
a38167de-9652-580c-b90b-bc2a92606021 | date | Date Completed:
e7e79b9b-f0bc-58a2-9b2b-3a96a8c6c442 | checkpoint | 2.4 - Building Hardstand
00812335-82b0-5f82-a978-d66410fe7bbb | note | Frequency - Each Hardstand
948565d6-733a-5129-949a-6d6626132e7b | note | Acceptance Criteria - Make sure hardstand is built according to the geotechnical temp design, no soft spots existing after proof rolling.
13626329-6635-5e4f-ab0d-9320cbea65c8 | note | Reference Documents - Geotechnical temp design
3ba010e5-4f98-50ab-9f06-1e842ade4b3a | note | Inspection/Test Method - Verify
e55312eb-1212-5945-b08d-29d1795a93f1 | note | Record of conformity - This ITP signed
fac0995c-3df7-564b-88ba-c6ef256d86c6 | note | HP*
07acc568-4d34-5e61-80ba-8d566d18a14a | note | Responsibility - Project/Site Engineer, Foreman, Geotechnical Engineer
033a81d7-b825-5c67-807e-e2a45faea285 | date | Date Completed:
196b06ac-ca40-5029-82a1-25b9e85b4c1a | checkpoint | 2.5 - Building Crossways
24afd2cf-7314-5d7d-8524-bb6e52f39473 | note | Frequency - As Required
6951fa49-1dc5-561e-a19a-05594f2f1e53 | note | Acceptance Criteria - Construct culvert crossing/driveway access where required as per the temporary design.
7af45202-667f-5d7d-844b-376be1ae9dce | note | Reference Documents - Temporary Design
9993275a-e295-5c89-8fea-488eed4ed7d0 | note | Inspection/Test Method - Verify
555f84ed-9ffb-5bac-94b6-eed048703976 | note | Record of conformity - This ITP signed
09403b2b-f310-53d7-9b6d-107cf6c40f3e | note | HP*
bc825d6d-54af-53f1-896d-cdcd4437350a | note | Responsibility - Project/Site Engineer, Foreman
4fae311f-986e-5084-9887-13b447c20d07 | date | Date Completed:
b7bf38dd-40ca-503b-9c6c-3c2f944e444c | checkpoint | 2.6 - Installing Fencing
2d642617-6f94-57c4-a8cb-79d6413ad8e3 | note | Frequency - As Required
6a4b3d31-c75a-5a35-ab95-c6707a983f3f | note | Acceptance Criteria - Fencing installation is done as per the temp design or Australian standards AS4687
cee0728a-ca97-52b3-9931-596a16407ea8 | note | Reference Documents - Temporary Design
70d40084-dc8c-5ebd-859a-3361fde9f881 | note | Inspection/Test Method - Visual inspection & verify
ad67a3d9-bcff-53d7-b960-693d887c30a7 | note | Record of conformity - This ITP signed
ae9c735d-ac9d-533c-9799-f4cd5f930588 | note | HP*
e81d5045-3b97-50c8-a580-ffe7680ddca9 | note | Responsibility - Project/Site Engineer, Foreman
613c1904-3c34-59be-aff9-6aabec9d5697 | date | Date Completed:
584e46b0-8c84-5cbc-8fcf-927a08f8bafa | section | 3.0 - Mobilization and Set Up
9b8789bb-08fc-5e44-933d-a6c1af9aa666 | checkpoint | 3.1 - Landing and Levelling Sheds
7df20ce7-1bce-5bad-b012-07f31c438756 | note | Frequency - Each Hardstand
16d6c691-10b3-547e-bf53-e42c8b13e516 | note | Acceptance Criteria - Sheds are level and as per the site management plan.
e01217b5-9153-58bc-bbdc-18783838db10 | note | Reference Documents - Manufacturers specification
797168ac-a472-531f-9cd6-fe49616e8dd9 | note | Inspection/Test Method - Visual Inspection
1c18e28a-aeb6-56af-8b04-09385f08da47 | note | Record of conformity - This ITP signed
6b27caa2-19ff-5478-9a42-982c2b053420 | note | HP*
ed054c00-a465-57f1-9e8d-e2841ca4ef42 | note | Responsibility - Project/Site Engineer, Foreman
8bae08db-8d08-599d-add9-df806f7f6e72 | date | Date Completed:
8f737ad7-8dbb-5065-8ec0-f419c46b67a2 | checkpoint | 3.2 - Erecting Hayshed
57049837-e6ce-58e4-848a-828da521ef1f | note | Frequency - Each Hardstand
bd1ac969-30a5-59cf-948e-d25e80e4213c | note | Acceptance Criteria - Hayshed has been constructed as per the verified temporary design provided by OPT
d818c8d1-37c4-5d90-9795-51b1448746f6 | note | Reference Documents - Temporary Design
c2c6e331-eebf-5ab1-b63d-5dae1c5edf6e | note | Inspection/Test Method - Verify
a79d71dd-7cce-52a7-a077-d8d34fef6462 | note | Record of conformity - This ITP signed
07272eac-048d-54b3-a9a7-324c54f19912 | note | HP*
475e6078-bd4f-58d3-9584-8dfbbf0e0133 | note | Responsibility - Project/Site Engineer, Foreman
791c8721-250c-51ba-9c7a-873b0d6eb072 | date | Date Completed:
07aa1c9b-d315-5fdf-9465-365031099f34 | checkpoint | 3.3 - Connecting electrical and plumbing services and appliances
52c6b1ec-caa5-507b-b7ee-81561729edb9 | note | Frequency - Each Hardstand
74ee067a-3644-5bd6-bc78-7023ae184444 | note | Acceptance Criteria - All appliances and connections are functional and tested and tagged
37ddfe63-6932-5aa1-be1b-260df3edf73c | note | Inspection/Test Method - Verify
f9f078d4-88a9-532e-9806-4bd6abf31f24 | note | Record of conformity - This ITP signed
f4e10d7d-947f-5f4c-80e2-bcf1d06ffc36 | note | HP*
d84d564b-45d2-566a-bd7f-4d5be6c4422a | note | Responsibility - Project/Site Engineer, Foreman
2bee9357-f1c3-5394-87f1-7515da434d13 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
26cc0429-e587-5450-b454-1ebe89d0daf6 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
383b649f-0c48-5212-8c94-fd8b492b7fc4 | textbox | Print Name:
0cf105b1-a508-5f4b-aa82-8acee5a17fd9 | textbox | Position:
2e5731f2-7afe-535e-97ba-f3610e5d15c5 | date | Work Completed On:
2c9bcd1c-9204-524f-9d2e-3f7b651761c8 | date | Date:
c7f2a25d-63b1-576a-877c-1278810f36d3 | checklist | FH-ZU2-QU-ITP003 - Stripping Topsoil and Bulk Excavation - Rev 0 | itp | ITP003 - Stripping Top Soil and Bulk Excavation
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b0bf35cf-bf6c-5dcc-bc41-0235c9052364 | note | Frequency - Prior to works
e04509c7-936f-53e0-8fb6-f7bcc1a327ea | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
fdc5d8e3-669e-5553-b761-b07e1a397496 | note | ○ Using the correct and complete set of drawings.
48eb929d-4aad-5b25-ae8d-1d7116fe3a1a | note | ○ All drawings are the latest revision
6ca6d629-4784-5861-a79c-4c0ba3d6f4eb | note | Reference Documents - Aconex
dd16b1cc-ab12-505c-a2b7-7bb53fe3bd1d | note | Inspection/Test Method - Visual inspection
2d9a6b90-f30a-5624-8211-191e8989370d | note | Record of conformity - This ITP signed
cc09c387-0c2f-5dda-adea-a8ef80176672 | note | IP
ea4975d0-50ea-5d69-bb76-c1968543b9ce | note | Responsibility - Project/Site Engineer
cf4ecca4-eaeb-5bec-9d03-95e47a4cca08 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
a1c6b7af-0051-5b47-adee-2ba83b1e11a9 | note | Frequency - Prior to works
0fbcefe2-64ad-51a3-9613-d315fef28308 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
e4c9d16e-a953-5b9b-9a45-8877156edfba | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
7d8cb712-2e8a-5a0d-a8b0-c44a5c45ec04 | note | Inspection/Test Method - Visual inspection
d25d94ff-7601-53b0-919b-c613f70f2323 | note | Record of conformity - This ITP signed
b7a0ec80-5f8e-587f-834b-1d098369588f | note | IP
0a63dfdf-bbf5-580e-a8d0-ae9bf172ca29 | note | Responsibility - Project/Site Engineer
72eda7e5-1afb-5c67-acd8-196c3e10781d | date | Date Completed:
e7a6e343-1080-52f9-bd48-1f0f6f5a115d | checkpoint | 1.3 - Survey
b28ddb15-dca5-55f8-87fa-e72f19e92a7a | note | Frequency - Prior to works
8f6fc471-c5ab-56c6-92c3-cdc17da61ba1 | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
895ea11a-326a-5b69-9652-f24fcd91fd48 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
d8337aa2-37fe-515d-b4f3-1bacfc84dc3c | note | Inspection/Test Method - Visual inspection
7717e169-d754-5552-bb9d-d4f6f8d10b45 | note | Record of conformity - This ITP signed
eb0c37fb-eed5-5944-85a7-b335db33ccc5 | note | IP
fd3a1bf8-2181-59f0-ac7e-d79f06a26e54 | note | Responsibility - Project/Site Engineer Surveyor
bf4564b4-0f61-503c-bcf3-02eccb92fc4f | date | Date Completed:
bd6fccff-030c-5e03-b297-aee09316b255 | checkpoint | 1.4 - APAM permits
f25c9f2a-2ac1-560f-9017-7b5a7084fae8 | note | Frequency - Prior to works
24dd5cb6-1f04-5f82-a4dd-46e652983d3d | note | Acceptance Criteria - Excavation permit issued. If working near HV electrical, an Electricity supply Isolation form and cabling permit has been issued from Melbourne Airport.
9212205d-6ac3-54ab-8fc9-fee1a896df2e | note | Reference Documents - Excavation permit
c8d42d6b-eab7-5cb6-8755-e20453f295ab | note | Inspection/Test Method - Approved permits
cd6b0421-3dd9-5c4c-b73a-de6b1c4ef85c | note | Record of conformity - This ITP signed
8c0fd384-a553-5a21-86d2-9c2ae1ecfe59 | note | HP*
d444af54-ebc2-5cb7-8451-2ffc6d07021f | note | Responsibility - Project/Site Engineer
8be9d07d-a5ae-5841-b757-795c9b56f251 | date | Date Completed:
2e351d7f-b3b9-5262-b49f-9acd784e8df1 | checkpoint | 1.5 - Fulton Hogan Permits
46947f88-5c71-5c7e-b717-22cd2b1a7fc2 | note | Frequency - Prior to works
71e0ef47-8be4-5ac0-962e-604e87161e84 | note | Acceptance Criteria - Fulton Hogan Excavation permit issued to plant operators prior to excavation works. Native Grass heatmap issued and boundary of working area has been set out.
6f1796c9-4d05-53e0-bdde-821c5592e2a9 | note | Reference Documents - Excavation permit
d8325656-3f12-56e1-b210-0d4b6ceac6e5 | note | Inspection/Test Method - Approved permits
4967b778-ff83-52d9-ba59-8cdfef0f275f | note | Record of conformity - This ITP signed
286d6d2b-0311-53eb-ab23-9f4d05737f61 | note | HP*
e52bf27e-db56-57ab-bf83-dafe2c698d6d | note | Responsibility - Project/Site Engineer
eee46c57-60e0-571e-a3f7-97999f76db52 | date | Date Completed:
4bc40f29-44b7-5162-af9f-0698ea5dc38f | checkpoint | 1.8 - Plant and Equipment
725e528d-8b52-5ff5-85fb-0ada1e94e3c8 | note | Frequency - Prior to works
85884f2f-55a6-5be8-9305-0ab219e520c7 | note | Acceptance Criteria - Plant and Equipment used in the works are appropriate to achieve specifications requirements. All plant inducted and inspected as per Fulton Hogan’s plant safety guidelines.
0c019c51-0614-53a0-a154-a2497f8f1c0a | note | Reference Documents - WMS - 003
49aa4a47-fa8b-5fc8-9e34-53bd8059363b | note | Inspection/Test Method - Visual Inspection
6f0ef1fb-f190-53d8-bb13-c894ce09a267 | note | Record of conformity - This ITP signed
1200834b-44a9-5646-b802-8fb932cef07a | note | HP*
acb14978-a615-5ab1-b64f-c6ca52037d13 | note | Responsibility - Project/Site Engineer
d2181fa4-4cd9-5c12-8779-31f6d7c56cc6 | date | Date Completed:
ea5dc8b5-493b-5278-aaf7-f712b642d5b6 | section | 2.0 - Stripping / Bulk Excavation
4e2902bd-6fa2-5de7-a9a2-a7d948c2aa61 | checkpoint | 2.1 - Site Preparation
e27a247b-1e88-5f51-a280-e8299a920aef | note | Frequency - Each lot
0a25fe0f-b005-5d68-9994-e63d04d72117 | note | Acceptance Criteria - All excavation and filling will be free draining to low points clear of the Works. Sufficient pumps, well-points or other equipment for work area de-watered during the works shall be provided where required. Existing drainage lines and water mains found to be traversing the site must be removed as shown on drawings. Contractor must provide temporary pollution control devices or ponds in existing drainage systems and receiving waters.
fb794ab0-50c9-5a06-9d65-96021ddcebff | note | Reference Documents - ZULU- BECA-001- DWG-00001 to ZULU- BECA-005- DWG-01119
57f65844-de94-507d-8927-bfcd2dc9e32f | note | Inspection/Test Method - Visual Inspection
de7135f9-ef45-53c4-a19f-d3aee6734303 | note | Record of conformity - This signed ITP
1e268370-06e4-51b0-93f7-5fe806d0e603 | note | IP
fdf1cd7f-ee62-5ff2-92da-3766f85b1d48 | note | Responsibility - Project/Site Engineer
a585c59e-e787-55aa-92e0-4d29ff87e6d7 | date | Date Completed:
6b0d4de9-7bdf-5139-bfb9-9bbf4e32fa40 | checkpoint | 2.2 - Dust & FOD control
4d67a5f8-2cd4-5cd9-9125-ce8a13c6a8e4 | note | Frequency - Each Lot
9d8de3bf-fc2b-5dc9-a674-f8c8cc422829 | note | Acceptance Criteria - Prevention of dust during earthworks and subgrade preparation. Sweeper onsite at all times to manage dust / FOD.
4ad3cfa1-c539-5aed-8a56-1a9ecdfb9de9 | note | Reference Documents - Site ECP
c801db41-4373-5367-9606-050abb383544 | note | Inspection/Test Method - Visual Inspection
ffd00528-9efe-5abc-885c-e0a0693ef0cd | note | Record of conformity - This signed ITP
191ac37f-fb65-59aa-9cf7-0486937f3484 | note | IP
8e80ef2a-479d-5ee0-bfd4-90df9d4824b1 | note | Responsibility - Project/Site Engineer
58934db1-aab0-59e1-af23-b9571dc42add | date | Date Completed:
a9be7178-4948-5336-bda8-c7104a9e9d10 | checkpoint | 2.3 - Stripping Top Soil
a2cb99da-1e4a-5761-888c-818826c7f6f0 | note | Frequency - Each Lot
795111e8-641b-57d4-817c-253a3653277c | note | Acceptance Criteria - Prior to bulk excavation, site shall be stripped of all topsoil and organic matter as shown on the drawings. Spoil to be taken to Gate 11.
e90c0149-9f06-5f8a-befe-fb458a02b66b | note | Reference Documents - WMS - 003
58244c20-c81e-55b3-810d-ca191ccd8952 | note | Inspection/Test Method - Inspection Point
544ed1e8-6d34-59ab-93b7-0c67e29edcbe | note | Record of conformity - This signed ITP
b8aec92e-8e8a-5dac-95b4-9a205065a43a | note | IP
b77161e9-7ad9-5ed9-bb01-df12fda98a3b | note | Responsibility - Project/Site Engineer
f8d6de4d-e30d-5464-bfc8-fdf096736fcf | date | Date Completed:
9b151195-b645-57b8-8894-c358f2e97edb | checkpoint | 2.4 - Excavation
655ef21e-d583-540b-b0e8-1ae4f87f9ef6 | note | Frequency - Each Lot
fd71f423-e2b8-53ba-bbee-19f9db30e125 | note | Acceptance Criteria - Bulk out subgrade to 100mm of subgrade. If rain is imminent, ensure subgrade is left 100mm high prior to trimming.
c7cc11d3-553d-5d81-b8f0-0f6f1407a670 | note | ○ Rocks Under <800mm can be taken as mixed fill to Gate 11
623c6037-b637-5187-982a-aec791a42130 | note | ○ Rocks >800mm to be sorted and taken to Vic Civil
00c8d2f8-9d2e-5735-9cec-8d01d06b07aa | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
14dccc02-a646-50f9-8f6d-32f24959c516 | note | Inspection/Test Method - Inspection Point
5d396ef6-eb80-5b2a-b64b-d36b8ef0cd6f | note | Record of conformity - This signed ITP
f0aa852a-6306-543b-81bf-7bb4fe5f8563 | note | IP
5d0cec04-02dc-5c0f-8bfd-6084f48216a9 | note | Responsibility - Project/Site Engineer
55143d0a-4292-5671-8588-0096dd2b279b | date | Date Completed:
ee92312b-90a8-534a-a85f-46726ca60607 | checkpoint | 2.5 - Batters & Temporary Support
0078066f-7ff2-5a7e-8bd0-f096e2d634ee | note | Frequency - Each Lot
a9d660c2-8e06-58b0-819c-137e62261509 | note | Acceptance Criteria - All batters to be kept at 1:1. If not, temporary support will need to be designed, engineer and approved for use. Temporary support will remain in place until it is no longer required.
29b426b8-1462-5593-8f23-9614a99f34eb | note | Reference Documents - WMS – 003 Spec 001 - Cl8.5.3
126bb257-8287-5830-aac8-804f9eb9a3ce | note | Inspection/Test Method - Inspection Point
2c813702-c8eb-5da1-a4cc-6123c2135816 | note | Record of conformity - This signed ITP
087bd442-d3ce-5bd3-a28d-e96e359893d3 | note | IP / HP* (if required)
391bd648-17fe-558b-a9e4-f3742978176b | note | Responsibility - Project/Site Engineer
5b4b410e-8682-530d-bb89-ffc8cee3cc2a | date | Date Completed:
1f461390-d201-5a9a-9dc1-82fc60ff9cfd | checkpoint | 2.6 - Excavation – Detailed Trim
409c906c-8df3-5ce5-baed-d2848aa53b27 | note | Frequency - Each Lot
6c4e7036-00b5-55de-ae66-e0e7d66c0a00 | note | Acceptance Criteria - Detail trim Subgrade with excavator / dozer
261f738f-711f-58c1-9b34-cd5f799091d7 | note | Reference Documents - WMS - 003
c48ff060-151e-56f8-8dbd-337de1a3b9d6 | note | Inspection/Test Method - Inspection Point
857f60cb-c4f5-52c7-a914-3d2c5f25ef5e | note | Record of conformity - This signed ITP
d00655ce-58a8-571d-a4f0-17a5c069092c | note | IP
2e518698-e4ba-51be-a036-130fbe55bbbe | note | Responsibility - Project/Site Engineer
b7c1f4d5-948f-56cc-8b7f-1d61781f5e30 | date | Date Completed:
3bf76795-3e73-576b-94f4-19c2ecefa43f | checkpoint | 2.6 - Contaminated Materials (if found)
67d60ac1-c767-5cea-b33a-9c957fe6607c | note | Frequency - Each Lot
7449cf1a-8fdd-5cbe-ae73-f35efccbcd1c | note | Acceptance Criteria - If contaminated or hazardous materials are found, immediate notice is to be given to the Principal’s Representative. These include the following;
18a1b02f-fa5f-5c4b-b29e-8f690d0c20a9 | note | ○ Asbestos or material containing asbestos;
0e601b8e-85e3-5a48-a95a-ce16b3c42b43 | note | ○ Flammable or explosive liquids or gases;
2ffaae20-313d-56b8-af17-0013db1ffe64 | note | ○ Toxic, infective or contaminated materials;
62627aff-bf7a-5503-aaa0-559e22ae8235 | note | ○ Radiation or radioactive materials;
07a861b9-fcc3-52fa-867a-fdd1a56a7642 | note | ○ Noxious or explosive chemicals; and
ea990217-0df6-564d-b132-aaf6c7ce482c | note | ○ Tanks or other containers which have been used for storage of explosive, toxic, infective or contaminated substances.
37992f1d-ea50-5adf-8ffe-baa1ff457dd3 | note | ○ High levels of PFAS
2b53e1b2-cddd-5f0b-ad08-820e0dc38a18 | note | – Agreed removal location to be confirmed with Principles Representative.
9480a3e7-6a36-5ce4-ae96-c773283c46a8 | note | Reference Documents - WMS - 003
c114f601-e3b3-5150-891f-fd79140ee62f | note | Inspection/Test Method - Inspection Point
544d69e3-e333-556a-a981-ea4bfb155186 | note | Record of conformity - This signed ITP
a5480ed3-09c5-55d5-9668-ff3b1e52ce26 | note | HP*
1ec73940-2fe9-55e5-ae19-877a013ce1a4 | note | Responsibility - Project/Site Engineer
cae0531d-97c9-55cc-8a76-caf2995f702c | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
b663b21c-3dfa-536b-b178-91b4f1c37e18 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
ee31d79b-0f59-5a23-82d1-8fe5dd6ec31c | textbox | Print Name:
664f83e7-742d-544a-9d95-9b5f459e4f81 | textbox | Position:
b8ae34f3-9bd9-5e79-9bd4-5cef927f9b58 | date | Work Completed On:
3fe6fc4e-f7a1-5d0e-aa19-8fd21eac62dd | date | Date:
741da932-01e5-5ed2-b7bf-7bd6c0ccbab0 | checklist | FH-ZU2-QU-ITP004 - Select Fill Placement - Rev 0 | itp | ITP004 - Select Fill Placement
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
08c4b17e-a29e-56a5-be50-2ab69afd4d71 | note | Frequency - Prior to works
ec07a3cb-c1f0-5188-bcf9-00a8a0a7c914 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0afb9d20-3984-59f9-afad-cbce551ff055 | note | ○ Using the correct and complete set of drawings.
9934483f-2306-58cc-9494-554d12355379 | note | ○ All drawings are the latest revision
ffc9abf8-4d0f-5d97-bd9f-25c82ca3379e | note | Reference Documents - Aconex
ab0c1193-80ea-588b-943d-7498f0b43bae | note | Inspection/Test Method - Verify
9190310b-61ff-55e1-b585-7c6deddfd16d | note | Record of conformity - This ITP signed
d5d4dd88-73b5-5173-aa38-2d4c061b361e | note | IP
f1a09c02-c144-573f-9bf1-fc6e921e59dc | note | Responsibility - Project/Site Engineer
5582b486-373d-5a50-a97b-1b17f5be5c85 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b26f041a-9e1a-53f5-a2a7-ae357fb1b158 | note | Frequency - Prior to works
5f736424-2c68-5813-9f3e-9938bc60e9e0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS and WP.
f2c2258a-099b-5a2d-bbb8-405e99612b87 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
2a982293-b48a-53b5-9ab5-3e0ad4ffa560 | note | Inspection/Test Method - Visual inspection
4651ff39-7b00-5362-9150-e2db58cfff0d | note | Record of conformity - This ITP signed
2f29ce51-e199-555a-98f0-058275729f9f | note | IP
2f332fd5-58f8-54ee-b8b4-6bcfbdb45e3b | note | Responsibility - Project/Site Engineer
847d413e-f5a2-5801-bdce-d489bf57302a | date | Date Completed:
e7a6e343-1080-52f9-bd48-1f0f6f5a115d | checkpoint | 1.3 - Survey
b94c6f79-9487-5050-adc7-6028f0f7816c | note | Frequency - Prior to works
bb4e26e8-aa42-5610-aa37-25d1a70889db | note | Acceptance Criteria - Area has been surveyed, highlighting any areas where excavations should not occur (e.g. exclusion zone).
d71e8c39-5636-59d4-aeb9-34f2bc826c1b | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
a5158671-8dd3-51d0-8cea-a932a5e0b6ce | note | Inspection/Test Method - Visual inspection
5e36ac1e-3494-5b2b-8bbe-78c39bdf135f | note | Record of conformity - This ITP signed
09f23b99-26a6-52f7-a317-f1e4add963d3 | note | IP
2bb97587-0580-57bc-8c47-320a24478bc9 | note | Responsibility - Project/Site Engineer Surveyor
43a2c40b-d1a0-5c47-a992-6064ca6125ff | date | Date Completed:
42f3e87a-e178-51d2-a080-8cf107eecf0a | checkpoint | 1.4 - Select Fill Material Source (Under Pavements, Imported)
daaba572-1025-5653-afd5-9bf625b59ef9 | note | Frequency - Prior to works
cbb4fed3-7ecd-5ef1-9d34-d585415b842c | note | Acceptance Criteria - Material to meet the following the properties:
be36a13f-2979-5221-b8a4-81124970ae9a | note | – – – – – – – – –
00897eec-50ef-56f5-b303-a4a67d250bfb | note | Wet strength ¦¦ Not less than 125 kN wet/dry strength variation less than 40%
49dcfc3f-2abb-5459-8068-e575a930b0fe | note | – – – – – – – – –
2c356531-e24e-5bfe-a5ed-558c7e48cfbf | note | Linear Shrinkage ¦¦ < 6%
1e1a2f50-b31b-599f-b1b8-b6cedf70dba4 | note | Organic Matter Content ¦¦ < 0.2%
4dec1663-fb29-55bd-95db-83504927c099 | note | Maximum Particle Size ¦¦ 75 mm
28ecf767-cd52-5370-a3ff-72d6443e29f1 | note | % Passing 0.075 mm sieve ¦¦ 0-12%
476e4531-4980-5b57-a950-4372438293d5 | note | Soaked CBR ¦¦ > 20%
b265c9d2-38af-59c4-8e30-d0393ed05e4d | note | CBR swell % ¦¦ ≤ 1.5%
c9074b6f-1d34-594b-b824-102bd68533e0 | note | Permeability ¦¦ < 5 x 10-9 m/s
d8ecc50e-bce7-5f79-8a5c-a4b2dc1bfc3f | note | – – – – – – – – –
d8e6513b-c0b9-52ee-bf6c-8f331b0195b6 | note | Material Property:
814c752b-bb60-50f1-96f9-edf0e7c737d7 | note | – – – – – – – – –
c0a6959d-2e3d-5fb8-ac12-ff1d57863ae2 | note | Material Property ¦¦ Requirement
f2a02c5d-7e16-43b5-bb11-24639f86353b | note | Liquid limit ¦¦ < 35%
6023c1d1-dc64-42b9-b566-66672555818b | note | Plasticity Index ¦¦ < 12%
cf82e18b-2dd1-4b6c-af80-f76a73ba9eb2 | note | Wet Strength ¦¦ Not less than 125 kN Wet/dry strength variation of less than 40%
a6256b04-31e1-4c46-bb8b-be1963b43002 | note | Linear Shrinkage ¦¦ < 6%
c25f9859-1f75-4146-8214-12162e402f21 | note | Organic Matter Content ¦¦ < 0.2%
28a6fc05-a96f-400f-9a83-f665e36487fe | note | Maximum Particle Size ¦¦ 75 mm
18e70ce3-cd41-4e80-b2e7-cdecd621e86f | note | % Passing 0.075 mm sieve ¦¦ 0-12%
426ddf19-4a19-428c-81d9-a0976b6ba863 | note | Soaked CBR ¦¦ > 20%
56b31f61-ec77-4a26-9c02-193aec6fd96f | note | CBR Swell % ¦¦ ≤ 1.5%
3c76cdd8-3729-43ea-9684-809f18ec2000 | note | Permeability ¦¦ < 5 x 10^-9 m/s
279ea369-5031-4f1b-91e8-626b863153c5 | note | – – – – – – – – –
d5283e63-ac96-4ffb-8466-b3b6a9038e9a | note | Gradings:
c2e5e53a-5d01-4f32-a8cb-c9d3eec343f1 | note | – – – – – – – – –
e962e5c9-1583-517a-8479-ab3ac3cd2746 | note | AS1152 Sieve Size (mm) ¦¦ Percentage of mass passing sieve size
cfe1cd19-1284-5aa2-9cf8-91fea8545b4f | note | – – – – – – – – –
bed041fd-d001-5108-af09-ef0e9711b9e0 | note | 75.0 ¦¦ 100 to 100
f320a33c-f6e6-5e94-99ea-c648d595de8b | note | 37.5 ¦¦ 67 to 100
2f304236-d42e-550f-bb74-14664bc6880a | note | 26.5 ¦¦ 54 to 100
1c1acd2b-5d4c-5220-9478-f62ad2876162 | note | 19.0 ¦¦ 44 to 85
6d8636bc-a42b-5f14-9b5f-c72cb8ab9d44 | note | 9.5 ¦¦ 31 to 65
31e3bec9-ba20-56cd-8c5a-6f576fda8073 | note | 4.75 ¦¦ 21 to 50
0faee927-3dcf-5944-91aa-5c5917c5dccd | note | 2.36 ¦¦ 13 to 38
c568518d-b7e3-533f-a9a7-bc6383d1fb15 | note | 1.18 ¦¦ 9 to 30
b3f56a11-f6f1-5983-937f-1d114c23c723 | note | 0.425 ¦¦ 4 to 23
0d6d1251-8dbd-5410-b46f-a3b6e67d4b61 | note | 0.075 ¦¦ 0 to 12
d6ae7631-afe6-5798-9b1a-d28144e937a3 | note | – – – – – – – – –
040eeceb-01be-5cb7-acbf-c3f57fee68c1 | note | ○ Production testing if supplied select fill will be: 1 per 1,000t for first 5,000t, increase to 1 per 2,000t following conforming 5,000t of conforming results. If material source changes, testing to be re-conducted from start.
04ffc556-268c-52b6-b721-d92339b742b2 | note | Reference Documents - Spec 002 – CL2.5 Cl2.7.5
3ca23b7d-514d-5470-97a3-39d41093fa60 | note | Inspection/Test Method - Test Report
9c5f393c-f175-51db-9434-fda4147480d2 | note | Record of conformity - This ITP signed
8a63c909-49de-5436-b4b5-575aefd813ac | note | HP
02927e97-19f7-5fbe-a3b4-eee1b7c62d58 | note | Responsibility - Project/Site Engineer Principles Rep
da34b4ca-7a9f-578d-9c02-d4fabb27fd31 | textbox | Checked by: Principles Representative - Aconex:
071c1a9c-2607-5e67-a29d-6a65f01f5cb8 | date | Date Completed:
2851e022-b0d9-56e3-9a4e-6c082b32a0d6 | signoff | AUTHORITY HOLDPOINT
f232dced-33bb-568f-a2fa-a747fd009e10 | checkpoint | 1.5 - Select Fill Material Source (Other Locations, Site Won)
063b6ae1-0810-55a7-b6a7-6b5db22bfcbb | note | Frequency - Prior to works
258f4ebc-f34d-5d30-bd3f-22d86510d714 | note | Acceptance Criteria - Each source of select fill shall be approved by the Principles Representative.
ac6389cc-17e2-595b-b34b-dd88ffe8864e | note | Reference Documents - Spec Cl 2.6.2
719895c5-7f3e-5091-ba15-8a37bcc0b054 | note | Inspection/Test Method - Test Report
b178ae95-a6a8-5f30-a71e-77c3180b179a | note | Record of conformity - This ITP signed
5fea5191-b455-5379-a562-341e47f23a5c | note | HP
1b1175c9-563b-5f66-9a51-8150698498ab | note | Responsibility - Project/Site Engineer Principles Rep
e3e36edf-af24-4dfa-9403-05f346394d44 | textbox | Checked by: Principles Representative - Aconex:
51923049-c02d-5ec6-b16f-c5aea6323641 | date | Date Completed:
4f1faf1f-32cf-5c03-ada3-e9a28be51c49 | signoff | AUTHORITY HOLDPOINT
78804ac0-3e61-566e-8208-64cfe762ca7d | checkpoint | 1.6 - Submission of Select Fill Methodology Plan
d005a128-0585-5c5f-a4ed-dc6cd7fed680 | note | Frequency - 14-days Prior to works
7f0a4f4d-b378-5a12-b0e4-f56352981a2f | note | Acceptance Criteria - Principal Contractor to submit a Select Fill Methodology addressing the criteria listed in Spec cl. 2.3.1. Hold Point to be released by Principal’s Representative after acceptance of Select Fill Methodology.
9669e478-dd97-5343-81cd-5199ba8b11fb | note | Reference Documents - Spec cl. 2.3.2
9a4f811b-2c81-59e0-bc06-90aeeca2bea8 | note | Inspection/Test Method - Select Fill methodology & verify
7ee34b39-a2d3-5e3b-b6b4-d71bab0d7184 | note | Record of conformity - Select Fill methodolog y & this ITP signed
ab118804-4cfd-581c-a8b2-4173b3f62ba2 | note | HP
c427744c-00ec-5244-95ee-1968a0a0506d | note | Responsibility - Project/Site Engineer Principal’s Rep
3ff59667-9db9-5e0f-af41-a6422fa1c607 | date | Date Completed:
603923c1-5792-516e-9695-7b16fe07e83f | signoff | AUTHORITY HOLDPOINT
93a0280e-652b-5cbf-b020-d3fa7b051fb8 | checkpoint | 1.7 - Starting Works
191a663e-328f-5ce5-a946-a8d013cca794 | note | Frequency - Prior to works
6988de33-b3cc-59d5-ab8d-79735df2e94a | note | Acceptance Criteria - Principles Representative to approve works starting in each Separable Portion
d953518c-4665-5be5-9df4-3b5706752e35 | note | Reference Documents - Spec cl. 2.3.1
8da07ef4-0244-55ed-84cb-82af9c176d0f | note | Inspection/Test Method - Verify
9c0d8931-832c-56ec-b854-27402cac329e | note | Record of conformity - This ITP signed
01cc9dd3-f181-5d4e-b595-c5bddced1061 | note | HP
1c0dfe50-17e6-5aec-a644-70f7bd58cd85 | note | Responsibility - Project/Site Engineer, Principal’s Rep
f8c8d075-b3c2-428c-b172-8159d39d679b | textbox | Checked by: Principles Representative - SP8 Aconex:
b154fc99-0a6d-550d-b606-cf95d0f9bece | textbox | Checked by: Principles Representative - SP9 Aconex:
5e843dd3-b3d2-5eb4-9338-9d3baeddc93d | textbox | Checked by: Principles Representative - SP10 Aconex:
ed099b5c-abd0-5fc3-bf77-6287326c1569 | date | Date Completed:
59b60230-39ed-59c3-b78a-fb4e61c6129e | signoff | AUTHORITY HOLDPOINT
c558d9a3-521a-5d48-b5a0-ab318534cad4 | checkpoint | 1.8 - Preparation of Underlying Surface Layer
3fd33117-7eb2-586f-aa85-c38c3a5e3e4e | note | Frequency - Each lot
d49700fe-80cf-52d1-b05b-5a9dd1b1a079 | note | Acceptance Criteria - All excavation and filling are free draining to low points clear of the working area. Sufficient pumps, well-points, or other equipment for work area are de-watered as required.
29337356-89d0-56e5-9ce6-bb65769f6fa6 | note | Reference Documents - Spec cl. 2.8.2 ITP003
be289948-f406-5e5d-aa09-44a86a08572d | note | Inspection/Test Method - Verify
6554c8ee-bac9-53ad-8ac4-0c6a0f9b9336 | note | Record of conformity - This ITP signed
509f5b45-e354-5884-871e-a14c5219f88e | note | IP
a8de60f0-59c1-5c31-8c97-7ab7c45d6531 | note | Responsibility - Project/Site Engineer Foreman
843759f7-5dbd-5c16-aced-bd975265065d | date | Date Completed:
fe92d223-db1f-56f0-9a40-9bee7d494c9e | checkpoint | 1.9 - Cut Floor Level
6c8d8f56-6505-5557-a082-4e1a61cb67ac | note | Frequency - Prior to works
e41bf1b5-9786-5635-8da4-452b93549516 | note | Acceptance Criteria - Cut floor to be inspected for suitability - compacted, firm and dry
b5ec83c9-941c-5393-a618-6317d028adb3 | note | Reference Documents - WMS003 cl 3.3.3
4d0e6c39-2d95-58d1-8054-9ff4a0c20dc4 | note | Inspection/Test Method - Verify
1357443b-4fe8-50f2-bc24-5754a41f44d2 | note | Record of conformity - This ITP signed
8ca3c972-2063-5790-8b54-d410a0ba7407 | note | HP*
47799b55-8c62-5420-b582-d3bfe6e9728d | note | Responsibility - Project/Site Engineer Foreman
a61bf0fe-c74c-5468-8b07-734f781a523f | date | Date Completed:
956d87eb-1ea3-5a3b-b0ad-217a98aa1992 | section | 2.0 - Select Fill Works – Imported Material - Under Pavements
49f2c445-65d8-595e-a8e7-1a7107a4605f | checkpoint | 2.1 - Select Fill Placement
a285683c-8b89-5d00-8ee5-7dd4aed4cce1 | note | Frequency - Each Lot
1088eff9-1f90-59a7-b41b-14d0f0ad1908 | note | Acceptance Criteria - Each Lot of fill must:
76abb573-0b41-5839-8ab6-8f3a78d19147 | note | ○ Not be greater than 200mm in thickness
c7e45ad8-2f77-5838-8b90-c5dfcf3d6e79 | note | ○ Material is to maintain within 1% of the optimum moisture content during all steps of placement, compaction, and finishing
678a7288-b1b6-53dc-b1f4-3c67e7ce5832 | note | ○ Placement of material to commence at the crown or the highest side of the pavement, with each lane spread adjacent to the previously placed lane
6db7de3f-3c47-57c9-8429-27b32fabba9d | note | ○ The first layer of placed material is dropped and spread using a dozer, grader, or similar plant to prevent trafficking 7mm seal
af09624f-e3c1-5797-9314-8274a1c59ed7 | note | ○ Material to not be contaminated by foreign materials and other contaminants
dea3f41c-156d-5b00-bb00-1ff047c6fc4b | note | ○ Plant and equipment does not traffic 7mm Aggregate Seal
3dbc7cb7-6509-580f-91f9-e9a368e88d35 | note | Reference Documents - Spec cl. 2.8.4
f4e6e6d0-2488-542e-a580-ab6ff313a746 | note | Inspection/Test Method - Verify
255c8a3e-d31e-5112-864d-8f0b1a95a4c9 | note | Record of conformity - This ITP signed
cbb35942-afe0-5989-8175-5db882b1f056 | note | HP*
5f20e431-67c6-5049-94d6-bf6ddc20f219 | note | Responsibility - Project/Site Engineer Foreman
d8351717-5829-52da-9630-21fa92547fd8 | date | Date Completed:
cd06c634-3b25-54fe-9f17-72e175164dd2 | checkpoint | 2.2 - Proof Rolling & Compaction
f6bcdc13-2b29-5e73-a520-feffb5a5ff4c | note | Frequency - Each Lot
e256642d-13d3-5932-b4a9-3a0ded3bfdae | note | Acceptance Criteria - Each layer of select fill under pavements is to be inspected with the Principles Representative.
d7d39b8c-6eb2-537e-8c6f-760b58edb6fe | note | ○ A medium size vibrating roller (or larger) is to be used for all proof rolls.
ba9f68a4-a645-56b1-abbe-2ce5f7244fd2 | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
4f3eb4f4-7107-5840-9dee-53fc6614bbc9 | note | ○ At least one working days’ notice is to be provided to schedule the presence of the Principles Representative.
24ebd48e-de5b-5a02-b3d8-bd75dd473447 | note | ○ Maximum allowable rutting of 25mm.
8400133a-8770-5d5c-aa61-6afb25a99e31 | note | ○ No heaving to be observed.
d47c6d07-a0d7-4b4c-a959-37094aa81598 | note | ○ Proof rolling of the select fill will be approval to place Sub-basecourse or Basecourse. If rain falls on select fill prior to placing next layer, a further inspection will be required.
aa8ce4a4-dfad-50ae-9679-f4a320171abc | note | Reference Documents - Spec cl. 2.10, Spec Cl 4.6
43d9517b-b833-59e1-a928-f0e9191db911 | note | Inspection/Test Method - Visual Inspection & Verify
007a5866-30c6-5e94-9f7b-eda3d6be2915 | note | Record of conformity - This ITP signed
75d45070-7e38-5e90-be33-a40b6c4d25f9 | note | WP, HP, HP
1035b6bc-5313-55a3-89f8-247dc8516c36 | note | Responsibility - Project/Site Engineer Principal's Rep
e74b8669-4382-5781-a35f-13ab9e7a638b | date | Date Completed:
f9d3f337-d7df-5819-a509-9fab63543ffa | signoff | AUTHORITY HOLDPOINT
c2466015-5915-51a9-8eca-423a20554634 | checkpoint | 2.3 - Final Trimming and Surface Finishing
b969e5f6-98cc-5976-a1db-96e747fccfd0 | note | Frequency - Per lot (final layer only)
c5073318-1d2b-5d22-8b0a-7bfc85218377 | note | Acceptance Criteria - Final layer of Select Fill surface to the required level, grade, and shape with a tolerance of +0mm and -25mm. Intermediate layers of select fill do not require a Survey Conformance Report
bbcd9e54-00b8-5001-8b05-4da4db95e2bb | note | Reference Documents - Spec cl 2.11 WMS003 – cl3.4.5
cb48011c-a1e9-5dfd-ae7d-68851eeacc67 | note | Inspection/Test Method - SCP
61bdba24-af61-5bcf-8e88-65004e5e2603 | note | Record of conformity - This ITP signed
cbc322f2-a319-54e9-95bd-9652bfb5dd3d | note | HP
d843fe42-ddf3-58e3-b760-959cd61a1cff | note | Responsibility - Surveyor, Project/Site Engineer
5f10bc1c-6362-5c7f-b1df-be0007331eb8 | date | Date Completed:
c0aade32-64a8-5f42-87c3-c0ceb97e85c1 | signoff | AUTHORITY HOLDPOINT
480a09e0-ea92-5938-b3d2-6cc734b0994e | section | 3.0 - Select Fill Works – Site Won Material – Other Areas (Not Under Pavements)
611c3468-2940-5641-8ce8-27310ad03598 | checkpoint | 3.1 - Select Fill Placement
dd600633-1855-5efb-aa7a-b22b1a16b9ad | note | Frequency - Each Lot
6cf86ae2-1ebf-5597-a601-ce96a64e12c9 | note | Acceptance Criteria - Each Lot of fill must:
5c46b0da-a8eb-525b-805d-7a15fe1ddb17 | note | ○ Not be greater than 200mm in thickness.
ff7b2559-af03-547a-9188-aff61a7ed3ad | note | ○ If required, material to be lightly watered to aid in compaction.
164428fd-9f41-5a84-989b-371e5ef907e5 | note | ○ Placement to start on the high side.
606c0f40-6a0a-5a36-a25b-d94b5802f1b9 | note | ○ Material to not be contaminated by foreign materials and other contaminants.
595e330f-84d7-5d07-bdd1-f36f30d40394 | note | Reference Documents - Spec cl. 2.8.4
261751eb-649e-54fc-858d-2c38f03f9163 | note | Inspection/Test Method - Verify
6a4957a0-b9ab-5808-9006-ec62b9ccf935 | note | Record of conformity - This ITP signed
84c8b8d1-03dd-59e6-9d99-6c4ff276b04f | note | IP
2a1f2666-ba88-513c-b479-bda9af6ebe9e | note | Responsibility - Project/Site Engineer Foreman
3cd2359e-478d-5a7c-937b-723ea792aa09 | date | Date Completed:
1bfe831d-057d-54d6-9332-9df26d5d643a | checkpoint | 3.2 - Proof Rolling & Compaction
61716091-7ff1-53da-be97-6525d3ab0d02 | note | Frequency - Each Lot – intermediate layers
0e621325-bc78-538e-9d1c-ad5c898e2500 | note | Acceptance Criteria - Intermediate Layers
7eb80e75-eeda-5830-bbf2-877aa402d695 | note | ○ Each intermediate layer will be visually inspected for conformance to the specification following compaction.
16d757da-361e-5a78-a738-deaa432d1861 | note | ○ No rutting greater than 25mm observed
de4e646d-a05c-5dcd-bdaf-e12065b7296b | note | Reference Documents - WMS003 – cl3.4.4.1
1121916d-79fd-5972-b23d-a650ab4d24a8 | note | Inspection/Test Method - Verify
1c5f4405-0f62-5fb5-8c5f-310627cbe0fb | note | Record of conformity - This ITP signed
554a3ed7-20f7-5e35-83f7-6728a552da00 | note | HP*
e63bbe64-3698-541a-9ae4-d8da7237141a | note | Responsibility - Project/Site Engineer Foreman
ccaaa446-44ab-5a1a-af6f-eff82876dee0 | date | Date Completed:
59b6de6f-36db-4e4d-808a-997b73e3906b | checkpoint | 3.2 - Proof Rolling & Compaction
c08bae98-5572-5c0f-bc54-6c2e4e967af5 | note | Frequency - Each Lot (final layer only)
c5d002ec-66be-5b68-8f97-eae95a2aed15 | note | Acceptance Criteria - Final layer
546f7143-3279-5d94-9daf-380e3a1eaf5c | note | ○ Principles Representative to be invited to visually inspect final layer of Select Fill not under pavements.
333ff332-9e8b-5a29-a97a-d2e1c8e1531e | note | ○ At least 5m of longitudinal Select Fill and 500mm of lateral overlap of proof rolling between adjacent areas is needed.
5d380afc-eb96-5670-9bfd-668848f80509 | note | ○ If requested, Proof rolling is carried out in the presence of the Principles Representative
d960ea35-51db-573f-89d1-ce44c75a5cac | note | ○ If requested, at least one working days’ notice is to be provided to schedule the presence of the Contract Administrator.
b49298b2-d1ef-5f42-8be4-cf51205e8922 | note | ○ Maximum allowable rutting is 25mm.
af69c2c0-630e-5064-96fa-814131dd5fee | note | ○ No heaving to be observed.
b59bcabf-c714-52e2-92ff-fa9244039adc | note | Reference Documents - Spec cl. 2.10 WMS003 – cl3.4.4.1
381fbbab-cc3c-5605-9803-bee173c2d21b | note | Inspection/Test Method - Visual Inspection & Verify
716b97f9-32ec-58ce-8d4f-8e536b454e40 | note | Record of conformity - This ITP signed
93ca3368-b935-5713-9776-0469b8471dbd | note | WP, HP, HP
5c34c3a5-4097-5295-a686-eb8106c9fb84 | note | Responsibility - Project/Site Engineer Principal's Rep
40dbf905-4676-5e94-ae72-655a8ae24718 | date | Date Completed:
4059a6fb-81ea-5f9c-a1ce-717bd26edeb7 | signoff | AUTHORITY HOLDPOINT
f7b45ac7-7370-5e15-b918-9d991e274492 | section | 4.0 - Testing & Acceptance
670307a5-96f5-566b-91dc-2ebfaa94544c | checkpoint | 4.1 - Classification and Testing (imported material, under pavements only)
497bfaa0-6206-5775-81af-233539a11d92 | note | Frequency - Each Lot
271fc17f-30a4-59e8-bbca-65edc4f02acc | note | Acceptance Criteria - Imported Material Under Pavements
27355161-24bb-5967-93e9-dda843f4ba98 | note | – Dry Density as per AS1289.5.3.1
3179e986-b82b-5056-98ff-4aabbe83c0dc | note | ○ 4 test per lot to achieve average
e64042f7-dd1c-50be-926d-7c64a5cbf840 | note | ○ Minimum average standard dry density ratio of no less than 98.0%.
fdb3a14a-9a9e-55d1-ab92-eb781d5eda6f | note | ○ No single standard dry density ratio test result being less than 97.0%.
4dfaf25b-ec5f-5a98-b76f-018000e525bb | note | Reference Documents - Spec cl. 2.9 AS1289 5.3.1, AS1289 5.4.1, AS1289 5.8.1, Spec tab. 2-3
cde87d4d-e124-5808-9805-530b6d47ec39 | note | Inspection/Test Method - Verify
20e31860-c7e0-59f1-bbe5-e62b5343e90b | note | Record of conformity - Test results & This ITP signed
fec63964-1ec3-5c2e-b894-f48a5a9eee1d | note | HP
befcf3c6-d0dd-5b27-b626-a9a33bf6131f | note | Responsibility - Project/Site Engineer, Principles Rep Foreman
57cd6c31-ace6-54db-9b2e-2802c5fd7311 | date | Date Completed:
23824eb6-508d-5398-b1e5-f8ed54d7b2ad | signoff | AUTHORITY HOLDPOINT
ecd1a6b2-d49b-594c-8bb7-55abdcbc9c40 | checkpoint | 4.2 - Lot Acceptance
fd6d64c3-6ffb-527d-8b4b-bcb152ea8af2 | note | Frequency - Each Lot
6094e51b-56c8-55be-81e7-ccc9388928af | note | Acceptance Criteria - Principles Representative to review acceptance of lot according to table 2-3. Acceptance of lot will not hold up placing succeeding layer of subbase.
2da0f362-8c08-58fe-9a83-451b169eb89d | note | Reference Documents - Spec Table 2-3 Cl2.12
5cadbf22-2e7d-5c0b-8f81-bb24150c0f16 | note | Inspection/Test Method - Verify
5317b649-84e5-5a25-8ad7-23504448e577 | note | Record of conformity - Test results & This ITP signed
565abba3-17d0-5afd-9e87-56fb95d8fbf4 | note | HP
c23be552-5ce0-5137-bd63-cde77864010b | note | Responsibility - Project/Site Engineer, Principles Rep
f8286b5b-50b2-5dec-af24-fffc837e80cd | date | Date Completed:
39d52e64-abdd-5af5-bc89-31082ce50170 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c99016f3-cb40-5a62-aebc-b4d7bb465048 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
f2bc87cb-c91c-5291-95da-3deaa91d47f1 | textbox | Print Name:
997fdfdb-a196-5436-9205-97836b076b0c | textbox | Position:
68dcca9c-d28c-529d-b4b1-3ceac23b94e3 | date | Work Completed On:
2181d0aa-ae54-5dfc-8386-981fe6cd1902 | date | Date:
eacdf556-7493-5d31-8b67-b3ac4559ccfa | checklist | FH-ZU2-QU-ITP005 - Stormwater Drainage - Rev 1 | itp | ITP005 - Stormwater Drainage
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
54e098fd-2875-533c-ae63-868a90e30081 | note | Frequency - Prior to commencing activity
3a9488af-ceef-526d-a9e6-e8a30e966b9f | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
471f36d6-b4b4-5388-a9d2-5ae7ece93b5f | note | ○ using the correct and complete set of drawings
8f7a1599-66cb-573c-9016-a55fbc589bc8 | note | ○ all drawings are the latest revision.
c2e5a589-5901-5b02-9701-76e4ce132a9a | note | Reference Documents - Drawings and Aconex Register
a2ee1067-eb31-532d-8b47-6005b527fbc3 | note | Inspection/Test Method - Visual Inspection
bfafb1b0-e9c1-591c-b5de-dc2927d5d9b0 | note | Record of conformity - Up to date drawing sets & ITP
839ea919-c7d7-547f-a4c5-a127348d8a0e | note | HP*
95bf2957-8d71-57ca-98d9-f701505fe279 | note | Responsibility - Project/Site Engineer
16f17a8f-429d-5221-b86f-2a3ff34b50bc | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
2b1c2541-a2e3-53ee-acdf-59d7d816963e | note | Frequency - Prior to commencing activity
56e020d7-7c16-5716-9b87-daa768345924 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
bc2543d4-aa2d-54cf-a7b6-1c651c7eef89 | note | Reference Documents - CEMP, TMP, SWMS & WP
b2945d35-791b-5282-9eab-f1096aae2e5c | note | Inspection/Test Method - Verify
6743976f-a864-5448-8b47-d3bd43ab57a1 | note | Record of conformity - Site and Office Inspection
f3bde6b2-9eeb-5f16-a6fd-7ab73df5c502 | note | HP*
7247c46e-49a4-5101-afd6-c19f89422b74 | note | Responsibility - Project/Site Engineer/Supervisor
a959ad58-ba7b-515e-934e-cfe533042728 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
67c58622-d040-5817-8e40-c14ba3c81201 | note | Frequency - Prior to commencing activity
858c6e33-5f6d-5f36-b9be-131e6512679b | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
d89748f0-3fe4-5f6e-bd16-db487ca14c10 | note | Reference Documents - Excavation Permit
5ac316e1-5683-5604-bf46-2f6aa45e1fe3 | note | Inspection/Test Method - Verify
2a3b06da-8a9d-55ae-a1b3-00d7413308e1 | note | Record of conformity - Proof of signed permit
62992194-6156-50b2-81f9-ef93471b5596 | note | HP*
11702d77-2c52-5332-81a8-f6e2b636d283 | note | Responsibility - Project/Site Engineer
5da7027f-4163-53a4-8cf3-0db8251e49d5 | date | Date Completed:
8a938930-5b81-5c2a-981f-3429c2180500 | section | 2.0 - Stormwater Products and Materials
5f7ce117-da10-5b8f-8bce-12ebc1eaf9df | checkpoint | 2.1 - Drainage Pipes (RCPs)
41d9fad8-a375-534c-a828-f397d7515358 | note | Frequency - Prior to commencem ent of works
6f00cc3b-c4a0-5f15-b5f6-bf98b9efe43f | note | Acceptance Criteria - Drainage pipes supplied in accordance with AS4058.
bb56e26e-19e7-566c-ba5d-74cdce66240b | note | ○ Material submission approval.
b162d0c8-25a1-5911-b3f4-0422cfa98d99 | note | Reference Documents - CL16.6.1
8228597f-c73b-526f-af9d-351be9066490 | note | Aconex ref: DCWC Mgt-GCOR-009281
25943020-9f4e-5ca1-bb79-37472b1edede | note | Inspection/Test Method - Document Review
ad6d63b5-fe57-5348-bd57-1d841f377ee4 | note | Record of conformity - Aconex
d8eba816-e46c-541d-aec8-fefd40c15961 | note | HP
57487e94-4c41-5a5e-8e96-638ad350df34 | note | Responsibility - Project/Site Engineer, Beca
179683db-9a8d-5462-955f-c7ee24fced30 | date | Date Completed:
e3753df8-916f-5363-bbda-b521a4126ecb | signoff | AUTHORITY HOLDPOINT
1b2eb359-4c69-5a42-8120-5367c623b1bb | checkpoint | 2.2 - Pipe Support Cradles
8d618c69-5b5e-5645-817f-836c8e834b02 | note | Frequency - Prior to commencem ent of works
9c03adc9-e7de-52a6-993c-ccf61071cfe7 | note | Acceptance Criteria - Pipe to sit on firm foundation with pipe support cradles.
cea46deb-31cf-5803-af12-5fe92b2db20f | note | ○ Material submission/ Shop drawing submission.
b213bf5e-eb9c-5753-b606-7d40d87cd7e4 | note | Reference Documents - Cl16.5.6.1
a40cf2e5-0db3-51ea-b1c4-75fbd7cbc6d1 | note | Aconex ref: DCWC Mgt-GCOR-009496
076afd1f-35a5-5927-a7fc-edd5de7cec1e | note | Inspection/Test Method - Document Review
3a0220cb-cceb-5803-a539-4a7b71938cac | note | Record of conformity - Aconex
5acb6203-0f4b-5ceb-886a-84cdc070e164 | note | HP*
ec6daf90-e504-55df-a72d-5737e28ea03c | note | Responsibility - Project/Site Engineer
ee87f83a-c632-507e-9a14-1ea8ce2dcacd | date | Date Completed:
71c61f1f-7bf6-51f7-9473-621c8a53ddd0 | checkpoint | 2.3 - Encasement Material
046121b9-b4f0-54f0-8a63-31d5a43a9243 | note | Frequency - Prior to commencem ent of works
cfed6de3-a0e4-56e6-a0f6-bd5a01012fcb | note | Acceptance Criteria - Encasement Material to be 5Mpa lean mix concrete for all RCP’s.
75304e44-4159-53f3-9435-58d198c06a7b | note | ○ Material submission approval.
549db1d7-fd4a-5eab-b6d1-07156f91fe49 | note | Reference Documents - Cl16.5.6.1 & 16.6.2.2 & Tender Clarifications #36
eb1080aa-021d-5be6-b979-d353ecb13764 | note | Aconex ref: BecaCPL-RTRFI-000089
1ed1078f-fff6-57f8-b1e1-0cf5460b2dd8 | note | Inspection/Test Method - Document Review
42d9471f-bd13-5359-b02c-cf38eb141023 | note | Record of conformity - Aconex
be559595-6804-5b57-ac83-af45fe1f80c8 | note | HP
2e927600-b0f8-50f9-b5ef-90d1180e4339 | note | Responsibility - Project/Site Engineer, Beca
378e34be-3bd9-5bee-b76f-f57c9a9a2a99 | date | Date Completed:
d52c4130-ee00-55e4-80f9-ae18f97deb84 | signoff | AUTHORITY HOLDPOINT
ea30ceb6-447f-5f06-879d-cf20a33d83c1 | checkpoint | 2.4 - Backfill Material
fa1e2509-551b-53e2-b3e4-40cc2b17a126 | note | Frequency - Prior to commencem ent of works
00ce685d-1629-5606-af60-85e42324d169 | note | Acceptance Criteria - Backfill material to be 6% cement stabilised sand to pavement formation level or approved otherwise.
b7edf96b-f4dc-56ba-a385-62c46425914d | note | ○ Material submission approval.
1269190a-dcff-5390-9084-4e405c70093c | note | Reference Documents - Cl16.5.6, 16.5.6.3 (a)(i) & 16.6.2.2.
f4389ac0-ef80-594f-bf52-856b6d8aa05b | note | Aconex ref: BecaCPL-GCOR-000802
62c05dc6-f5a7-5245-b8ba-0b49ce5d172c | note | Inspection/Test Method - Document Review
1449f01c-c4aa-5c77-aa84-5af40b4e64e8 | note | Record of conformity - Aconex Ref
affd4a93-a921-5aa2-8cd0-44c441e6648d | note | HP
fd9f3fa5-4bfc-54a0-8e72-7bffd8a90810 | note | Responsibility - Project/Site Engineer, Beca
c7981258-9841-5a6b-88cc-4a9f38a7f6e3 | date | Date Completed:
f9b66524-c85f-5e85-aa46-2367e78ebd6e | signoff | AUTHORITY HOLDPOINT
b45f932a-0d12-5d1d-ac10-211cdf6d5105 | section | 3.0 - Stormwater Delivery
6d60dbb5-efe8-5503-9c41-8894fa297110 | checkpoint | 3.1 - RCP Delivery
88e5903e-8133-58e3-8e64-8e8887c3b17a | note | Frequency - Each Delivery
9ab65ed4-0c52-5684-b951-353241be59b1 | note | Acceptance Criteria - Drainage pipes supplied and delivered as per approved Material submission.
041fa456-d7d6-5468-88a3-8afbf07b794a | note | ○ Manufacturer’s conformance report.
325517ec-3131-5c6c-8485-ad1ddfe7f2ff | note | Reference Documents - CL16.6.1 & AS4058
4f86dc35-1ead-595a-963f-52d63f59fb27 | note | Inspection/Test Method - Verify
6c5cabb9-9f3b-5c37-b5c0-8304d309bcb3 | note | Record of conformity - Order Acceptance Form
5f4e3bae-bc6b-59ba-969b-1387a4915c0c | note | IP
fdf5360e-5800-577c-ad9f-ffc483d77ba0 | note | Responsibility - Project/Site Engineer
67bc3511-85af-51e9-a897-ae6d65695009 | date | Date Completed:
f12fff67-318b-5116-a2de-09fa37e1377f | section | 4.0 - Construction Activities
5c6df739-5258-5ade-9921-36b1301c399e | checkpoint | 4.1 - Survey Setout
184b7804-94df-5c10-9503-064b7e236985 | note | Frequency - Prior to construction and each lot
74e80b21-7b41-5c14-8fd1-0aaea06ed169 | note | Acceptance Criteria - Set out the stormwater drainage as shown on the Drawings to identify the locations, lengths and levels at outlets and inlets of pipes.
c997444a-d4ec-5293-9985-137593984628 | note | ○ This constitutes a Hold Point.
45c2e80c-419c-5521-b8b4-d3401d87004b | note | Reference Documents - Cl16.7.1
f12f3715-d50d-5ab2-ae65-f56d39c25ae4 | note | Inspection/Test Method - Survey
572ef53e-e8d6-50be-be91-ee3ee56e43f0 | note | Record of conformity - ITP Signed
39a0f67d-1725-5c40-9a71-dcb48f857a75 | note | HP
54ba654f-6272-5c0d-b9e1-ea03ebe60ed6 | note | Responsibility - Project/Site Engineer, Beca
fa4a235e-3294-560d-8789-a3d08c871e5a | date | Date Completed:
ff9f951f-7476-5d3f-ba8e-80db7c677589 | signoff | AUTHORITY HOLDPOINT
e4eb01cf-d31f-52a8-b825-5b5a10cd54a0 | checkpoint | 4.2 - Excavation
ae9b32ec-7fff-5d0a-9424-24163091f7a9 | note | Frequency - Each Lot
4d6accd7-8604-53a9-ba80-22e6de486899 | note | Acceptance Criteria - All excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
923600d7-e22b-5c6b-b9b3-98e96bec5038 | note | ○ Trench excavation is to commence at the downstream end, where practical.
c06bac9c-d541-57f4-9632-d0d3b38d1659 | note | ○ The width of trench to be such that the horizontal clearance from the outside of the pipe to wall of the trench to be minimum 300mm when under the runway and taxiway graded strip. Trench width outside of the runway and taxiway graded strip to be the greater of 150mm and D/6.
f20b6792-e317-56ec-9aab-88b5226f314c | note | ○ Subgrade Inspection to constitute a Hold Point.
107547f8-aa65-500c-ae0e-13c46097e260 | note | Reference Documents - Cl16.8.1 & Cl16.6.2.2
b4c9308b-6d7f-54c9-bb86-94b073803c26 | note | Inspection/Test Method - Verify
e4767b4c-5011-58e6-aed5-79760c673c48 | note | Record of conformity - ITP Signed
2ed83b9e-e250-51d5-9d5f-c97d45d2ec14 | note | HP
68cabd5c-0e9e-5d91-acd3-bdee66617bbb | note | Responsibility - Project/Site Engineer, Beca
a9d66231-9287-5067-8242-cbb0f31407c8 | date | Date Completed:
ff5e91b7-5a2a-57f8-87eb-01651d3a2682 | signoff | AUTHORITY HOLDPOINT
af37bbcb-ba49-5b6e-8c2b-a91b2ba28f0b | checkpoint | 4.3 - Site Dewatering
e99776f6-6cf4-5503-9c98-dd1a53bdacac | note | Frequency - Each Lot
389dad6e-d921-5c6e-84c1-f0e86313a748 | note | Acceptance Criteria - Excavations are to be kept free from water during construction and backfilling and provide pumps, well-points or other equipment as necessary.
b278c28b-7740-546c-9834-724a125c10a8 | note | ○ Any temporary works to be designed such that flooding upstream of the diversion does not occur. This constitutes a Hold Point.
c55d97ae-880c-5161-913e-dea6114660c2 | note | Reference Documents - Cl16.8.4
da00b571-a482-5590-8ee3-bbb311c60c04 | note | Inspection/Test Method - Site Inspection
93d02277-da10-5973-8a27-3ffba730c5a5 | note | Record of conformity - Aconex Ref BecaCPL-GCOR-000891
a7d77778-30f4-570c-a3f4-92e9ce0195a3 | note | HP
c829d6c5-3da0-555f-99f8-f98c7d2adf74 | note | Responsibility - Project/Site Engineer, Beca
8e733820-540c-5f3f-ba59-1d720e847f55 | date | Date Completed:
158e35e2-fa25-5a50-831f-0658256d25c8 | signoff | AUTHORITY HOLDPOINT
7ede9ad6-dd5b-5212-896e-f145ac8b730f | checkpoint | 4.4 - Confirm Ground Conditions
c24d7f4c-211d-512c-8f62-fb8c74c5f909 | note | Frequency - Each Drainage Line
1f1e2149-09a6-5a8a-bf8e-05bcf9343e0e | note | Acceptance Criteria - Min. 1 x DCP test to be undertaken per drainage line / structure to confirm ground conditions. If the first DCP is inconclusive or fails, additional DCP to be taken as needed based on on-site assessment of the ground.
03f1408a-fcfa-59d9-9794-c463a54760c7 | note | ○ Contractor to notify the Contract Administrator of any area of the foundation which contains material that is inadequate to support the proposed drainage structure.
21488094-6570-5bb8-b7d2-27530887acab | note | ○ Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, per note 4 on drawing ZULU-BECA-012-DWG-07102.
242cba19-a3d8-5f42-88f9-69b17170d46f | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
a504a46e-b0eb-5c9d-97d2-012af669a2a0 | note | Reference Documents - Cl16.8.2 & Tender Clarification 179
b45513b3-79a1-56a5-ad23-95b269d572e3 | note | Inspection/Test Method - Site Inspection
920754ad-5496-5649-ac23-cc159d334d41 | note | Record of conformity - DCP, Test Results
19a4ccca-6f42-515d-a026-65b358677d48 | note | TP
e0837cd8-3bb2-5877-86de-a5278106923e | note | Responsibility - Project/Site Engineer/ Beca
a252e786-e6c8-54d0-8b34-75422fb024b4 | date | Date Completed:
323efbc6-a12c-5e89-ae8a-d285ad22322a | checkpoint | 4.5 - Bedding
61b37c59-fb70-5d0e-a698-20adcac2ec80 | note | Frequency - Each Lot
af9fe81b-be0f-51af-9fc1-0aa0674506f3 | note | Acceptance Criteria - Bedding material/subgrade to be prepared for laying the pipes. Pipe support cradles to be placed on firm bedding. This constitutes a Witness Point.
a494ec9f-64b2-5c1a-adbb-3d56b1681edc | note | Reference Documents - Cl.16.6.2.1
3dbef3ef-2cbd-5041-8907-f8b8307af3a2 | note | Inspection/Test Method - Visual Inspection
1956b3b1-4e04-5e3e-9732-44247b2e39cf | note | Record of conformity - ITP Signed
b97739b7-6d89-55a2-b679-4865132d3009 | note | WP
092f1bf4-ab52-5aea-8233-0f976053f229 | note | Responsibility - Project/Site Engineer, Beca
d2238a42-f78c-584c-9962-043e884ad5b2 | date | Date Completed:
f4714e5d-4d40-5cef-833b-c6bd246f4dd3 | checkpoint | 4.6 - Laying of Pipes (Sample)
b0f015fc-6552-5b29-bc8d-4109aaefe0fa | note | Frequency - First Lot
fdcea21a-b0f1-5a9e-9488-f4881b37681d | note | Acceptance Criteria - Initial sample 20m length of concrete pipeline to be laid and approved by the Contract Administrator for line and level before continuing construction of pipe network, Hold Point.
8154e474-aae9-522a-bb86-a36adaf49a47 | note | Reference Documents - Cl.16.9.1.6
ff430c75-267d-5dc4-9bb9-27ba336032d5 | note | Inspection/Test Method - Verify & Visual Inspection
c912703c-040e-512b-9f93-f947c2067b52 | note | Record of conformity - ITP Signed
0a819ca1-a073-554e-b852-5981530c427d | note | HP
45418fb0-ad6f-55e9-bb76-4c331754f30c | note | Responsibility - Project/Site Engineer, Beca
364dcce2-0e59-5280-b67b-e0c39dfd3bbe | date | Date Completed:
f6289789-09b6-5389-8687-34863a6d111e | signoff | AUTHORITY HOLDPOINT
afa0a0c6-8f35-51b7-8ae2-75ecdc349b39 | checkpoint | 4.7 - Laying and Jointing of Pipes
55ab6429-192d-55db-90d1-e22d55d14f86 | note | Frequency - Each Lot
7ff6eaa5-759b-58da-bcda-b470e99c9620 | note | Acceptance Criteria - Concrete Pipes to be rigidly supported by approved steel pipe cradle during laying.
1ab0c57c-d867-51c9-805d-1cfba53d82cb | note | ○ Pipes to be placed with spigot end facing downstream.
6fe829fb-2d02-5890-ba73-92b42ff58f96 | note | ○ Pipes to be laid with the word ‘TOP’ and or lifting holes uppermost. Lifting holes to be plugged after installation.
3f96e12c-a485-5858-aabe-f2cf56590f05 | note | ○ All Concrete Pipes to be checked and subject to the approval of the Contract Administrator prior to commencement of backfilling, Hold Point.
2fcb497d-7650-53d4-a543-98138cafc299 | note | Reference Documents - Cl.16.9.1.6
eaf88d90-0d84-5b9d-9e63-fcd1e3dd790c | note | Inspection/Test Method - Verify & Visual Inspection
4ad99015-63ff-5ef0-baa5-e0c2fe2c7d66 | note | Record of conformity - ITP Signed
6a597174-ca65-5552-882a-99ff143fd83e | note | HP
c92309d5-ae3a-50f4-9998-027105030665 | note | Responsibility - Project/Site Engineer, Beca
e2eaa18f-509d-5079-a636-1319ae775611 | date | Date Completed:
d20dc25a-fc90-5eff-8bc2-8dcc4456488e | signoff | AUTHORITY HOLDPOINT
5ad7c8ca-97a0-5547-8ef2-3f3b02311170 | checkpoint | 4.8 - Survey
19ba0200-7d70-5c1c-9869-0b767944f1c9 | note | Frequency - Each Lot
ba84b8bd-9cfc-5c75-8319-359bfbd60ead | note | Acceptance Criteria - The alignment, level and grade to be checked on the obvert of every third concrete pipe unit.
051e0e72-b396-5bac-8001-2c429bd84e51 | note | ○ Pipes shall be laid to the lines, grades and invert levels shown on the Drawings. No deviation shall be made without the prior approval of the Contract Administrator.
3bcbb87d-38bc-50b8-854c-b22cd0532cd9 | note | Deviation from Invert Level
9cfa4cdb-4a32-599c-897b-a0be107b8529 | note | ○ Maximum deviation from design invert level to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
b404e9c4-7ff7-5ee3-9781-a07bfd70a889 | note | ○ Where the design pipe grade is less than 1%, maximum deviation from pipe socket to pipe socket does not exceed 20 mm.
bf35ce05-4c92-599f-848f-79c69bdded2a | note | ○ Maximum deviation from design invert level between upstream and downstream structures to not exceed 20mm and not result in zero grade or reversal of grade in any length of concrete pipe.
8ab47876-2624-553a-a091-f979dbe03713 | note | Deviation from Alignment
8746020d-7933-5d0a-94d6-715b8f5b708e | note | ○ Maximum deviation of the concrete pipe from the alignment shown on the Drawings to not exceed 25mm.
00bf8704-8b53-5f6d-90eb-dbeac1b3f060 | note | Reference Documents - Cl.16.7 & 16.9.1.6
98e36215-0999-5d5f-b355-ee54b245c97c | note | Inspection/Test Method - Survey
45d4783a-a78e-5de2-a1e9-a5aaae115305 | note | Record of conformity - Survey Report
e8c5c51b-7c73-5362-bbab-5bc699b81f75 | note | SCP
ec49249a-59ed-5f71-bd09-36378a6def97 | note | Responsibility - Project/Site Engineer
29281e2a-c5e9-596e-a91c-3ba3578fbc68 | date | Date Completed:
a21a4ac7-d74f-52f9-80a8-ed14b5804858 | checkpoint | 4.9 - Backfill Materials
d330036d-185e-5e46-8366-c2c7f4b375fe | note | Frequency - Each Lot
c465880e-2673-5fe3-a924-adb7d7121a49 | note | Acceptance Criteria - RCP’s under Runway and Taxiway Graded Strip
0ff8ca7d-6a9b-587d-82b3-ae0b80d2a9c6 | note | ○ 5MPa wet lean mix to 200mm above pipe obvert.
b7a47116-f844-5054-8ea5-77a8929a72a8 | note | ○ 6% Cement Stabilised Sand to pavement formation level or approved otherwise.
2b325fbd-334e-55c4-a31c-ad9693321040 | note | RCP’s outside Runway and Taxiway Graded Strip
8e1d4e99-575a-5cb3-a0db-2ff00c22e48e | note | ○ 5MPa wet lean mix 150mm above pipe overt completed in stages
a2be7076-28f2-5a0b-989c-7dd7e1330b73 | note | ○ Site won material completed in 200mm loose layer thickness (maximum) or 6% stabilised sand to pavement formation level or approved otherwise.
be32f9d6-757b-5617-af9f-340f9192925c | note | Reference Documents - Cl.16.5.6 & IFC Drawings & Tender Clarification #164
599b4af8-1dfc-5861-8e5c-a43813aff579 | note | Inspection/Test Method - Verify and Site Inspection
c8ab4ca6-dd7b-503d-a5d1-861f531aca8e | note | Record of conformity - Delivery Docket and ITP Signed
0d893b32-e969-5749-b54c-411d59d73362 | note | IP
ada9dd1b-ddca-5e6e-b385-6d121df1925c | note | Responsibility - Project/Site Engineer
5b8512f3-b805-5670-9e2b-46b008eb4aa1 | date | Date Completed:
8f5ad56b-ccbc-5351-8e29-07e076d4b2bc | section | 5.0 - Testing and Inspection
5269f1ff-a783-5266-b983-4f37188b54be | checkpoint | 5.1 - Compaction Requirements (RCPs)
20cf176f-a6b7-5c20-a15f-3a00128219f6 | note | Frequency - 1 test per lot.
130a3c59-641f-510a-aa7a-32754c96dced | note | Acceptance Criteria - Concrete Backfill Under Runway and Taxiway Graded Strip
d7323c0b-d2a3-52ba-b3c3-bdbbc0c3869a | note | ○ 1 compressive strength test for each 50m3 of backfill
b81c3dbe-96d4-5cad-8aaa-3c074b3ed218 | note | Concrete Backfill Outside Runway and Taxiway Graded Strip
13116915-82ef-58ce-a250-2e687f1b84fa | note | ○ 1 compressive strength test for each 100m3 of backfill
5b0edd3d-8dc9-5638-81b6-d2af923ddc36 | note | Backfill Zone - Outside the Runway and Taxiway Graded Strip (for site won material)
28818352-ac85-59f9-9890-d6dc2ad38044 | note | ○ Minimum RD of 95% SMDD (1 lot consists of every 50m3 for concrete backfill and every 2nd layer of backfill zone material every 40m.)
50268ddf-4832-5a04-b762-7344556c95dc | note | Reference Documents - Cl.16.5.6.3 (c), Cl.16.9.6 & AS3798.1 Table 8.1
e4e7c828-7985-5b35-9867-0ed080422016 | note | Inspection/Test Method - Site Inspection
7c2f5a42-9f8d-5f65-b4c2-8ab18d53ae71 | note | Record of conformity - Test Records
c98f2819-da3f-5a3b-9606-d21d1a15883d | note | TP
f5adbcf0-2707-52f6-844c-97e15c83e568 | note | Responsibility - Project/Site Engineer
49e3653e-dbb4-598c-928a-a15de17bcc47 | date | Date Completed:
425ea013-7e49-55f0-b058-434e57d240b7 | checkpoint | 5.2 - Inspection of drainage lines
dc0e3d4b-5cd4-5d5d-a0ed-7e2dd2a289ab | note | Frequency - Prior to constructing pavement
6dd1734b-9742-579c-9bb6-cb16e9c5a269 | note | Acceptance Criteria - CCTV inspection of RCPs required at the completion of the works.
65d7ac9b-b970-5c02-bb61-569d311577b3 | note | ○ Submission of CCTV footage to the Contract Administrator for review is a Hold Point.
21589f61-502d-5693-b289-8a8c5369d97a | note | Reference Documents - Cl.16.10.1
bd1cb358-993c-50bd-b162-888a5e2fe05e | note | Inspection/Test Method - Verify
5bfc6948-2c78-54c6-8b42-5e86765dbe38 | note | Record of conformity - Aconex Ref
5125a29a-784c-58df-bca6-136d172fd69d | note | HP
0a750240-ecff-52c8-9832-f0ad5e348793 | note | Responsibility - Project/Site Engineer, Beca
84fa9f99-d2e5-53e8-991a-df278960a6a1 | date | Date Completed:
cf83799e-b148-56c3-9496-619f3a2b924e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
07843a40-ad75-597b-8d27-a2d33627f1bb | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
74bea63c-2144-54cf-8d9c-2c5d0a5c32bb | textbox | Print Name:
ceef9121-eb7a-57ad-9b81-0ff6d16629d8 | textbox | Position:
93d9e161-3a8c-5069-bbc8-466eab8fc03c | date | Work Completed On:
4ad221ca-63b8-5fac-8d71-1d492ee82fa6 | date | Date:
723ead20-e652-509e-a1ee-bdda34e5a4b3 | checklist | FH-ZU2-QU-ITP006 - Subsoil Drainage - Rev 2 | itp | ITP006 - Subsoil Drainage
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b203efa7-9a22-5926-bd73-8de13b415a22 | note | Frequency - Prior to commencing activity
bbc090e4-5691-53ff-8630-4771d69f82b0 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0bd51d55-9b65-50b8-b133-094970bffa42 | note | ○ using the correct and complete set of drawings.
2796cb7c-8938-5ce3-864e-aed637875e7b | note | ○ all drawings are the latest revision.
46916086-2b53-5d88-ad5d-4ec4e0b35143 | note | Reference Documents - IFC Drawings
2331c893-c1ca-5edd-a5bc-32cd368b8062 | note | Inspection/Test Method - Document Review
0c7059cd-7c8d-5927-b2a6-53aeda36e7f6 | note | Record of conformity - This ITP Signed
2a4ea12c-0fc8-5bf2-8321-e0e60a39e82b | note | HP*
62a43976-e7ef-5bb6-b3c4-d0f251e5ed9b | note | Responsibility - Project/Site Engineer
babe2d24-e642-593a-b977-cfdd507e634e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
941dc993-a111-5574-9200-06146195396a | note | Frequency - Prior to commencing activity
40f86d52-0a66-57a8-890a-0408cd16eb95 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
2e4953e3-5ca0-5ad7-8b53-475ec0eb0254 | note | Reference Documents - CEMP, TMP, SWMS & WP
c9883755-8c08-5007-a533-cc805d703693 | note | Inspection/Test Method - Verify
9f40c57f-8d81-5fbc-97cc-5cc438a222b3 | note | Record of conformity - Site and Office Inspection
d456838d-d521-5f5e-9814-6ebab7e168ba | note | HP*
13a3a736-2da8-5338-9439-c66cf07d0f9e | note | Responsibility - Project/Site Engineer/Supervisor
8d3617a0-ff7a-589c-97a6-7746d94759b0 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
4621e442-d233-5395-83bc-ce811358abeb | note | Frequency - Prior to commencing activity
c10cec44-4414-5d8f-adad-794206ee4cef | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
6a9c7f96-9941-5267-b05e-e17eaf8ad66d | note | Reference Documents - Approved Permits
b7759b67-f929-5676-a29c-9f2d90988101 | note | Inspection/Test Method - Verify
f39f1bfc-9cd3-5716-a541-b40dbc723cf1 | note | Record of conformity - Proof of permit & ITP signed
7a6a615a-ed94-53da-aa6d-817b63f120c6 | note | HP*
178bd2a1-3ba0-50c6-afce-5996683f0817 | note | Responsibility - Project/Site Engineer
99112c83-d7a5-59d9-aef3-fc94599fd70f | date | Date Completed:
640c5bd1-aac8-5fb6-adc2-66cc46a99347 | section | 2.0 - Subsoil Materials
ff30ac65-459e-5113-9d3a-ab4a10f8d53e | checkpoint | 2.1 - Subsoil Drainage Pipes
5b646d98-aa7a-5836-ae73-381d8ebf1b62 | note | Frequency - Prior to commencing work
bcaec0c9-9031-5295-9942-dbf72084364d | note | Acceptance Criteria - Pavement Subsoils:
b7359a8d-0550-508d-8b02-ed66b1b36fc1 | note | ○ 100mm Dia slotted with filter fabric (sock) CL1000 SN20.
d5a93f8c-7cf5-5dd9-ac9b-3357d03174ae | note | Subsoil Collector Pipes:
b092e40d-b547-5be0-99d7-08a0a40cc028 | note | ○ AGL Carrier Pipe: 80mm Dia PN12 uPVC Non-Perforated Pipe.
c71454fc-b17e-5349-9e45-7aa67f16c22d | note | ○ SSD Carrier Pipe: 150mm Dia PN12 uPVC Non-Perforated Pipe.
0fe68566-15e7-5f87-ac33-ea7c86b3cb4d | note | Reference Documents - Cl.16.5.3, Cl.16.5.4 & IFC Drawings
7db0c490-ad5b-577f-af6c-8253694d2b26 | note | Inspection/Test Method - Verify
7b19fdb1-45b4-5c3e-8438-1738fb265c3e | note | Record of conformity - Order Inspection Checklist
5a52b1f3-475b-5840-a3fe-5ad3d836fb4e | note | IP
6a41afaf-d4b0-56ae-9cde-29297e7b2dbc | note | Responsibility - Project/Site Engineer
7e10c348-b168-547c-b344-2948e99a3363 | date | Date Completed:
e858c774-7201-5034-909b-d12807265395 | checkpoint | 2.2 - Bedding and Backfill
0a65b798-f2a0-50d4-8a54-048370d7f9e6 | note | Frequency - Prior to commencing work
65490841-89f8-52b9-a6c8-0e6ade8c75c5 | note | Acceptance Criteria - Subsoil Drain Pipes Under Pavement
8d673ba2-f482-50d9-8e8d-01e35ea81db5 | note | ○ Holcim’s 5mm Moriac Sand or approved equivalent.
ea074592-f6e0-5276-8ecf-09e2aa464e5e | note | Subsoil Collector Pipes – Under Pavement
90d57a37-66c0-5a63-9a00-37a0d5ea31cb | note | ○ Approved 5MPa lean mix.
0a750720-2d3c-5829-b0b1-43f7a714381f | note | Subsoil Collector Pipes In Grass
f6feccc3-2a5b-5c58-8c91-7bc66bc2ac4e | note | ○ Holcim’s 5mm Moriac Sand or approved equivalent.
a375508d-7a04-5b79-a062-dd33308b9ec0 | note | ○ Excavated Soil
0be3036b-e5c3-5cd3-94d1-82069d58357c | note | Reference Documents - IFC Drawings & VicRoads Section 702
192a4443-013d-5350-bee7-1ced123affd2 | note | Inspection/Test Method - Verify
04805040-cf54-5fbd-ab74-74d27943c596 | note | Record of conformity - Visual Inspection & Delivery Docket
12a91005-a1ce-5115-9639-3ff57f494a39 | note | IP
75b3b35e-138d-55f3-86be-0386538781c7 | note | Responsibility - Project/Site Engineer
977a00fc-306d-59b1-9a0a-2ac71d410998 | date | Date Completed:
32c59ad7-af87-5ed9-bdb5-404bdab7319f | checkpoint | 2.3 - Geotextile Fabric
1f00f2b1-23ff-5d29-ad30-843835eca1db | note | Frequency - Prior to commencing work
3654a3b6-f2a4-5ef2-a001-4d0b5aca6d9b | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter or approved otherwise.
e7938520-5e9f-54bc-91a5-5d8faeca7148 | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
cbdc78d0-0722-54da-8205-b90cc9af3622 | note | Inspection/Test Method - Verify
447ec906-7210-5a3a-a5f3-6f908f3d604c | note | Record of conformity - Visual Inspection & Delivery Docket
0c6a5fea-3afd-512c-8368-a5417aef9492 | note | IP
f8fe6ab3-b47f-56cd-a396-18119f9ec08b | note | Responsibility - Project/Site Engineer
d3362b11-23dc-5195-9144-10052d55416a | date | Date Completed:
b8e682d2-d993-5fb5-9467-4b54608abadc | section | 3.0 - Excavation and Installation
7d370922-7733-519c-b084-007467ea59e9 | checkpoint | 3.1 - Trench Excavation
93bdb9fc-556e-5244-9d83-f6783c956641 | note | Frequency - Each Lot
8c640fb9-21ba-520b-a95f-471abad2330d | note | Acceptance Criteria - Trenches shall be excavated to the minimum depths, widths and batter slopes as shown on the drawings.
56f6e280-b7f1-5fd9-a677-7c644276b746 | note | Minimum Trench Widths:
43759727-e5da-57a1-af50-b01cf3d394bb | note | ○ Subsoil Drain Pipes
43e28dc1-5a6a-5792-b73e-e85f01e8c46f | note | – 300mm total width for the subsoil drain pipe (DN100).
af2bffd1-df6b-5b82-83e6-861c7441d94c | note | ○ Subsoil Collector Pipes
02934fcd-64ef-573a-95a1-a5782919ad2c | note | – Horizontal clearance from the outside of the pipe to the wall of the trench to be minimum of 150mm for all collector pipes (DN80 & DN150 both under pavement and in grassed areas).
c83e1bc1-a23f-50ea-a791-ee6fee052881 | note | ○ Excavated material disposed per approved CEMP.
d35269e0-0384-5008-8156-7ca76583fce3 | note | ○ Completed excavation works shall constitute a Hold Point.
30c8a41b-bf2d-5399-81fb-af8d6620b1df | note | Reference Documents - Cl.16.8.1 & IFC Drawings
84ef1c63-e86c-5e80-8a4a-3617827e4c3e | note | Inspection/Test Method - Verify
20ae350c-40fc-5b50-9d8f-19f392727a14 | note | Record of conformity - This ITP Signed
2579ceae-223e-5bc5-813e-452564241e37 | note | HP
bc954475-f8de-599e-8749-faa5b05ffb8a | note | Responsibility - Project/Site Engineer Beca
6efe9634-1020-5184-b917-5d6940c41288 | date | Date Completed:
f3ac8999-e404-5e36-bf08-9da493dca846 | signoff | AUTHORITY HOLDPOINT
7c207bae-6922-56c2-bc1c-fd1a1380798c | checkpoint | 3.2 - Geotextile Placement
ef9802b5-3e5f-5715-a88b-5cb5dc0ff26f | note | Frequency - Each Lot
deb9c76e-c3ed-54e6-b14d-4668eeb6639b | note | Acceptance Criteria - Geotextiles in trench drains shall be placed to conform loosely to the shape of the trenches.
21d2eb47-3873-541e-b2c9-79d7673f0a3e | note | ○ Site trial to be undertaken to evaluate the proposed construction process and compaction method, Hold Point.
dab879b0-1f17-5774-8e0f-6117afa132ea | note | Reference Documents - Cl.16.9.4.2, Cl.16.9.4.5 & IFC Drawings
82e70949-388e-58e4-a299-eb94ab7b8933 | note | Inspection/Test Method - Visual Inspection
71db4eed-f250-532a-bb94-bd3a828c4158 | note | Record of conformity - This ITP Signed
e5f82998-cc61-5ce3-93b0-24d850879a9b | note | HP
705d94a8-4029-58fe-a8b9-780793c31bca | note | Responsibility - Project/Site Engineer Beca
860b8d14-7b9e-506a-a000-6954dab63e0c | date | Date Completed:
19246d8a-6502-5423-8f48-410f20468d0c | signoff | AUTHORITY HOLDPOINT
c65e052b-cb68-5319-8e1b-8bfead12d177 | checkpoint | 3.3 - Bedding
edf8c917-c28c-5c70-b565-3e2d432fd2dd | note | Frequency - Each Lot
62421231-2c6d-5eca-9810-3473afb30050 | note | Acceptance Criteria - Bedding for Subsoil Drain Pipes Under Pavement and Subsoil Collector Pipes in Grass
bc12892a-da80-540e-8469-0dfa293e3156 | note | ○ Bedding of granular filter material or approved equivalent:
9ef781b3-6406-5d7a-b1e3-c4c4d0ffd4bb | note | – 100mm for subsoil drain pipes.
8739fd5d-84f9-595e-bd56-eb792fcc829d | note | – 75mm for subsoil collector pipes
4a1d56be-0e72-559e-8a13-4adfe3968569 | note | ○ Filter material shall be placed and compacted with minimum disturbance to pipes and in layers no greater than 200mm uncompacted or as approved otherwise.
f7bbff52-7368-5ad4-ac3a-16b9fd15f9eb | note | Reference Documents - Cl.16.9.2 & IFC Drawings
a1ff3c14-5b58-56dd-9b30-9a770d99dedc | note | Inspection/Test Method - Visual Inspection
edbf6be4-9c0b-5c1e-8e98-001ed939039e | note | Record of conformity - This ITP Signed
11b14a64-c51f-50ef-a675-66ea99711356 | note | IP
60facb07-3d1a-5dc6-9896-76c918e4279c | note | Responsibility - Project/Site Engineer
b6e19c2b-861b-5e35-aa57-f3dfa61fcc93 | date | Date Completed:
bf93a28a-5e59-52ec-b619-d5e40854365f | checkpoint | 3.4 - Laying and Jointing of Pipes
acc63919-1859-5956-accd-4338e7a69607 | note | Frequency - Each Lot
982dab69-d0d8-5ee3-9b07-5a9200f9ad52 | note | Acceptance Criteria - Pipes laid at the depths and lines indicated on the drawings. Where grades are not specified, the bottom of the trenches shall be trimmed to provide no less than 0.5% longitudinal fall.
43ca6168-124c-5106-916f-7f05a8f1181f | note | Reference Documents - Cl.16.9.2 & VicRoads Section 702.03, 702.09
f30b24eb-069d-52f8-9c80-00edf093fa0c | note | Inspection/Test Method - Visual Inspection
8d17080c-d48d-5c25-8294-368a7b2b11f5 | note | Record of conformity - This ITP Signed
12ccdfeb-6447-5b5f-9c90-89d12c8e5783 | note | IP
5af6caf2-1f5c-55ba-9bda-dd7a686406ea | note | Responsibility - Project/Site Engineer
5fed5454-4550-5138-823f-625274cf1e2e | date | Date Completed:
929f05a2-5222-5ae8-8d37-53da19f97499 | checkpoint | 3.5 - Backfill
82e0d72f-b673-55f3-a373-a8ea5a346c9c | note | Frequency - Each Lot
782fda5e-a891-560b-a090-0d895cc5246e | note | Acceptance Criteria - Backfill for Subsoil Drain Pipe (⌀100mm pipe)
16f6de95-850c-54e9-9cda-8db3e3234d8a | note | – Granular filter material or approved equivalent backfill is to be placed to the underside of the CTB layer.
c65b7a80-90b6-58d2-b607-783ba0e61707 | note | ○ Backfill for Subsoil Collector pipe ⌀150mm Under Pavement
db90f132-f0d7-53d9-8eae-ea8a81b12ea0 | note | – 5MPa lean mix backfill is to be placed to a minimum of 150mm above the pipe crown to underside of pavement formation.
7815479a-a64b-514a-a8ac-c710635bff3e | note | – Backfill to be completed in two stages to avoid pipe floatation.
52e3cb2e-51b0-5ed2-a80d-117db9ebcc0a | note | ○ Backfill for Subsoil Collector pipe ⌀150mm In Grassed Areas
e01eaf9d-2a64-523d-b88e-eaba57882e10 | note | – Granular filter material or approved equivalent is to be placed to a minimum of 150mm above the pipe crown.
04f9a45d-67aa-5f3a-9cf6-d80049db9353 | note | – Excavated soil recompacted in layers not exceeding 200mm loose thickness to underside of topsoil.
7a5f02a3-76eb-5822-a496-80137de680ef | note | ○ Backfill for Subsoil Collector pipe ⌀80mm
3d708b91-b862-571a-bd20-879a1ca722a2 | note | – 5MPa lean mix backfill to be placed to top of 150mm FCR subbase layer
d63fb179-d759-5832-859e-dff393f317ce | note | – Backfill to be completed in two stages to avoid pipe floatation.
e2f44423-fabd-5fc4-a2bd-d2019986ed13 | note | Reference Documents - Cl.16.9.2, IFC Drawings & Tender Clarification #38
2c3a2b19-1ecf-55da-b4cc-23359d952d5d | note | Inspection/Test Method - Visual Inspection
c359ccd0-b0bf-56ed-9d34-2103b9b83abc | note | Record of conformity - This ITP Signed
89d9dfb0-fe82-54a4-b618-7d17b9f3ecf1 | note | Project/Site Engineer
5a6ddc48-3b75-5b34-a0cc-51ff2e6bbcdb | date | Date Completed:
aa113495-ff71-5ee9-af22-889d3a144bc7 | checkpoint | 3.6 - Geotextile Protection
2729af9d-76e7-5b4f-b482-22072c7b5378 | note | Frequency - Each Lot
93d4d9f0-a715-5621-902f-6b616213da84 | note | Acceptance Criteria - Geotextile must fully envelope the backfill material in the trench with a minimum 150mm lap.
9cac07ab-e16d-4284-bfb7-7686791e9c0d | note | ○ Prior to placement of next layer of pavement material, inspection to be undertaken to check if the geotextile is correctly overlapped and free from punctures or tears and ensure it is pinned down to prevent movement and the filter material becoming contaminated. Should these issues occur, they must be rectified prior to placing the next fill material. This shall constitute a Hold Point.
43351c17-7eda-5104-ba99-610b06d2a88b | note | Reference Documents - Cl.16.9.4.2, Cl.16.9.4.3 & Aconex FHPL- GCOR- 006263 & IFC Drawings
f54cbdc1-b074-5ceb-b237-b304e63b3eca | note | Inspection/Test Method - Visual Inspection
118f5f81-1efc-52a1-88c9-a445cb2c84c2 | note | Record of conformity - This ITP Signed
dc0e6d00-83df-50ea-81de-bb9fbdfead91 | note | HP
02300ae5-d391-51c9-a516-b20c5ddd137f | note | Responsibility - Project/Site Engineer, Beca
cc3b74dc-e10e-501a-a4f7-2f5006fa8096 | date | Date Completed:
3bc895d2-9865-5f8e-b872-b810f8cc5d91 | signoff | AUTHORITY HOLDPOINT
0d640a99-ec2e-5652-9486-4672ee480699 | checkpoint | 3.7 - Subsoil Drain Outlet
4ce793d0-4b56-55ae-bbda-0be872c461e9 | note | Frequency - Each Lot
160fda7a-f329-55cf-b8ba-fdf84ab370a6 | note | Acceptance Criteria - Subsoil outlet point to be located at a drainage pit, pipe end wall or outlet in a fill batter or drain. All subsoil drain outlets shall be fitted with Vermin Guards.
59bd5fb0-e432-5242-b273-7bf5b9e311ed | note | Reference Documents - IFC Drawings
7b40b719-15b4-5402-93d8-59527c560432 | note | Inspection/Test Method - Verify
f3ef272f-cdec-523a-903c-f3f96bd94df1 | note | Record of conformity - This ITP Signed
4717fb7b-5e44-5540-b72d-1c7a289ab715 | note | IP
c6899f67-80fc-5df1-80cf-fe23901deb0d | note | Responsibility - Project/Site Engineer
47d5459c-6674-578c-9823-3add99fab108 | date | Date Completed:
b16f032e-a06c-51da-bedd-4bf211c93ec3 | checkpoint | 3.8 - Flush out Risers
4ca51bc6-a49b-5cdc-90f8-be1ffe24b462 | note | Frequency - As applicable
3e406be0-0322-543b-a8ef-6daa7ba05a9f | note | Acceptance Criteria - Cleanouts shall be located at the heads of all subsoil drains and as specified on the Drawings.
4a800173-7989-52ab-8d58-a3d54e3636fa | note | Reference Documents - Cl.16.9.2 & IFC Drawings
6cd03d77-7d8a-54ad-9359-c814cb1e0d82 | note | Inspection/Test Method - Visual Inspection
5494ab28-0f52-5649-b76a-f86b564fb504 | note | Record of conformity - This ITP Signed
7d927a6d-e401-5733-aaf5-fff9868ebd5e | note | IP
3d8ea8a8-f64e-597f-b966-ffb378018b49 | note | Responsibility - Project/ Site Engineer
89424513-edb2-57cc-b080-fa44a44fceac | date | Date Completed:
d0dd6e34-86d2-5297-913f-37b8b638172d | section | 4.0 - Post Construction
29e6a9a6-c10a-5416-a835-e9aa5e568085 | checkpoint | 4.1 - Flushing Test
ac2cde80-3d01-529a-812e-aef469bf814a | note | Frequency - Each Lot
33817df8-516a-506f-bf30-2f709891d88f | note | Acceptance Criteria - Flushing test to be carried out for subsoil pipes to remove material that has entered the pipes during construction and to ensure that the drainage line is free from obstruction. This constitutes a Witness Point.
9b875275-a4ca-5915-bdf5-2499e12fbd6d | note | Reference Documents - Tender Clarificati on #33
eee59dc7-f9c7-5a81-8506-01615d50d95b | note | Inspection/Test Method - Visual Inspection
02293552-747a-5fd4-866a-94f45d6e5a3e | note | Record of conformity - This ITP Signed
62c6cda1-4101-52c8-9adf-97edc1fddbc1 | note | WP
67f67238-bbbc-5e97-b0ec-911c93b51479 | note | Responsibility - Project/Site Engineer
c6604951-a6da-5fa5-a47e-d47d5f6087bd | date | Date Completed:
f28c1d32-46be-5ee4-a0e8-31aecf23fb4d | checkpoint | 4.2 - Records
265d3813-d435-55c9-8a25-0b3901c43330 | note | Frequency - Each Lot
a5ebcd79-d827-530b-81ad-26bce792df85 | note | Acceptance Criteria - Levels and alignment recorded in as built documentation.
5a5215f2-64c1-573e-ae61-0cbce602f745 | note | Reference Documents - As built Data
4c686766-1525-5f55-bbeb-013432f0beb7 | note | Inspection/Test Method - Verify
0d197c67-89f3-5a1e-b1ae-c8ebc5c7e02f | note | Record of conformity - Aconex Correspondence / Asbuilts
287c6857-e310-5e63-8b19-69f7316bccd1 | note | SCP
5b6a66e7-a082-5f5d-b2a2-fea9a80aa612 | note | Responsibility - Project/Site Engineer
5ebdc4ef-343c-5375-8a19-e6b25236d540 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
61331d75-b3c7-5352-8079-414b603e3db6 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
5572ef30-e932-5a08-a991-e4f08674c94b | textbox | Print Name:
f6667217-4fcf-50bd-b2bf-6f44ca637a42 | textbox | Position:
f259472e-32a8-5470-b3b9-9487c05a4eb7 | date | Work Completed On:
933ef43f-f06a-5888-ba35-78c4fb61c965 | date | Date:
beb379db-a922-5180-82d2-2d45e5dc0c76 | checklist | FH-ZU2-QU-ITP007 - Precast Drainage Structures - Rev 1 | itp | ITP007 - Precast Drainage Structures
d7d6e24a-41e3-57a2-9551-08a3da3fcd83 | section | 1.0 - Preliminaries
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
5db1b43a-1481-53e1-8de3-6d2f2dc31855 | note | Frequency - Prior to commencing activity
1a76d17f-abc3-50a3-b63a-504f13b3a613 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
0d8d158f-73f0-5a63-b5b1-81123ed6bfe9 | note | ○ using the correct and complete set of drawings.
bbdc7d62-c614-531d-9e87-93061dcfdf4b | note | ○ all drawings are the latest revision.
2cceb0a1-7ceb-5f46-90ba-44ce40a286b7 | note | Reference Documents - IFC Drawings
57e73c5b-8753-5f96-9e6b-7503760b523e | note | Inspection/Test Method - Document Review
3453148d-86f9-55d1-9874-e84456f23411 | note | Record of conformity - This ITP Signed
f2aebf2b-e43a-5cb6-b55f-8253f262294f | note | HP*
31f3edd6-0a74-5ffd-994f-63f47528d216 | note | Responsibility - Project/Site Engineer
9b90ffe2-5c62-5bad-b57d-2238a6456e16 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
7db392a2-fa21-5236-8c16-e9900da3e150 | note | Frequency - Prior to commencing activity
f4083910-855f-57c0-9147-6a80de365aa0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: CEMP, TMP, SWMS & WP.
06f95c10-fae3-5fe3-ab27-fe120bb891db | note | Reference Documents - CEMP, TMP, SWMS & WP
8a3feeb6-5bce-57be-b8e7-c3078292fad6 | note | Inspection/Test Method - Visual Inspection
016a468e-f575-5630-a16d-5dfbd4f4075a | note | Record of conformity - Site and Office Inspection
a0e8ae7d-3b8c-58c4-9d58-ac3382dc190e | note | HP*
bb752f86-d03a-511d-84ff-723e46cdeb21 | note | Responsibility - Project/Site Engineer/Supervisor
dba43527-ddff-57f6-bb82-05b51bf52559 | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
b22648d9-7d02-580d-85cd-cdbdcad4c8ac | note | Frequency - Prior to commencing activity
191cd235-416b-56c4-ae45-ba847c9b457a | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
3fd46ef3-909e-574d-bc0a-517872f8ebd0 | note | Reference Documents - Approved Permits
aed208a1-ac7a-596e-9042-0a061c81d802 | note | Inspection/Test Method - Verify
83a18917-fc0f-5b77-80ab-116c9821c0b8 | note | Record of conformity - Proof of permit & ITP signed
5d722d91-8a36-5933-b731-3c1675a16b46 | note | HP*
2368bad9-cb75-5cf3-a8ba-657e6c725e1b | note | Responsibility - Project/Site Engineer
70234546-ef16-5344-83b2-265b140986d3 | date | Date Completed:
12d91755-f6b0-5418-b819-f73d40c1e0c5 | section | 2.0 - Material Approvals
f7951c56-de28-5258-8451-17b4166c3f84 | checkpoint | 2.1 - Precast Structures
ab58fa24-f116-51e1-bb56-2a5a9c8ec0a2 | note | Frequency - Prior to commencing activity
cf5ed991-6585-57b3-b911-3d0f86fa22e2 | note | Acceptance Criteria - Details of the proposed precast drainage pits, headwalls, and culverts to be as specified on the IFC Drawings.
bdd411b2-4986-53fb-b73b-7e7c7000d1e2 | note | ○ Approval of the shop drawings constitutes a Hold Point.
dc249841-c08f-5a5f-af73-76dbf53cd354 | note | – Outline of sampling and test program
fed5492d-1da5-53b7-a7cf-795b5d8a04cc | note | Reference Documents - Cl16.6.1 & Manufacturer's documents
1301e68d-a0a5-5b05-bcea-f42d62c4a43f | note | Inspection/Test Method - Document Review
727e61f8-7fd4-50b5-a15d-86daf5052d56 | note | Record of conformity - Aconex Correspond ence
0599f0ff-d4c6-5ff8-8896-4d09cc6f8ea3 | note | HP
60e01000-b791-57e5-bb2f-4f7d4d1ff2ac | note | Responsibility - Project/Site Engineer
2794c579-9153-5731-8224-ae2a4141554f | date | Date Completed:
b4c31f0b-0aa9-590b-a901-d453e8a0654a | signoff | AUTHORITY HOLDPOINT
64f2e985-6054-5a03-b410-dc6ff9bee5d3 | checkpoint | 2.2 - Access Cover and Grates
ee79c773-1a56-5fe8-899f-c58377ade254 | note | Frequency - Prior to commencing activity
738d9405-acdd-56c8-ba83-7a8e734ab43c | note | Acceptance Criteria - All Pit covers to conform to AS 3996 and the applicable load class to be as noted on the Drawings.
fa10de75-6a4c-5fb4-a5fb-5874320a4794 | note | ○ For all drainage pits, pit lids are to be Class D.
e579fe7a-accd-5bed-91df-d69f754eb26c | note | Reference Documents - Cl16.5.7.1 & IFC Drawings
ec5278a1-6e0e-5f5b-b066-f574f2cc1a35 | note | Inspection/Test Method - Verify
26f47815-84b6-555e-8d46-79bb5eaf571e | note | Record of conformity - This ITP Signed
01dc8e7e-e7f0-55ad-8db3-4ececbf30b27 | note | HP*
bd40906a-f0ca-51cc-ad66-83ab99c6018f | note | Responsibility - Project/Site Engineer
bb342a11-5224-5e4d-95e4-d782fb070f5c | date | Date Completed:
e6b7e050-8df8-5309-8d57-3ace2e422035 | checkpoint | 2.3 - Box Culverts Bedding, Side, Overlay and Backfill Zone Materials.
688061a6-81b0-559a-8250-397751cc1678 | note | Frequency - Prior to commencing activity
f4a418bf-6ffb-5a9d-aba5-c09c320a74ba | note | Acceptance Criteria - Materials are to be compliant with the requirements detailed in Cl.16.5.6 or as approved otherwise.
38053ff1-cd39-5fdf-8ce8-f5930d7b639e | note | ○ Material submission approval.
16451f44-84f4-5e7c-9a14-7a0da0f8e1d3 | note | Reference Documents - Cl16.5.6 & 16.6.2.2
8b226639-1b33-5015-b62c-a5ab6e527522 | note | Aconex ref: BecaCPL-GCOR-000960 (Box culvert installation methodology with approval of materials for use)
30b99241-d916-525a-bfc3-2d08052484b7 | note | Inspection/Test Method - Document Review
2eb85dda-ae6a-50fa-bbfb-e924fb5d65de | note | Record of conformity - Aconex Correspondence
bb4d22c6-594e-5e4e-a331-0681ccdd570c | note | HP
7fcdd18b-5de0-57e4-9b71-aaa4a4660761 | note | Responsibility - Project/Site Engineer, Beca
08680424-9ec9-592b-8546-d45754dd8cba | date | Date Completed:
1d22fc60-66a1-5916-ade2-7806e4ace807 | signoff | AUTHORITY HOLDPOINT
7a40bb56-ecee-5114-bbd7-28b82b977398 | checkpoint | 2.4 - Blinding for Drainage Pits and Headwalls
2cdc4b40-de5a-5ded-8076-77119d0265f3 | note | Frequency - Prior to commencing activity
a24482b1-7c81-59d4-a748-46579e1d29c8 | note | Acceptance Criteria - Approved bedding material as per IFC Drawings or as approved otherwise.
783bb8e2-be87-5037-9220-8c38c2c4dd3c | note | Reference Documents - IFC Drawings
7ab25307-343e-5eb3-bcf9-7a0d3eeb0fd4 | note | Aconex ref: BecaCPL-RTRFI-000089 (Blinding mix) & DCWC Mgt-GCOR-009582 (Crushed rock bedding for pits)
f44ffccd-5943-5302-aed5-53db29ae97ce | note | Inspection/Test Method - Document Review
63f4a899-fbd9-5678-a97e-10b5d6ed1165 | note | Record of conformity - Aconex Correspondence
e90d6749-9565-5df0-b4c1-b94133094ae9 | note | HP*
930504cd-e750-5cfb-b16e-1becd7073c2d | note | Responsibility - Project/Site Engineer
11bca55f-d813-5454-a26b-d1954d7f4432 | date | Date Completed:
b4208e7e-9703-5497-9cf6-a7359c21d079 | checkpoint | 2.5 - Geotextile Fabric
0951a30d-bcd5-5f82-bef2-ba9a2aad8644 | note | Frequency - Prior to commencing work
f891fcef-102e-5a05-8555-ad08670e8ccb | note | Acceptance Criteria - Non-woven type complying with the requirements of VicRoads for first stage filter or as approved otherwise.
24b2885c-192f-549e-802c-228765e85054 | note | Reference Documents - Cl.16.5.8 & VicRoads Section 702
e5e4b048-774b-50c9-ba9a-7182b3bd8257 | note | Aconex ref: BecaCPL-RTRFI-000144
c630faca-13d4-560f-830e-3f4aa85bed97 | note | Inspection/Test Method - Verify
1294c6fe-f4d9-590b-9f86-0f6f852ba88a | note | Record of conformity - Visual Inspection & Delivery Docket
c0d53522-9130-5af2-a8d7-de0dc81e3b98 | note | IP
4dba0165-a49b-5344-86bc-0d5dd9ac3264 | note | Responsibility - Project/Site Engineer
b2b17873-ad3d-59da-a630-c012a3d50118 | date | Date Completed:
66be0a60-ccaa-5da5-82e3-47322e7bc7ce | section | 3.0 - Material Receival
4e595278-c063-523d-9160-3efd6b8df4d5 | checkpoint | 3.1 - Precast Structure Delivery
510d066f-aaad-521c-acd0-6ab33d93d77d | note | Frequency - Each Lot
dd9eb527-123d-5ff3-8a1d-3dc9615eb7ee | note | Acceptance Criteria - Ensure each precast component is inspected upon arrival ensuring:
07b2c205-7888-5b47-92a6-db01e80e6c1d | note | ○ Dimensions are as shown on manufacturer drawings.
7cc21e09-88cc-50a3-9e6f-0ca3fb4973b0 | note | ○ All blockouts in correct positions and to dimensions.
135c1ef7-713d-5cc5-ba69-8ad6e14a1ce1 | note | ○ No damage to any precast structure component to the satisfaction of FH Engineer
8d9ffef1-ea02-531e-8f73-963f781550bf | note | ○ No modifications to the pits are to be made without written approval from manufacturer.
5074dbb4-fe4f-5a86-8c38-d55d527c200c | note | ○ Manufacturer’s conformance report
6d2e38b7-5e7a-579b-98aa-27efa490fb76 | note | Reference Documents - Cl16.6.1 & IFC Drawings
16726ebd-142c-5e2d-94c3-c144f08e5ef2 | note | Inspection/Test Method - Visual Inspection
315da72d-1ceb-58aa-8eff-c1fd0d60823b | note | Record of conformity - Order Acceptance Form
59a9abc0-badd-59c7-8e34-ca95cacf72b3 | note | HP*
0f267815-5dc3-5586-9e6c-2588f0be04e8 | note | Responsibility - Project/Site Engineer
9b599835-4289-5d69-b59b-6d98ad2786ab | date | Date Completed:
8411b870-30d9-58f8-9930-1bfc13a433c0 | section | 4.0 - Drainage Pit, Headwall and Culvert Installation
5c6df739-5258-5ade-9921-36b1301c399e | checkpoint | 4.1 - Survey Setout
96f73f4c-1ddb-5ecf-8655-9ec86c40c259 | note | Frequency - Prior to construction and each lot
80120edb-cad5-57b6-b432-a9dfba621b6a | note | Acceptance Criteria - Set out the drainage structures as shown on the Drawings to identify the locations, lengths and levels:
eaaa0d90-e5de-575a-bd91-aeb0a7373072 | note | – All pits, and inlet and outlet structures.
c40a009b-6410-5c62-97aa-7dbe26d35a79 | note | – Ends of wing walls and headwalls.
15456013-b6fe-5a16-8b34-9444a9a3f601 | note | – At outlets and inlets of box culvert structures.
739131ea-764e-5029-b752-a70fa5c75714 | note | ○ Setout of each drainage system to constitute a Hold Point.
6c41b77b-65df-5b8e-9a67-f535ee05e9e9 | note | Reference Documents - Cl16.7.1
1f07cdb5-abfd-522c-b9e8-564f84f66c66 | note | Inspection/Test Method - Survey
16a01d25-681e-5993-bc13-59adf1d5e086 | note | Record of conformity - This ITP Signed
219b5388-f45e-56f4-a1df-a87748de4426 | note | HP
14944d7e-92c0-52a4-bacf-e90676402f30 | note | Responsibility - Project/Site Engineer, Beca
fa7a906f-cd3c-519d-84f4-67963423f62e | date | Date Completed:
ff9f951f-7476-5d3f-ba8e-80db7c677589 | signoff | AUTHORITY HOLDPOINT
e4eb01cf-d31f-52a8-b825-5b5a10cd54a0 | checkpoint | 4.2 - Excavation
1176e267-a531-5cdd-b74e-306ee86a5a72 | note | Frequency - Each Lot
e374136f-55f7-5a35-86e5-f75d59b8c3a4 | note | Acceptance Criteria - Excavation to be performed to the minimum depths, widths and batter slopes as shown on the Drawings, regardless of the type of material.
1a9ec8b6-abbe-5c22-9433-db8811c2a6dd | note | ○ Inspection of completed excavation works to constitute a Hold Point.
d8d48fdc-af48-5f58-80f8-c3a8dd8d7a41 | note | ○ Pits: The shape of the excavation to be as required and the size sufficient to enable construction of the structure.
dde9fb29-d00c-5e0f-80d9-470fd164b600 | note | ○ Box Culverts: The width of trench to be not less than the exterior width of the culvert plus 400mm, and not greater than that required for satisfactory backfilling.
ccdb8dbb-6936-568e-baa8-372a04b9834d | note | Reference Documents - Cl16.8 & Cl 16.6.2.2
c5d4529e-db4c-5d84-959d-20a5f2f5efb7 | note | Inspection/Test Method - Verify
d9f522df-c5ed-5ac9-9d83-0fa5b613c708 | note | Record of conformity - This ITP Signed
571c1da6-a91a-5fa3-a70c-66ec3ae68a74 | note | HP
c6c80ad7-00a7-5073-908c-c069c67ae74c | note | Responsibility - Project/Site Engineer, Beca
94484256-bf2c-5fd8-b6dc-a6317e71bd2a | date | Date Completed:
ff5e91b7-5a2a-57f8-87eb-01651d3a2682 | signoff | AUTHORITY HOLDPOINT
f916e68d-a2b3-5b1e-b050-5226d6cd6b04 | checkpoint | 4.3 - Confirm Ground Conditions
b8d350c1-8ff5-5b96-973a-67f22efdb856 | note | Frequency - Each Structure
20e25821-d580-5c2e-b669-b1ad3bb75e5f | note | Acceptance Criteria - Min. 1 x DCP test to be undertaken per drainage line / structure to confirm ground conditions. If the first DCP is inconclusive or fails, additional DCP to be taken as needed based on on-site assessment of the ground.
36164437-c5cf-56ae-9d48-c40a20b3ed9a | note | ○ Contractor to notify the Contract Administrator of any area of the foundation with inadequate material to support the proposed drainage structure. Inadequate material is deemed to have a bearing pressure less than 130kPa, equivalent to 4 DCP blows per 100mm, as per note 4 on drawing ZULU-BECA-012- DWG-07102.
2f1f7b49-708c-5f8c-a252-fe31b08cae2d | note | ○ Inadequate foundation material is to be replaced with a layer of coarse crushed aggregate compacted to 95% relative standard compaction to AS1289 Section 5.5.1 over a geotextile Bidim A29 or approved equivalent.
2350b2d8-7113-5a27-a640-aeecc9cfcaee | note | Reference Documents - Cl16.8.2 & Tender Clarification #38
ea4ce89e-4f55-53c5-bd51-7609dc2a8f82 | note | Inspection/Test Method - Site Inspection
2423809a-6b01-53b2-8e5b-8dd890b86fdd | note | Record of conformity - DCP, Test Results
06e8b35d-cbaa-523b-9400-83dc0bda6785 | note | TP
6c53e3f2-cb75-566e-aa85-9477e2f68835 | note | Responsibility - Project/Site Engineer
0414f3d0-9444-5ffb-b0fa-d989cc17b6be | date | Date Completed:
e8bd3d80-c970-5ff2-b8d8-884efdcd9bc0 | checkpoint | 4.4 - Blinding for Drainage Pits and Headwalls
bcad1afe-016b-5246-927e-c5f03a90f683 | note | Frequency - Each Lot
b55575d8-14b3-5e3f-8751-50467135ca28 | note | Acceptance Criteria - Blinding to be installed as per the depths and widths shown on the Drawings.
45ac2b98-d9a1-5003-b229-0a8f31ab2df2 | note | ○ Pits: 50mm Crushed Rock bedding
89a61e11-443b-50b1-8d5a-9700e1abaa68 | note | ○ Headwalls: 100mm 15MPa Concrete blinding or as approved otherwise.
ebd7362e-49bf-5a7b-9ffb-9e0d8661adbc | note | Reference Documents - IFC Drawings & VicRoads SD
0e10937e-f79f-5a21-a6a5-a510f354efb2 | note | Inspection/Test Method - Verify and Visual Inspection
7f27ad83-67f0-59e9-b805-d75ab259c9b1 | note | Record of conformity - Delivery Docket & This ITP Signed
dc4048a4-91fe-5f55-ada0-70be55bd2a52 | note | HP*
d9ac6299-f974-558c-b572-02ef9cc116d3 | note | Responsibility - Project/Site Engineer
f8ec5fdd-ff5b-5701-9419-f7ff43c7b7ef | date | Date Completed:
360c7d9d-bbd2-53e4-8559-df3b0d350a25 | checkpoint | 4.5 - Bedding for Box Culverts
f6104982-9dea-5959-98f6-70237c3d3dd8 | note | Frequency - Each Lot
4fa34d6c-f014-5a38-beb1-1c3e335ffd31 | note | Acceptance Criteria - Bedding material to comprise of approved select fill or as approved otherwise and to be placed for the full width of the trench.
42c26375-9a6c-569e-9359-fb0c5cfd5717 | note | ○ Upon completion, the bedding is to provide a uniform firm foundation with the top surface of the bedding shaped to the details shown on the drawings. This to constitute a Witness Point.
14025ba8-9afd-54e8-be08-4d2e8e8a27af | note | Reference Documents - CL16.5.6. 1
20d97cde-028a-5067-846d-c4bcc652d396 | note | Inspection/Test Method - Verify and Visual Inspection
18606999-4387-52e4-a1c1-37ccd808471b | note | Record of conformity - Delivery Docket & This ITP Signed
f52e261e-1bef-5aa7-8741-0bb3dabc2c2b | note | WP
61c2e6db-e12f-5367-ad8e-43d826fcc22d | note | Responsibility - Project/Site Engineer Beca
34b4a718-4ed3-563b-bec5-2a949aab05dd | date | Date Completed:
8e65e6b4-af39-5ca6-a9c5-8b0ace278aea | checkpoint | 4.6 - Positioning of Precast Structures
11f1ce0f-933d-5c66-b10d-8ca75e1a0230 | note | Frequency - Each Lot
cc95c182-f51a-5dd3-8794-6c3a70be63aa | note | Acceptance Criteria - Precast structures installed as per survey set out points marked on blinding / bedding layer
df1710e5-23d8-5ac6-b0a9-32a51a5dfb01 | note | Reference Documents - Cl.16.8.1 & IFC Drawings
52618993-76b4-5fe0-b5ec-760dd3780ed4 | note | Inspection/Test Method - Verify
d0e4ca64-9106-55b0-a47a-48a846c16bf7 | note | Record of conformity - This ITP Signed
62ffd668-108d-5f05-a822-06fac03094e8 | note | IP
5ef51f22-b49d-5375-87c3-b02487c59eac | note | Responsibility - Project/Site Engineer
ac26066b-3fa6-50e3-bf9c-b1f302782640 | date | Date Completed:
159501bb-b6bb-53ea-9a80-faa22dafd3d2 | checkpoint | 4.7 - Backfill Materials for Box Culverts
f797f376-3caa-58b0-bd53-dfce5ebb7902 | note | Frequency - Each Lot
4fa89b10-99b2-50e1-818a-1cb940c0473e | note | Acceptance Criteria - Side Zone, Overlay Zone and Backfill Zone Subject to Vehicle Loads
d2e1e579-fd48-5bdc-aee0-64eb6b1073a6 | note | ○ Approved 6% Stabilised Sand.
29ef28c6-caad-5e95-a851-4720cb916273 | note | Overlay and Backfill Zone – Not Subject to Vehicle Loads
39bc908f-7787-552e-9edc-bcd4afe87479 | note | ○ Approved 6% Stabilised Sand.
5f59707d-fbdf-5d92-aa4c-011a03990d19 | note | Reference Documents - Cl.16.5.6 & IFC Drawings
04391806-868e-55c2-967c-a5a34dd0621a | note | Inspection/Test Method - Verify and Site Inspection
f87b33fe-04c5-5d60-8d00-8d73cafd1cb8 | note | Record of conformity - This ITP Signed
32827412-ef03-5eae-97ff-c2b0e931a375 | note | IP
23df4aec-6efa-5a2b-bcf0-63d5419c08b5 | note | Responsibility - Project/Site Engineer
3d43666e-c673-5375-aaad-1c98ed6901b8 | date | Date Completed:
c83fdcaf-9e5c-50db-9b66-3cf10748adc8 | checkpoint | 4.8 - Compaction Requirements (Box Culvert)
98400f66-d4ff-57da-81dd-2aa44bd1cdbf | note | Frequency - 1 test per lot.
e82ad8bb-5d63-55ba-b493-617779f660fa | note | ○ "1 test per layer of bedding for bedding materials."
6505258c-50fe-5498-909a-6ec23215c323 | note | Acceptance Criteria - Bed Zone – Minimum 90% SMDD
cdbf78aa-742b-5d44-acd4-73ad8c9d8c0a | note | ○ Side Zone Not Subject to Vehicle Loads – Minimum RD of 95% SMDD
224642d9-8551-5dfa-9f37-38db447150ec | note | ○ Side Zone Subject to Vehicle Loads – Minimum of 95% SMDD
7185abd0-f6b6-5e6d-9992-fe193d868633 | note | ○ Overlay Not Subject to Vehicle Loads – Minimum RD of 90% SMDD
20b777a5-0948-5cab-a93d-a92f0a9be3d4 | note | ○ Backfill Zone Not Subject to Vehicle Loads – Minimum RD of 90% SMDD
a6406e74-85d9-50e7-bb1f-e5c15ddfa32d | note | ○ Overlay and Backfill Zone Subject to Vehicle Loads – Minimum 95% SMDD. Top 300mm under pavement to a minimum of 98% SMDD.
c3136cf7-8b38-5165-872c-2c5d937abe76 | note | Reference Documents - Cl.16.5.6. 1 (b) (iv)
db9b4411-efa6-5856-af78-2ea2b9335782 | note | Inspection/Test Method - Site Inspection
f82995cc-38b0-5b15-a358-a96ca9566be0 | note | Record of conformity - Test Records
473aac9c-b16d-5edb-bb4d-33375d1f8a79 | note | TP
d5d91f95-4800-5240-bfec-fc3ad1f31973 | note | Responsibility - Project/Site Engineer
af50add4-63eb-5738-b5a5-38eb32e83ab0 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
4bfba408-c2c7-5b13-a5b6-2aac8afb6c80 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
bd8aa650-6082-5eb0-9fb1-0784fb190a53 | textbox | Print Name:
07933e25-3d1e-5871-b20e-a61376c04a4e | textbox | Position:
94923ded-cd73-539a-81ee-c1c46804e037 | date | Work Completed On:
9c06ea5a-c74f-5bfa-9993-ce5fe6ee7f38 | date | Date:
83dcff00-7f03-54c5-96ff-8dfbf2083bb1 | checklist | FH-ZU2-QU-ITP008 - Lime Stabilisation / Subgrade Improvement - Rev 0 | itp | ITP008 - Lime Stabilisation Works
ff951edb-ead3-5ac5-97d7-0fdf5903d931 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Materials and Trials
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
f80ad63e-e054-58a6-a576-5a5156f8f8f3 | note | Frequency - Prior to commencing works
34372137-72c1-5b78-8857-0f4f56117113 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
580de26a-94ed-5a77-9d34-68c0de8454b4 | note | Reference Documents - Aconex
5884289d-b391-508f-8f26-6eb97aee0dc9 | note | Inspection/Test Method - Visual Inspection
2221d813-5b0e-555c-b17a-b06903a82588 | note | Record of conformity - This signed ITP
1641ee97-6204-5c83-9048-3a8b6c09dcc5 | note | HP*
0916181f-7bd9-570f-ba06-450763029d6b | note | Responsibility - Project/Site Engineer
3a82f130-c2e3-5900-9703-54d723e73696 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
2c1d7258-8000-5b31-8f79-226a154efb79 | note | Frequency - Prior to commencing works
417cbc72-d3c4-5e70-9d6b-6d7fd9543fa3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
f58b910f-8b97-58b0-9ec4-8d835fad21a5 | note | Reference Documents - PSP, EMP, TMP, WP SWMS
16c2ed29-62a0-56d2-a6bd-dcc04d5066c9 | note | Inspection/Test Method - Visual Inspection
c098280e-eab5-5450-82a7-3064d0f70f3f | note | Record of conformity - This signed ITP
4a2d40a3-38c1-5039-a5f4-dd646da1fe9c | note | HP*
cc8e0828-610c-5047-af96-86a758dd60ef | note | Responsibility - Project/Site Supervisor
17c04995-8757-5c6f-82eb-4b3d59be076c | date | Date Completed:
65eca0b2-e9e2-5d31-b703-45bbc204d847 | checkpoint | 1.3 - Current excavation permit
48755452-95f8-5c14-a233-f2e1cf26d6fc | note | Frequency - Prior to commencing works
b01f95de-178b-54ed-aeb7-b45562fdd472 | note | Acceptance Criteria - An Excavation Permit and an Isolation permit issued by Melbourne Airport. Fulton Hogan Excavation permit issued to plant operators.
fbbb0ee7-a34f-5610-bf1a-f5a488b2f235 | note | Reference Documents - Excavation Permit
d7fb0750-fc55-58dc-9eed-a9c56f8dc487 | note | Inspection/Test Method - Visual Inspection
4d53328b-f3e0-5e07-9229-c4368426e0b3 | note | Record of conformity - Permits
a28cb457-3300-5049-a9dc-6df79138d9f1 | note | HP*
16159f6c-a4d3-5c8a-9ff3-26033da1286f | note | Responsibility - Project/Site Foreman
b1e6b55d-eb1d-59ed-94ef-517a38151dd1 | date | Date Completed:
14c56455-f0de-5f93-9717-18fd02274123 | checkpoint | 1.4 - Preceding Lots Satisfactory
7b4d2be7-586c-5c08-92ec-a97afa14a7d4 | note | Frequency - Prior to commencing works
5a0cab34-2cd9-5151-83c4-bffc7a581e96 | note | Acceptance Criteria - Review ITP004 (Select Fill placement) and ITP003 (Stripping and bulk out) has been completed to a satisfactory level
d8e0fc77-3146-5441-a683-eca1b40121a0 | note | Reference Documents - ITP004, ITP003
11225a67-461e-574a-a52e-67f98e2149e9 | note | Inspection/Test Method - Visual Inspection
a50494c7-dc42-5d61-9716-1ad5c838a926 | note | Record of conformity - This signed ITP
c01588dc-e681-5eb9-ac50-cf96b17b44ea | note | HP*
947156b6-065d-5acf-b73c-792903b506a4 | note | Responsibility - Project/Site Engineer
2a7c5747-5127-549f-967b-707955a736f5 | date | Date Completed:
76b2ed20-883d-56e1-9e50-63150676e11e | checkpoint | 1.5 - Test Pits
7c8519cf-ff0c-5c02-aa96-9b158f5e6e29 | note | Frequency - Prior to commencing works
41a79849-3252-57fd-b30f-d4a68214ffbb | note | Acceptance Criteria - Test Pits have taken for the works area and suitable lime content parameters have been established. Test Pits should be taken at least one month prior to works beginning.
71daa2cc-6103-565b-b46c-98841bbca874 | note | Reference Documents - WMS003 – cl3.1.9
57acbe24-3046-54bd-bb53-a17a9127cecb | note | Inspection/Test Method - Visual Inspection
64134581-a21c-506b-99a9-d0d1c880f2a9 | note | Record of conformity - This signed ITP
ea9433d0-78af-51f7-94a0-b0b613798d59 | note | HP*
f22378cc-3fca-5bf0-b859-26e4d26a13d4 | note | Responsibility - Project/Site Engineer
545db90f-ab5b-53d7-bea8-b422883bd1d6 | date | Date Completed:
b3dd08dd-11b6-5f39-8645-239ea003b322 | checkpoint | 1.6 - Stabilised Lime Content
f2f31c7f-52ce-57ee-9395-40c354934c6f | note | Frequency - Prior to commencing
0e307209-0378-5981-9057-c4b66b6e204d | note | Acceptance Criteria - Stabilised Lime subgrade material shall have a minimum of lime content of 4% and a specified minimum strength of 20% CBR after 7 days of curing.
0ad1c593-f993-5554-b867-61a4f26394a8 | note | Reference Documents - Spec cl. 3.3
dfe53d81-bbca-5d9e-8f62-4e024c45e26c | note | Inspection/Test Method - Testing
21a7fda0-7769-5e6f-9181-6b849c545dfd | note | Record of conformity - Test results & This ITP signed
083f471c-d4f2-5af5-aaf9-70e82188470f | note | HP
cea4568a-f969-58c2-b43b-f9e846f19f75 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d0ac1f16-ef5b-5c04-b294-6e28176e1e57 | date | Date Completed:
a36502c5-adb9-560d-a70d-678505437c86 | textbox | Principles Rep - Aconex Ref:
83aa5d6c-d189-5195-a97a-4c1a535c3e2e | signoff | AUTHORITY HOLDPOINT
1e3af235-d8a6-52b7-8154-473184406420 | checkpoint | 1.7 - Stabilised Soil Trial
e3d0b6f7-6262-5ae7-a116-cdf8203cc42b | note | Frequency - Prior to commencing
2e2fcecc-d65e-5881-8a0f-c4e3d62082c6 | note | Acceptance Criteria - Trial of the Lime Stabilised Subgrade is greater than 500m2 to demonstrate that the Subgrade is able to meet the required specification.
d9320f77-f9cf-5415-aeee-ad3e50d4eeb0 | note | ○ If trial is approved and accepted by Principal’s Representative. Trial of Lime Stabilised Subgrade will form the completed Works.
764a3254-a6cd-5bb3-8d96-1553077c9681 | note | ○ Principal’s Representative to approve trial before commencing Lime Stabilised Subgrade placing.
c74c4ef1-a31a-5983-b31f-08be016efe25 | note | Reference Documents - Spec cl. 3.6
ee59310b-da9b-5b45-944b-c2caf07af9ba | note | Inspection/Test Method - Verify
97a2130d-f4a2-5239-b27e-9e5f00e946b7 | note | Record of conformity - This ITP signed
f0486ae8-36d6-593f-af18-abc1300c6ef1 | note | HP
f78d5313-a3c9-5c16-9805-4ae05ace1554 | note | Responsibility - Project/Site Engineer Principal’s Representative
8f783d79-6766-59c1-bb70-a94fb669fd07 | date | Date Completed:
c36a71d2-164f-57c8-9dfa-96c797a967ac | signoff | AUTHORITY HOLDPOINT
92110380-56da-5e6c-8b29-049697713c30 | section | 2.0 - Subgrade Preparation & Replacement
639e9b05-062e-503a-92c8-f9b52bb2162b | checkpoint | 2.0 - Pre-treatment of earthworks
62101956-cfd2-56c5-a143-4fcaba515afd | note | Frequency - Each Lot
ca2ab39e-38b8-5645-8e8e-460eeec59cf4 | note | Acceptance Criteria - Inspect subgrade that will require lime stabilisation.
f7698896-93d5-5474-af2c-25a6768a2d96 | note | ○ Subgrade that is excessively wet and/or contains rocks greater than 60mm to 100mm, subgrade will need to be removed and replaced with site won material.
449ef220-c86c-57a5-9b93-86589310e7a8 | note | ○ No testing or proof rolls required on replaced subgrade
e925ddb6-f95f-555d-bd8a-84e3a6919e3e | note | ○ Survey to for any excessive high and/or low spots. Fill / excavate spots as required.
6574d0fc-589f-501c-b9e6-d4e591f900c9 | note | Reference Documents - WMS008 – cl 3.2.1
d934765e-d9f6-599e-85ab-b2db351f6738 | note | Inspection/Test Method - Verify
2d74c1c7-55a6-5095-a646-e3a7e197179d | note | Record of conformity - This signed ITP
9c64b3e9-bc04-5d0a-b882-244b2a0eb039 | note | IP
6198c2fc-43cc-59eb-be6f-1ed67fefda31 | note | Responsibility - Project/Site Engineer
fc7a943e-af06-5ce0-ad19-febd7032786d | date | Date Completed:
c293051d-8e81-5993-be55-a414c1752978 | checkpoint | 2.1 - Rip Subgrade
0ed5f65f-3dd4-572f-b3f2-fc4a6da3a75f | note | Frequency - Each Lot
289ff85d-0e0f-52af-a6c4-b533252d1c95 | note | Acceptance Criteria - Prior to spreading lime, the subgrade is to be ripped and pulverised to at least 400mm
78a69a18-ef9f-5a5f-b19f-44f9a9e27cfa | note | Reference Documents - Cl3.7
07a86b6f-2f5c-53df-9cd7-e2343a34de4f | note | Inspection/Test Method - Verify
8ebee48c-0faa-5a95-8e7a-c814d37c73e5 | note | Record of conformity - This signed ITP
8987659c-3dd4-56df-8cee-3eafa73c79e0 | note | IP
0978e5f5-b066-569d-8337-01eadd85b626 | note | Responsibility - Project/Site Engineer
e412f8a9-a9a1-5572-a8f5-fca294ade8de | date | Date Completed:
1a1bf616-437d-580e-b174-4d67646e5283 | section | 3.0 - Layer Placement
0d246930-b701-58d1-9f0f-0403386ba8dc | checkpoint | 3.1 - Layer Parameters
99e44411-a4ad-5fcb-830f-e0d514ee55f7 | note | Frequency - Each Lot
9668753c-07fd-5ae3-9a2d-500b9dad8b2d | note | Acceptance Criteria - Summary of Layer Parameters:
e7987681-aecf-5adf-9e89-02b191d8bde4 | note | ○ A Lot is defined as one days production
fddf2ea4-53ad-52e6-9b97-31c9a6cd1f6a | note | ○ Min depth of 300mm for PT01, PT03, PT08
0b2f3865-99cd-5ea6-a77a-5b4f53aada8e | note | ○ Min Depth of 400mm PT02
a12d4f6f-4b99-52bd-a159-699b10b67c91 | note | ○ Shape: <12mm over a 3.5m straight edge
042cf666-81dc-5ef0-a900-b9ebf2205b1a | note | ○ Surface Level: -25mm to +0mm
d55ac57e-4ef5-53a8-a429-8559b87327f8 | note | Reference Documents - Cl 3.16, Cl. 3.14.3
f37964be-4804-592f-8472-6ac8abb7c365 | note | Inspection/Test Method - Verify
b6018f76-a667-5ba2-857f-b65ce20ea6e5 | note | Record of conformity - This signed ITP
4244dc42-aa65-5ad0-b98b-0e643ce23f76 | note | IP
ee8912da-58a6-5c54-a045-2dcd5397f24e | note | Responsibility - Project/Site Engineer
70f4e856-2faf-59ca-9345-bdf1a240d1f2 | date | Date Completed:
e188e23f-7387-546a-be1a-ef1b527e3391 | checkpoint | 3.2 - Prior to Works Starting
f09b7eeb-84a5-5d2c-a892-80da7ab3a55c | note | Frequency - Each Lot
8c0af34f-fa40-554b-af73-418ad7d50957 | note | Acceptance Criteria - Check weather forecast for rain and wind. Works to not beginning if rain is imminent. Works must not start or cease if wind increase over 15 knots.
e886f363-b2b7-5d65-a0d3-74b740221ef7 | note | Reference Documents - Cl3.7
428c7c0b-bcd8-5ef4-b124-ab659e25d26b | note | Inspection/Test Method - Verify
edea983b-1021-5459-87af-07fad8ad33ea | note | Record of conformity - This signed ITP
40298fdd-eece-5a4d-bf52-24aa79d1721d | note | IP
840a110e-9bae-54b5-b7b6-7aa8312005d7 | note | Responsibility - Project/Site Engineer
2097ba3d-a9c1-5756-a462-013f70a97ea0 | date | Date Completed:
7cff3135-aaaa-5a07-be57-d8a647bc4b01 | checkpoint | 3.3 - Spreading of Lime
78e2769e-331f-565f-ac61-b2172501c3a3 | note | Frequency - Each Lot
ee78259e-b187-553c-a8f8-a39f8b65891d | note | Acceptance Criteria - Lime to be spread uniformly over the prepared surface at the Lime spreading rate calculated.
33187a45-846e-52b6-ab6a-5d438b34c101 | note | Reference Documents - Cl3.7
ca0f43a1-fc2a-5041-9c08-4906d7047af9 | note | Inspection/Test Method - Verify
d8bc3daf-9fff-5d39-a2f3-3270cfd3f663 | note | Record of conformity - This signed ITP
0976379c-eeb2-55c7-91f8-d74f1929eb49 | note | IP
4ee44097-ec15-5b67-b8c6-59ed3780f975 | note | Responsibility - Project/Site Engineer
420033b4-467d-50e9-a35e-c3d53789f22b | date | Date Completed:
66449636-bf24-5bb3-86e0-ea99af02cfa4 | checkpoint | 3.4 - Spreading of Lime
a75badb0-eb77-5a41-8fd7-57d54ba88ce7 | note | Frequency - Once Per Hour
b74e3e83-f0f3-54a3-affc-686b1d414fcc | note | Acceptance Criteria - Lime spread to be checked every hour and shall be with +/- 5% of the specified amount. An area to be checked is required to be not less than 1x1m2.
3390d410-7f7c-5242-8e9f-d6a14c96a9d9 | note | Reference Documents - Cl3.7
94907931-d99d-5f4a-9ed1-72a7bd40a53c | note | Inspection/Test Method - Verify
1d6bc099-7de6-521e-a53b-c1dc33af1031 | note | Record of conformity - TP
6bce729d-7697-5a49-bed7-d09bba0b0fdb | note | IP
ad236bae-a6ed-5aed-89d2-cbd80ce624e7 | note | Responsibility - Project/Site Engineer
704bcd53-dd10-5f8e-abf6-1d85f6e1e264 | date | Date Completed:
933cace5-29ee-5793-b62c-7744cf4d97ac | checkpoint | 3.5 - Mixing
342dc891-c403-5f90-b824-bbf8f7a88c87 | note | Frequency - Each Lot
390ce6f2-6e8b-5b9c-af40-e7318e0b4f9e | note | Acceptance Criteria - All lime to be mixed to the specified depth within 8 hours of spreading. Mixing passes to overlap to ensure subgrade is mixed twice as a minimum.
cc5e43e5-aeea-5ebe-89e0-150f5c893321 | note | ○ Where possible, adjacent material will be placed within 1.5 hours of initial placement to avoid joints from forming.
1dffa4ef-977c-5200-9704-d4057650e30f | note | Reference Documents - Cl3.8
6bfe17ce-16bc-52bb-a1c0-3e907940d531 | note | Inspection/Test Method - Verify
e0aabdf2-0f0c-51bd-855e-f54daab64e09 | note | Record of conformity - This signed ITP
d0540783-c182-5522-b955-56420d6d484a | note | IP
994e21c9-ca3a-5509-a5a3-0cf0d1059d7e | note | Responsibility - Project/Site Engineer
9a5228ee-ec2b-5d18-8311-95a576bf01a8 | date | Date Completed:
ff71ab95-b7a7-5d0b-b295-91823ce88429 | checkpoint | 3.6 - Mixing
c562766c-54bc-512f-8f72-d70eadefc4f0 | note | Frequency - Once Per Hour
c1f928cf-02bb-562e-8be8-3b04caaf0ac3 | note | Acceptance Criteria - Approximately every hour, mixing plant will record the depth of application to check compliance with the specification (300mm or 400mm).
ce08e854-5a2e-5f75-a0ce-ee62a04c30b8 | note | Reference Documents - Cl3.8
fddc46ec-5c36-548c-9341-af9ba77c9e32 | note | Inspection/Test Method - Verify
3718af78-1a8b-57a9-a532-0dea2ad1f0fc | note | Record of conformity - TP
6e7b5fd0-bb87-52f0-8aa3-de05d6a89a6a | note | IP
604b6d97-13ba-5a6c-a11c-15e0afee918b | note | Responsibility - Project/Site Engineer
9911afd3-d0e0-521b-bea9-867e1aa90967 | date | Date Completed:
3697a363-4bf7-5a6e-9fc5-ad0f8c7a4397 | checkpoint | 3.7 - Joints
d260d097-aab9-5437-a478-470276285dfb | note | Frequency - Each Lot
87275da8-6c25-52f9-a6f7-98b66d093217 | note | Acceptance Criteria - Construction Joints when required, will be placed to ensure no single plane of weakness. Construction joints of adjacent lots will:
56b137d2-41f8-5edb-9b14-5cb2bf5b70bf | note | ○ Longitudinal Joints – Will be avoided by overlapping adjacent lime stabilisation mixing runs.
3ff60da7-8cef-5b45-aac3-88eb76284fb9 | note | ○ Traverse Joints – Will be staggered to avoid forming a single joint.
09fc5b76-e89a-55e9-91a1-304745c6f012 | note | Reference Documents - Cl3.13
4f5cf043-d1a6-5402-9422-ec3286759824 | note | Inspection/Test Method - Verify
0f8796f9-0f68-5d9d-911c-4dd0df554f39 | note | Record of conformity - This signed ITP
91fc4eb7-572e-5e1d-b5bb-73b2d8d06491 | note | IP
59a162e2-9def-5e63-800f-f58f1cd41a8f | note | Responsibility - Project/Site Engineer Foreman
71be9b34-2f3f-51e8-96e1-c87052da0403 | date | Date Completed:
413572a0-25bc-542a-acdf-8a670d1944f6 | checkpoint | 3.8 - Compaction
98edc022-ce50-597f-a49e-fd5f9cd8f64f | note | Frequency - Each Lot
a802c0d7-976b-507a-82ab-78328487457b | note | Acceptance Criteria - After satisfactory mixing, compaction shall commence within two hours and be finished within eight hours of mixing completion. Additional moisture may be added if required.
4c8d3682-ad1a-5729-9c6f-2e04e34da9f8 | note | Reference Documents - Cl3.11
e5693786-39f2-5aae-81e9-a3617205b081 | note | Inspection/Test Method - Verify
e15bc505-3a49-52dd-9b7c-9ed1054f2c30 | note | Record of conformity - This signed ITP
43fc5fae-6188-59b1-82a8-c5d0d4f56eeb | note | IP
a7256504-2d31-5e6a-bb32-f6b1487cad93 | note | Responsibility - Project/Site Engineer
813850de-8025-5607-84f0-7cdf4c1621ec | date | Date Completed:
2d7fbba9-dc8c-5587-8a0f-e95b8eb31515 | checkpoint | 3.9 - Trimming
b2c11689-93f9-520e-b751-4b92349a7772 | note | Frequency - Each Lot
70ccdfdc-aa8b-545f-9f9d-36c5789170e9 | note | Acceptance Criteria - Surface to be trimmed to +0mm, -25mm
a4867d15-b3ab-57ac-b389-76f5f082326a | note | Reference Documents - Cl3.11
2c8e1993-e02f-5023-82c6-ff4971f7b99f | note | Inspection/Test Method - Verify
21f15f9a-1bae-52d8-9b6c-b7f6cf06e552 | note | Record of conformity - This signed ITP
e4704b06-5569-5e33-a586-8cc50ab7f1c9 | note | IP
1357d1c2-2430-5df4-85a6-b9c7d2652ddd | note | Responsibility - Project/Site Engineer
e44933a5-f7c7-5f2c-a310-b86a294811e4 | date | Date Completed:
c0af1ea1-39d6-5efa-83e4-1636172927dc | checkpoint | 3.10 - Protection
3a917592-6749-5df9-b2e0-1e85c23e2f6f | note | Frequency - Each Lot
e2b99457-d65b-54d8-8fef-e7c361627566 | note | Acceptance Criteria - As soon as lime stabilisation activities start, no construction plant to travel across works zone (other than those involved in the operation for 48 hours minimum.
2dd506ec-22c9-5e37-a1bf-fc4acf1eedc7 | note | Reference Documents - Cl3.15
17f9f7c3-91cc-5b6c-8462-621aa1bfd5a8 | note | Inspection/Test Method - Verify
a3d5d5de-4b52-5924-9d24-2c0b71b05c48 | note | Record of conformity - This signed ITP
e7639432-5a5f-5ccc-88ff-b79580bbf1c5 | note | IP
7e023d29-6b28-5d62-b994-407b63ef41fd | note | Responsibility - Project/Site Engineer
eb4df604-5d71-5666-8157-65e62f99e767 | date | Date Completed:
f84bb287-d950-50cb-8abc-00e5cc9832d7 | checkpoint | 3.11 - Curing
f5d664e1-3302-5239-b31b-bb3d32877dae | note | Frequency - Each Lot
3634ecf6-60c9-5eb9-9428-1f7e010dcc54 | note | Acceptance Criteria - Curing shall commence as soon as practical. The curing period is 48 hours or until the succeeding layer is placed.
61592bc7-ee26-52a2-a062-6e051423a52d | note | Reference Documents - Cl3.15
7180bd48-55d1-52eb-bc1a-3e79860497ec | note | Inspection/Test Method - Verify
17d9e9eb-a333-5f92-a309-9d214f33daa2 | note | Record of conformity - This signed ITP
2ec1438f-9013-52d1-822b-308c154d145f | note | IP
02640a26-aa0f-5092-8fb2-64afa27ad078 | note | Responsibility - Project/Site Engineer
77d43f30-4dbf-58d2-86f2-a8ea53be2978 | date | Date Completed:
6ca566ab-1509-5601-bcce-96cd27b957db | section | 4.0 - Acceptance – Lime Stabilisation
347223d9-59ca-5890-96d1-49b7315b1ce5 | checkpoint | 4.1 - Proof Roll
2f9353b6-e54c-554e-8c1b-d099c954ad0a | note | Frequency - Each Lot
36368a93-d957-5fdf-89b4-f9e013b6bb09 | note | Acceptance Criteria - Following completion of the curing period, detailed trim and survey conformance, the Principle’s Representative will be invited to a proof roll (24 hours notice). Proof roll will be accepted if no rutting greater than 25mm is observed. Proof roll will involve using a heavy vibrating roller (in static mode)
c68d0f35-ea92-50b2-a8f9-67e617c28a42 | note | ○ Proof rolling of the subgrade will be approval to place Sub-basecourse or Basecourse. If rain falls on subgrade prior to placing next layer, a further inspection will be required.
01c1e634-186b-5a82-a4b8-b45d73df62b1 | note | Reference Documents - Cl3.12 Cl4.6
87be2623-dfbd-595f-891c-8be21e24dbf4 | note | Inspection/Test Method - Verify
18dcd2dc-0dc5-50c3-9665-7cd0923ebd3a | note | Record of conformity - This signed ITP
6fc411fb-3ae7-5906-8a89-562298867e11 | note | HP WP HP HP
d1fa4d52-e8b4-590a-968e-cf95e9142cce | note | Responsibility - Project/Site Engineer Principle’s Representative
66401dcd-82fa-5286-aead-1904100de9e2 | date | Date Completed:
9d6eb9f1-cb88-5972-8c60-c08da8aff17f | signoff | AUTHORITY HOLDPOINT
62d9d645-c8d9-5c1e-8705-8289f13a5ebb | checkpoint | 4.2 - Surface Smoothness
837b0e22-2d8b-5699-84c5-515f36d75e55 | note | Frequency - Each Lot every 10m
de08aee8-f886-5796-a501-5eabd7247879 | note | Acceptance Criteria - Long straight edge surface not to deviate by more than 12mm over a 3.5m long straight edge, following subgrade treatment
55319a9f-9797-5e69-859e-50134128725b | note | Reference Documents - Cl3.16
16184e99-8bbd-5666-ad3a-1593c7749c5b | note | Inspection/Test Method - Verify
b9fa94eb-211f-52da-8503-97c347b9b63e | note | Record of conformity - This signed ITP, Results Attached
badb7c5b-c62c-5b51-9f76-70912fae58ac | note | TP
0789e41b-dcac-5f88-996d-89e182908747 | note | Responsibility - Project/Site Engineer
b79112a3-6ced-57fa-b89d-fddd9e664d09 | date | Date Completed:
574d05bf-851b-5876-a180-0a560a77c85d | checkpoint | 4.3 - Strength Testing (CBR)
d85a453c-5089-51ed-954f-8e86db541710 | note | Frequency - Each Lot – Once per 1500m2
f5a104ee-3f30-5158-8fbb-ace6a4d16cbf | note | Acceptance Criteria - To exceed 20% CBR after 7 days.
dcfc4b1e-0919-542f-b37d-11d9d298b83c | note | Reference Documents - Cl3.16
9aafccc7-b587-5e41-9e41-508f824c8f8e | note | Inspection/Test Method - Verify
7d77674a-c72a-53e8-8a83-e1b6063b07ef | note | Record of conformity - This signed ITP, Results Attached
da13dbcc-c9e4-57d0-8957-1788082fb56b | note | TP
d639452d-ccd1-5669-8883-d3a580538630 | note | Responsibility - Project/Site Engineer
a45fc774-3ef6-57c2-b1f7-690c9bddcf71 | date | Date Completed:
77efabb3-9ddf-5f45-b887-19ac7988e251 | checkpoint | 4.4 - Field Dry Density
5b50c56a-2fb2-56de-a1a9-589bcd9b2868 | note | Frequency - Each Lot – Once per 500m2
13f56cac-10c3-5539-9859-e527e2da735f | note | Acceptance Criteria - Maximum Dry Density used is lime stabilised subgrade 100% using standard compaction.
f62b5305-d129-5dbc-bf9c-8ff4bafc6a11 | note | Reference Documents - Cl3.11 Cl3.16
92188a49-9e45-5703-b6e1-72394050c8e9 | note | Inspection/Test Method - Verify
458eb129-b3d5-54be-9309-1a51f9e67403 | note | Record of conformity - This signed ITP, Results Attached
f5b3e371-e308-5ab0-b6ae-b1becb453e47 | note | TP
a6ee8b2b-41ec-5e59-a54f-86f1f31451df | note | Responsibility - Project/Site Engineer
7fb847a3-e1dd-5c9b-871a-e52592ada559 | date | Date Completed:
3b380c3c-68d2-570c-840f-61931a66179b | checkpoint | 4.5 - Surface Level
f264f4f4-7d4f-54d0-8b2f-52a809c0980a | note | Frequency - Each Lot
a9239d3b-556d-58a1-9f60-bb446b8a5ee5 | note | Acceptance Criteria - Stabilised and compacted subgrade surface layer to comply within -25mm to +0mm from specified levels.
dd91c709-302e-59a4-9b57-787abfb44091 | note | Reference Documents - Cl3.16
5c788dd4-2a4d-591d-bc3d-cf3bd5319e8d | note | Inspection/Test Method - Verify, Report
03035fda-fbdf-5aca-9ea7-6a19bf79a240 | note | Record of conformity - This signed ITP, Results Attached
a3606e88-472f-5d9d-8a9b-d3aa27803cec | note | SCP
22446a72-33e9-53a1-a9d8-daa4db972c79 | note | Responsibility - Project/Site Engineer
8536f0c4-4dcf-5494-a569-c3e75eed94ca | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
77834e6f-6574-54f0-b03c-6bcabe6cb4dc | note | On behalf of Fulton Hogan, it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
e9b4af31-26aa-5a17-b1c7-baaf6919ffd1 | textbox | Print Name:
a304cf96-b429-5255-a2df-662eb05d02a4 | textbox | Position:
7de9a745-74e3-5528-8e04-9e99c94961b2 | date | Work Completed On:
fb9de0d3-dd9f-5aff-9a96-ab452a1610b2 | date | Date:
fc56461e-5b2b-4a2b-92c7-0b8442422da2 | checklist | FH-ZU2-QU-ITP009 - Unbound Pavements (FCR & RCC) - Rev 1 | itp | ITP009 - Unbound Pavements (FCR & RCC)
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
9ddd2561-c351-5c44-858a-2e4143344a3b | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000825
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
f1bd1704-9d65-5504-9073-a58e0fb450e7 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000893
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
282695af-0cd0-5fe3-8b64-3dcbc3207e5e | checkpoint | 1.7 - Testing Determinations
435afed8-b133-50ef-9159-3038e4e9ce4f | note | Frequency - Prior to works
36ad8297-35ac-522d-abb9-b2825c174034 | note | Acceptance Criteria - 1. Basecourse and Sub-Basecourse thickness test points selected randomly.
23450c8f-eb32-5958-a1f6-4c1070f0aa49 | note | 2. Field dry density test locations selected in accordance with AS1289.1.4.1.
b46d1e09-9f04-5e91-94c9-e815bb795a73 | note | Reference Documents - Cl 4.21.1
523cd7eb-bebb-5653-b8f3-ced01627075f | note | Inspection/Test Method - Verify
a6984f74-007e-5d32-81f4-43d2d0ae7149 | note | Record of conformity - This ITP signed
9d271944-3ad5-5014-8b38-573d1b5c08db | note | HP
c4dc7eef-31c3-51c3-8336-cd5de23a3ab5 | note | Responsibility - Project/Site Engineer, Principles Rep
4e0c42ad-439e-5855-9604-6d597d69fa7b | date | Date Completed:
466d62da-b64c-5642-9815-ed935f373305 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000890
83a1d299-f349-508e-bab0-117c246c15aa | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | note | Principal’s Representative - Aconex Ref: FHPL- TRANSMIT- 001750
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
844a0099-8d6f-5795-a9d0-14824a95b1d6 | checklist | FH-ZU2-QU-ITP010 - Cement Treated Base - Rev 1 | itp | ITP010 - Cement Treated Base
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
8aa88d4b-ee91-5ba0-8457-6ddccc0d3aa5 | note | Frequency - Prior to works
f596a299-9f58-53ca-9c69-525ee7c3cc5c | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
e63a70e3-79b5-5073-95c3-410eeed9d6ef | note | Reference Documents - Aconex
66c5096d-0ffa-51b0-b947-f747cf16c41e | note | Inspection/Test Method - Visual inspection
5576b08f-da41-5fb2-928c-3099cdaa6f44 | note | Record of conformity - This signed ITP
bd555431-cb25-5b36-b645-bdbb62cd6733 | note | HP*
3b038d3a-33f6-557b-82bd-e7cd92c4d207 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
2f246865-c5bc-5edc-9639-3718d72b4815 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b0b243f7-51c3-55b3-a663-0dc1b1e0b83a | note | Frequency - Prior to works
f696c199-a47f-5990-bd66-7861ff848da2 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
94fa6461-840a-5ed1-8c42-e091c2be9c8f | note | Reference Documents - PSP, EMP, TMP, SWMS & WP
77b7ee44-7821-5616-bd18-d2ce2cac25ba | note | Inspection/Test Method - Visual inspection
63a96ffb-32b4-5e4b-8a97-562a0fa2a122 | note | Record of conformity - This signed ITP
af9cf847-45a8-50a3-a06c-f3aa247d5f84 | note | HP*
1bb9c244-d14a-5e0b-ad9d-5e50f2486391 | note | Responsibility - Project/Site Engineer
20fe73d9-f13f-5d4b-9540-7726d2227e41 | date | Date Completed:
b9437d57-cad2-5d07-86bd-bc4cd9694fa4 | section | 2.0 - Cement Treated Base Documentation & Trial
f713fe9a-9690-5e10-a912-023f37ca0459 | checkpoint | 2.1 - Submission of Mix Design
f84701ba-8df7-56a7-bbf7-fd0108956189 | note | Frequency - 21 days prior to works
4c9630b9-e2f4-5db5-896f-1a0e63df22cf | note | Acceptance Criteria - CTB material and test results to be submitted to the Principal’s Representative for review to ensure that specifications are met and are compliant, prior to the initial placement of the material.
e094d516-039e-569f-9119-c1c7926abfa5 | note | Mix design results will include:
6e374311-1c48-581e-bddc-512318494010 | note | ○ Cement sample should include a CTB material within +/-0.5% of the specified cement content.
7554aa82-ddbf-5f1b-bdd1-acb07d6ad61f | note | ○ Aggregates comply with either Section 4.4 or VicRoads Class 2 or 3 material.
74caf24d-bc49-56b5-a014-a303fa78a0dc | note | ○ Cement shall be Portland Cement Type GP or Type GB complying with AS 3972.
4bd42f13-d34e-5934-acc8-df754cb1cd35 | note | ○ 3% minimum Portland cement content by weight of the dry un-stabilised material.
0998a3e8-f98a-5b9a-be32-e00b897df493 | note | ○ Mean seven-day unconfined compressive strength of CTB to be a minimum of 5MPa and a maximum of 15MPa. No single samples are to be below 5MPa.
42cad487-7e07-5ecf-9580-c34b1c0004d7 | note | ○ Water to be pot
1b7669d0-aaac-57b0-96ea-a1fcdf6df9ca | note | Reference Documents - Spec cl. 5.4, Spec cl. 5.5 AS 3972 VicRoads Class 2, VicRoads Class 3
873572a1-d8cc-565f-94c0-b94eb417573b | note | Inspection/Test Method - Verify
a66909ef-0334-52a2-bb86-0d40152f53e9 | note | Record of conformity - Approved Mix Design Report
2a6c4f49-8b5a-554f-8666-bcb24bd3eb89 | note | HP
5f8594b4-a8be-5f85-bfc9-24cd96c89d3a | note | Responsibility - Project/Site Engineer, Principal’s Representative
6f53238e-be9b-5995-8685-fd629656dbea | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
66263921-7ec1-5447-8330-44ed2cae7d71 | date | Date Completed:
5b68e915-fa91-5491-8e7f-3cf5fa1c57e8 | signoff | AUTHORITY HOLDPOINT
b08682c6-b8e3-5977-9b10-3b486b29efa1 | checkpoint | 2.2 - Supply of Information on Materials Source
72c22c59-df34-5e6a-8aae-a691c8b99d03 | note | Frequency - Prior to works
f06bcd80-cb39-5f6c-b7ee-acc980e2837c | note | Acceptance Criteria - Principle Contractor to supply the Principal’s Representative with supply information regarding the source of the CTB material via Aconex.
8162544f-1551-5f20-8f89-31e412124556 | note | ○ Material information will include the material brand, material type, material supply source, and a supporting test certificate from a laboratory registered by NATA to prove material suitability for the Works.
0fa3973c-f303-515a-83ef-710cdaa6e7b0 | note | Reference Documents - Spec cl. 5.21.1, Spec cl. 5.21.1.1 AS3972
f426f090-b259-5e95-9fe5-efd9491e0e42 | note | Inspection/Test Method - Verify
f4fd7777-24a4-5e24-8f03-2efc20b3adda | note | Record of conformity - Approved Supply of Information Material Source
2c108637-99ea-5b69-8af2-367b81ad171b | note | HP
77f8cbba-a50c-5b3b-980b-bc14c923226d | note | Responsibility - Project/Site Engineer, Principal’s Representative
737f78ca-d449-5e8e-9300-55c08726cd26 | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
2deff7dd-cb7b-5ccf-9592-103910360dfc | date | Date Completed:
2be119e5-29ff-5f1c-b5de-c6aec4a7e549 | signoff | AUTHORITY HOLDPOINT
a3b266d6-20d2-577d-8bcc-cd0d95185e7c | checkpoint | 2.3 - Production and Construction Trial
2237b766-5dba-5d29-821a-e23e772d006b | note | Frequency - Prior to works
3851ad88-0336-50bc-9701-1a660bba0fbb | note | Acceptance Criteria - Construction Trial for CTB mix to be undertaken by Contractor and reviewed by the Principal’s Representative.
a16ae413-4a25-567f-a41e-e6d4836ce8bd | note | ○ Trial of CTB will be based on the first day of placement. Construction procedure to be reviewed and updated if there are any non-conformances associated with the initial trial.
b2ee570e-0077-5e08-a6d7-b9ab0e54b482 | note | ○ The size of the trial area shall be a minimum of 3.5m wide and 50m in length.
92a07a74-804e-50e3-927c-8e7863345b9a | note | ○ The CTB trial area may form part of the completed works.
9c4ed211-657f-57d9-81c5-2446d3c19ac0 | note | Reference Documents - Spec cl. 132, Spec cl. 5.6
717ed14e-d0fa-59c1-bb81-5da36d688f29 | note | Inspection/Test Method - Verify
2dee421f-a4d7-599a-92f8-3f4f57c30792 | note | Record of conformity - Approved Construction trial report
aae278da-12eb-5ac9-aa6e-efefd64eccb1 | note | HP
22a01488-e3ea-50b4-87f1-af2f3639ea98 | note | Responsibility - Project/Site Engineer, Principal’s Representative
05718d70-ae85-54e4-8dac-399b72b5185c | date | Date Completed:
b511eb0c-9811-5b67-89e8-b06a8ab74610 | signoff | AUTHORITY HOLDPOINT
36dd2170-94f3-5210-af3d-9abe62a51461 | checkpoint | 2.4 - Placement of CTB Methodology
8f31af96-a04d-519f-825d-c89d24070a0f | note | Frequency - Prior to works
22af0bf6-e6a7-533b-8b84-023de9149711 | note | Acceptance Criteria - Prior to placement of CTB the Principles Representative shall review this Work Method Statement for proposed methods of placement, compaction and curing
668d3fd8-fac2-52af-8caf-cb2488203135 | note | Reference Documents - Spec cl 5.9
9de3b2f3-7747-5f3c-baa3-785a2747e99a | note | Inspection/Test Method - Verify
c9bf8592-c08d-5316-bb18-160a3df6be87 | note | Record of conformity - Aconex Sign off
86c48c51-5b11-53ec-8c30-3f290786b3b5 | note | HP
da4ae08c-fac7-5e47-93e1-6f347419f540 | note | Responsibility - Project/Site Engineer, Principal’s Representative
7786b41c-8d21-537b-9856-adcc3eb88695 | note | Principles Rep - Aconex: BecaCPL-GCOR-000810
58f6c910-c461-5b65-a59d-decf015fc5c0 | date | Date Completed:
d887b5c3-5f02-5d22-ace4-5123e7694541 | signoff | AUTHORITY HOLDPOINT
ce085ba5-14a6-5251-aa31-3e4c7b381a10 | checkpoint | 2.5 - Provision of Material Samples
f34ea86e-e126-502d-b7d8-799a4d4501b1 | note | Frequency - At Least 5 Days Prior to works
dd7bb70d-a2b5-55c9-94b4-8dfc76fad08d | note | Acceptance Criteria - Principal Contractor to physically handover reference samples to Principal’s Representative of the approved CTB material. To be truly representative, the reference samples will be taken straight from the supplier of the material.
0c874d56-cf4b-5428-a181-0fb5c3e72280 | note | ○ The reference samples shall be divided into two representative portions, with one being held by the Contractor and the second portion by the principal until completion of the Works.
a7eaa790-89eb-560b-bb6a-42b034b9f4b6 | note | Reference Documents - Spec cl. 5.21.1.2
4123a350-addc-57f1-bedd-545a3336c7ad | note | Inspection/Test Method - Verify
e3479ff3-9d0e-5684-8e1e-0bf3b53ff2f0 | note | Record of conformity - Handover of Reference Samples and Aconex sign off
da9049f6-a774-5ab7-b2b1-03431ba9fadc | note | HP
92c0e4db-5ee2-5bbb-a183-8fea440ae72a | note | Responsibility - Project/Site Engineer, Principal’s Representative
ba3782a7-3abb-5d95-b86c-c78ef690149a | date | Date Completed:
dfd5e478-bd8f-595e-9f3f-8d4fc3db5035 | note | Principles Rep - Aconex: BecaCPL- GCOR- 000825
ce0e26d2-cdbc-5212-b7b6-711abae7313d | signoff | AUTHORITY HOLDPOINT
3a93befc-813a-54fa-93e6-ed544f594f7e | section | 3.0 - Placement of Cement Treated Base
e6432367-fc0d-5d29-92fc-3e7e2637f723 | checkpoint | 3.1 - Subgrade, Basecourse Preparation
1d26deef-fe2e-5fdb-a424-a3909955245a | note | Frequency - Each lot
90173b31-4a14-50e9-93e3-3fed40bb5797 | note | Acceptance Criteria - Existing surface of subbase is maintained in compliance with tolerances on surface smoothness and level. The subbase is clean and clear of any foreign matter before the placing of the CTB.
c310d359-b226-5439-8830-9bf651637b3d | note | ○ Principal’s Representative will be notified 24 hours prior to the placement of CTB to allow the subbase to be inspected prior to the placement of the CTB. This will be recorded in ITP009 – Unbound Pavements.
65fd1623-8231-5854-aa9f-5cda3e8b9715 | note | ○ Principles Representative to be notified of the intention to place CTB.
b1ae7aca-a8e4-5915-b171-70d23878625f | note | Reference Documents - Spec cl. 5.7, Spec cl 5.9
35910732-4634-5050-a1f3-a7e82e567390 | note | Inspection/Test Method - Visual Inspection
a9a3fb03-d34e-5643-aeab-c7f7c06b097d | note | Record of conformity - This signed ITP
0061e970-f3a6-5f64-861d-4a3562876699 | note | HP*
b5dc517c-d7f8-5f6b-b8b0-6a317bdab769 | note | Responsibility - Foreman, Site Engineer, Principal’s Representative
de55df49-5ade-5de7-908d-27572a37eefb | date | Date Completed:
d5f5265f-9acd-5150-85f4-b8e0fd5c4c1b | checkpoint | 3.2 - Layer Placement Parameters
15d20a59-abb9-5a63-bbbb-ae10c247e7e7 | note | Frequency - Every Lot
a7549654-01da-5468-98c6-45fd6149d6b2 | note | Acceptance Criteria - Summary of Parameters for each Lot;
9b307856-48e1-5148-b00c-36535f9c5285 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
443263a8-e71e-5b88-afb4-8b92e59bb419 | note | ○ Max Layer is 200mm
bed1a5bc-d098-5239-b2e4-030a8525d7c3 | note | ○ Min Layer is 100mm
187f4fc7-665d-5338-8487-8e92b1d07d02 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
7171547a-ee6b-53d6-b20f-7d3ad0a0d8c9 | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
01ea9862-06c3-54c0-8365-67d7ef6c4f5d | note | ○ Material is batched within 1% of OMC
154ea760-0093-5671-9a15-c4fb065e211a | note | Reference Documents - Spec Clause 5.9
23e30d10-91f9-5caf-bf9a-50c0b7a25197 | note | Inspection/Test Method - Visual Inspection
e3db2985-1629-55b1-86de-615aa90f8bca | note | Record of conformity - This signed ITP
92da49e6-752c-58e5-a3a5-368767d9eadc | note | IP
131f5628-0346-5a4c-830c-ee5d14e15223 | note | Responsibility - Foreman, Site Engineer, Principal’s
cc2418e7-c804-5128-ace2-e40bde4c6554 | date | Date Completed:
a791ad98-de04-56f3-baea-854bfe3fec6e | checkpoint | 3.3 - CTB Placement – Weather
a8945776-a6f4-5b36-b3fe-925c329ce3df | note | Frequency - Each lot
527d722b-c5b1-574b-81b0-1a2b37349e23 | note | Acceptance Criteria - Weather to be check prior to placement, CTB shall not proceed when;
8b6f23cb-bdd6-52db-9b80-19f7c3a85136 | note | ○ Ambient temperature is below 5°C
b5a25fd6-d1a7-555c-a444-784f86bdf94d | note | ○ Temperature is over 35°C
abb0ce29-4364-5f04-86af-c2c1030115d2 | note | ○ Heavy Rain fall is forecasted
e8bd97b5-51ed-58e4-b56f-93694ea86fc5 | note | Reference Documents - Spec cl 5.18
17631fb5-c95b-50f9-96d9-c8cb7cd5a4ae | note | Inspection/Test Method - Visual Inspection
d44b3070-6831-5703-af8f-496e3889538e | note | Record of conformity - This signed ITP
77032644-9c84-5d86-8fa0-8438ebe70d20 | note | HP*
19904e0d-6cd6-551f-af45-e992a7ccbd14 | note | Responsibility - Foreman, Project/Site Engineer
ccba4635-1cdd-5b1f-84fb-6f07cec24b9c | date | Date Completed:
a990dc3f-4e0f-51d5-8138-9ebb78589eff | checkpoint | 3.4 - CTB Placement – Checks
1bb2aa2a-c4ff-561d-a13d-7afbe13bc904 | note | Frequency - Each lot
32f8ef17-8490-50c9-9251-810682a3751a | note | Acceptance Criteria - During CTB placement Activities check;
40f02693-c8d1-535f-a199-ece05f6f73b8 | note | ○ Placement starts on the high side or crown of the layer where practical
048bd7c5-c004-55da-9bc4-93e115f79601 | note | ○ Material is spread in the direction of Taxiway across full width
4f433ccd-ee6c-524f-b818-eae38e7377da | note | ○ Underlying layer is not disturbed during deliveries
d08de34c-ea7f-583a-b415-47e596003fb9 | note | ○ Inspect Material for any contamination through placement activities
a61ff818-105d-5a4e-8680-ff9d042ce44a | note | ○ Adjoining layers are a clean face / vertical
8df5403a-2649-51c2-a3ad-c7303e4bb19d | note | ○ Segregation does not occur
b355b70a-b0ac-5a92-b3ac-1b8a400fe4a1 | note | ○ Placement to be completed within 120 minutes from time of batching and before concrete has obtained its initial set
f4942690-8cd5-558c-9f3a-44274fe159c5 | note | Reference Documents - Spec cl. 5.9 AS1289.5.2.1
b574633f-2bb1-5d4e-950e-ff2484b56389 | note | Inspection/Test Method - Visual Inspection
60226c75-b0de-5c5b-96e9-8673327b422c | note | Record of conformity - This signed ITP
b828ff37-ec7f-50be-94b1-ee32fc7cc07b | note | IP
d1b766ef-1c08-5b21-b039-7f9ab4683bf1 | note | Responsibility - Site Engineer, Foreman
2654885b-329c-5964-89f4-e465307a4a9b | date | Date Completed:
7401f6c4-9bed-5d6f-b4ec-db03b8a866c1 | checkpoint | 3.5 - CTB Compaction – Checks
d318849b-5618-597c-91b3-814e52d4f0e1 | note | Frequency - Each Lot
ae30e580-e65b-59b1-93b6-ceb7450cd2f2 | note | Acceptance Criteria - During Compaction check;
b10036b6-d4c3-53e6-a7dd-623f106280d5 | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
d1f1c126-533a-5e6a-8dc4-2e235688e671 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
05876ce7-e80b-5055-948b-92633bd9b857 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
8a9f03d1-75fb-512e-bbdb-7318c1488415 | note | ○ Watercart present onsite for conditioning
65490f31-31f1-55fa-ba27-62cb0064acd3 | note | ○ Materials are trimmed to required shape and level
18e147eb-3edb-5867-bda3-b7734942fa05 | note | Reference Documents - Cl 4.10
a5cc52f2-9ea2-51e1-9d76-86f779782816 | note | Inspection/Test Method - Verify
4ed1fdbe-a813-5556-8b34-fa80b91e4a55 | note | Record of conformity - This ITP signed
d2cb62fd-45c5-53ba-a041-c81c964b747c | note | IP
8ca58966-39f3-51c1-9bf7-7cfb7924a9f8 | note | Responsibility - Project/Site Engineer
7d2e2bd3-99ca-5153-891e-45c4cf8e6ee3 | date | Date Completed:
2bddfd15-ae28-5cbe-bfb1-25a7421f7b98 | checkpoint | 3.6 - Curing & Protection
d9202bed-4ccb-5e6c-8eae-441e32bd0d2a | note | Frequency - Each Lot
3d18e78a-fbc1-525b-822e-0dad77056df3 | note | Acceptance Criteria - Curing to commence as soon as CTB has been placed, compacted and trimmed. No plant (other than curing) to track across CTB for minimum 24 hours.
3ff88ce5-7c4d-55c3-8a20-b2077108bb2f | note | Curing to follow one of the below methods;
426e9ca7-487a-5f20-a6ae-ffdc3fd8f5d4 | note | 1. Wet Method: This will involve a watercart lightly spraying the CTB surface for minimum 7 days.
ac0408e5-01eb-511d-bec8-72574746a26a | note | 2. Debonding Coat: The CTB will be covered with a bitumen curing compound. In locations of PCC, will be the C170 seal with 7mm aggregate.
dcc282aa-d774-5d32-a21a-2340833e3a7f | note | Reference Documents - Spec cl. 5.15
c185cb39-41db-5b74-bf4b-58039a1d2486 | note | Inspection/Test Method - Verify
5ed27476-046b-5d4c-91f4-9d6dc280e91b | note | Record of conformity - This ITP signed
4127c5e4-b820-5275-befd-3ba282773570 | note | HP*
90a1f255-e2f6-5258-82f4-a6608d585ead | note | Responsibility - Foreman, Project Engineer, Site Engineer
b29214e6-d20d-57e7-b892-48164a53e9e0 | date | Date Completed:
6e009c69-70d7-514c-b44e-f3bb3867a1e3 | checkpoint | 3.7 - Post Placement CTB Inspection
c133101a-b607-579c-b4f9-2cf71ca93f9b | note | Frequency - Every Lot
a7f09b74-8c7e-5e9c-8c19-390ba5710f6c | note | Acceptance Criteria - Prior to the application of the succeeding layer or installation of the de-bonding coat, CTB final surface is to be inspected with the Principle Representative
3dd631f2-a2a1-571d-a620-d5d946c8b5bb | note | Reference Documents - Spec cl. 5.9
84554310-d991-5d29-82f6-a3c07c5d5599 | note | Inspection/Test Method - Verify
09e8586b-eca6-5d3a-a226-2bcb388209a4 | note | Record of conformity - ITP signed
5ccaaf5a-f383-5dcb-9802-a10733a58443 | note | HP
905e8200-14cf-53ec-a676-f2ddc9f34212 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d7a8daed-5a8c-5363-9fc5-cd375d53fabb | date | Date Completed:
1fbbaaa5-dcbd-58a7-a340-05841913c755 | signoff | AUTHORITY HOLDPOINT
131e830c-80ee-5bfa-ae6d-3cee6331c53a | section | 4.0 - Acceptance, Compliance, Controls and Quality Assurance
99e681f2-8a6c-56a0-be58-12603b6f7477 | checkpoint | 4.1 - Field Dry Density
f03186bd-59c9-5281-b6ef-20321711d5ed | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
102f1ebf-e51b-5ed9-ad43-a0896478ebdd | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
f5ceefec-34de-5727-916e-0b288c1aabd4 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
803c9230-1f43-5b08-9bac-c416ef40d10d | note | Acceptance Criteria - Average of Specified Minimum Dry Density Ratio (SMDDR) of 97% of the Maximum Modified Dry Density
0f72bb26-c4ac-5f47-9353-d47361c2c94d | note | – Average Equals or Exceeds 96% with no individual result be less than 93%. The lot will be accepted.
54e288c2-afc9-5831-bdd3-c814dbafdac1 | note | – Average Equals or exceeds 96% with a result being less than 93% - an additional 4 tests will be taken
7422857c-dbf4-5cde-8fcd-7a9eebb01ddf | note | – Average is less than 94%, the lot will be rejected
58937cc4-12d9-5cda-a665-45ab2a8da7e5 | note | – Average is in between 94% and 96% - an additional 4 tests will be taken
a9f58864-2561-54a2-bfa0-dab77c1e7259 | note | Reference Documents - Spec cl. 5.10, Spec cl 5.21.2.5
28029483-eb30-5e34-b3a9-ed80ee976a2f | note | Inspection/Test Method - Verify
71a6959e-311c-5755-aa07-77880c544a37 | note | Record of conformity - This ITP signed, Test Report Attached
16a6d560-db93-5e93-aac4-1ef0e3b58824 | note | TP
4d63e4ce-61af-549e-93cd-88e90439f6fe | note | Responsibility - Foreman, Project Engineer, Site Engineer
d729f33b-569d-5d94-bf25-bde0399b776e | date | Date Completed:
c083058b-dae6-5e3d-a513-cc68f715ae5a | checkpoint | 4.2 - Moisture Tests
48e1392d-43e6-58f5-af5e-7dedfde8269c | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
06c7fffd-057a-5683-a5f7-8a8c381a276e | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
2b0ffe7c-a0d8-59f6-bebc-62ca95b1f694 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
ebec3e40-e3e6-5a4b-9711-f0369aaf6a53 | note | Acceptance Criteria - Target Moisture content of +/-1% for information only. Production of CTB to be within 1% of OMC.
b5ab453a-a9ac-5e01-bf8f-b88b1b412688 | note | Reference Documents - Spec cl 5.21.2.5
31eba2f8-121a-5f0a-9bbd-1df0d0fcd5d6 | note | Inspection/Test Method - Verify
1d86b1f4-11bd-5c0c-9580-e4d32aaf98f6 | note | Record of conformity - This ITP signed, Test Report Attached
6a896df5-fbe0-5c11-9572-3ea136c6b665 | note | TP
dd17bd53-ffd2-53b4-ac3a-23be9eb1f240 | note | Responsibility - Foreman, Project Engineer, Site Engineer
da840038-f33d-5214-8629-cc69fb864320 | date | Date Completed:
435a97a0-8348-5acf-b9b1-f34f54f87f6c | checkpoint | 4.3 - Strength Testing
27bc8c7e-95d1-5dcf-88ae-82823e1085d9 | note | Frequency - Each Lot, divided into four approx. equal sub-lots
2fddab20-aeb3-51af-80f7-3033426b797b | note | Acceptance Criteria - A total of 4 sub-lots will be taken as samples, with 2 being used for the 7-day strength testing, and the remaining being used for the 28-day strength testing. 28 day results are for information only.
53e841bf-eed4-57b9-9fbd-fd88b73d2b2a | note | ○ The mean 7-day unconfined compressive strength of the CTB shall be a minimum of 5.0MPa and a maximum of 15.0MPa. No single sample shall be below 5.0 MPa.
2750053b-5e5b-527a-927e-8e87f4aab69a | note | Reference Documents - Spec cl 5.11, Spec cl. 5.21.2.6, AS1012.9, AS5101.4
520a4d5f-8343-5414-af26-941844343fab | note | Inspection/Test Method - Testing
51ba2912-8e23-5929-9c94-7c2fc5b9173a | note | Record of conformity - This ITP signed, Test results
102a9d58-c7cf-58d9-a254-e2b57c059a11 | note | TP
62c9a368-385e-5f8a-a5fd-3173b78cbeb5 | note | Responsibility - Project/Site Engineer
cd63fc81-2748-5204-8c71-1ecdc8d7094d | date | Date Completed:
a63f0532-32bb-5725-9bef-0a20b43e1e13 | checkpoint | 4.4 - Process Control
c610b4ae-a285-5c6e-8fcd-207cb4c478c1 | note | Frequency - Each Lot
139d6cc6-0860-5d37-84ea-5eec2d18cc61 | note | Acceptance Criteria - CTB production and process control test results to be supplied to the Principles Representative
4cf57679-b162-55ad-abc5-71060624730a | note | Reference Documents - Spec cl. 5.21.2.1
a2362452-e6b9-50cc-8ab0-15193aa438e1 | note | Inspection/Test Method - Verify
6b11e16c-b89c-532c-8d84-0dde9b1f6e07 | note | Record of conformity - This ITP signed
f14b3625-4f6b-54d3-86cd-83ac17befadb | note | IP
cbabd8ff-86fb-5ea7-adaf-3d9bcd3a5cc2 | note | Responsibility - Project/Site Engineer
81b3934b-4a7c-5973-9a83-ac3ddb5484e9 | date | Date Completed:
2bcbf63d-6c13-5d63-acf0-f62700f979cb | checkpoint | 4.5 - CTB Layer Thickness
1799115e-1fc2-519a-85de-f01907f95ab3 | note | Frequency - Once Every 30m2
fb01f919-1253-50b5-bafd-444151f02c79 | note | Acceptance Criteria - CTB layer thickness to be measured, recorded, and included in the Quality Assurance records. No CTB layer thickness to be less than that shown on the drawings other than allowable construction tolerances
86aed6fe-a7e1-5bbe-b54d-a6febb6dcee1 | note | Reference Documents - Spec cl. 5.21.5, Spec cl. 5.21.7
1751b0ea-39bf-557f-a987-76db1c978ff5 | note | Inspection/Test Method - Testing & verify
8f655c65-eeac-573b-a41b-ff7a4763d512 | note | Record of conformity - Test results & this ITP signed
1edaa5b4-7fe2-53f7-904d-ef6ccb84713b | note | IP, SCP
440d35fd-e0b5-5913-b784-e8a1609522a6 | note | Responsibility - Project/Site Engineer, Site Engineer
8486d6a6-edbe-5b6f-ad1b-e3320c99b948 | date | Date Completed:
a65f8491-197d-5f8d-98e9-df0607f9802b | checkpoint | 4.6 - Quality Assurance Records
e28ad406-42b3-54df-bd45-1d533d8a6992 | note | Frequency - Each Lot
6bff1fb8-fc6a-5245-be5d-b0d34882f2da | note | Acceptance Criteria - Provision of ITP test reports must be submitted within 60 days after the completion of the Works. Principal contractor to supply electronic copy of reports detailing the results of the quality control and testing undertaken.
ff73a1e8-da4b-56d3-b9ad-dd3e0a5b5867 | note | ○ Reports to be transmitted on Aconex and Aconex Reference to be quoted as Hold Point Sign off.
901e3f69-22d4-5dff-a8fb-4777b97224e0 | note | Reference Documents - Spec cl. 5.21.3
dbe748d1-13fc-59a6-b11a-3fde2f3eafe5 | note | Inspection/Test Method - Submission of ITP reports
d186873f-c9c4-57e7-a8a6-10ef7c2b1f91 | note | Record of conformity - This signed ITP
ddbf53ba-4ba6-5162-a876-1db4a0b8cda0 | note | HP
6a8940a0-674a-51b8-a949-c153ebc3521f | note | Responsibility - Project/Site Engineer, Principal’s Representative
a6b55153-f7f0-5005-ad8c-0083e0fd459c | date | Date Completed:
d26e1c20-cd8c-5956-8617-743c63ff978f | note | Principles Rep - Aconex Ref: FHPL- TRANSMIT- 001750
ad2de4d9-5721-5145-9475-1d1edaefaba1 | signoff | AUTHORITY HOLDPOINT
39c190b7-b116-57f8-a2a7-da1cc234c6f0 | checkpoint | 4.7 - Survey As-Built Report
2275ba0b-0e87-5dba-a66e-9441454b85ae | note | Frequency - Each Lot
dbb59df4-c843-56b6-8c73-5f8a99b22177 | note | Acceptance Criteria - The surface level at the top of the final CTB layer shall not deviate from design level at the specified points by -10mm or +0mm. Contractor to provide Survey Conformance report of completed CTB surface layers per Lot.
61d1d193-4712-5f16-853e-4cf7e99a2d55 | note | Reference Documents - Spec cl. 5.17, Spec cl. 3.14.2
c5212fbd-57c5-5049-9e22-15468fa5c769 | note | Inspection/Test Method - Verify
b30b9298-b275-527f-83c5-0965084bdb9c | note | Record of conformity - Completed drawings, survey report, & this ITP signed
a9cbc0bd-f47a-5f26-81e9-5f5cb769aaf6 | note | IP, SCP
3d2bd58c-980e-593c-8704-511a08c99272 | note | Responsibility - Surveyor, Project Engineer
c5056a76-945c-5f08-b874-d76e1d320dbe | date | Date Completed:
0f7f576e-520a-5643-9fc4-f169fffc004d | checkpoint | 4.8 - Surface Smoothness
5d4acac4-2875-5596-93f5-1a785ba3e054 | note | Frequency - Every Lot
93786c44-4ebd-54d3-aca1-951acc07afb5 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
91fb8cd2-d46e-5227-b807-708f1a461489 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
c01c18c5-37ba-58b4-a6a2-642d82ab94c0 | note | Reference Documents - Cl 5.17
58c12aac-2d98-5ac4-b686-7c9e9cfaa8e0 | note | Inspection/Test Method - Verify
ed18d16e-eb2c-55be-9c34-5b2c4fd34347 | note | Record of conformity - Report
3b7bb992-09a4-5bdd-9c10-fcc45ede27d4 | note | TP
f9ae33fc-2416-5f39-a778-8195e2fb3791 | note | Responsibility - Project/Site Engineer
effa941f-c08e-5def-b3a5-5ecdab676233 | date | Date Completed:
c801c62f-58a1-5837-8f7c-89512b249fce | checkpoint | 4.9 - Correction of Nonconforming Work
9ec784eb-353e-506d-9619-b27d85a09297 | note | Frequency - Each Lot (if required)
369bd2a4-9673-5e6f-b9a7-c89bb20602c2 | note | Acceptance Criteria - All CTB that do not meet all the specified requirements will be rejected by Contract Administrator. Materials to be removed full depth of the layer and reinstated, unless otherwise approved through the NCR process.
ac35cc23-2d07-57ea-aa08-9d3098856e40 | note | Reference Documents - Spec cl. 5.21.4
99ba277c-f48e-501e-89c3-e4675b0c7544 | note | Inspection/Test Method - Verify
55f90695-7572-5a0e-8395-fe465a26db9f | note | Record of conformity - This Signed ITP
db96ea5a-921e-5ed5-8c15-2a19c2d9a5bd | note | HP
6a3f2218-7f09-5a57-b7a7-c49b0d52d177 | note | Responsibility - Project/Site Engineer, Principal’s Representative
dba5f565-ca20-52ba-aca1-c9ea7c152251 | note | Principles Rep - (if required)
e18f55d4-6a0b-5027-bffa-6021233c4d87 | date | Date Completed:
a1f73c0c-47cf-52f8-abb9-28b1f1690f2e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
f9a7189c-b860-50c9-ac40-38214720411f | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
2ed5916a-4453-538c-a5f9-3dc1b4870a03 | textbox | Print Name:
3b7bd65a-2e57-5fdf-babf-8993d668d7c2 | textbox | Position:
90d84dfb-f506-5b4b-b2a3-b1f9ce2894e4 | date | Work Completed On:
bbf80422-452e-53b5-8e68-f944166304fe | date | Date:
34dab725-d24e-5abc-bb57-788fb4f92dc1 | checklist | FH-ZU2-QU-ITP011 - Concrete Production - Rev 0 | itp | ITP011 - Concrete Production
d1d7c36c-2cf6-5a58-97fc-e2b1a4a2ed68 | section | 1 - Plant
bb149d3d-8aaf-5a14-bfd7-edfc4cdccea4 | checkpoint | 1.1 - AS1379 4.2.1
ec167bae-073e-5196-ab41-92473e890fab | note | Inspection Description - Batch tolerances
d0878c4c-a23d-5965-97d4-579044b8b2ec | note | Acceptance Criteria - AS1379 Table 4.1
5ed08f6d-628d-5eb0-b0dd-4434f6270e6b | note | Frequency - Each Batch
52121fff-1c4b-5854-991b-b198f71b2ce7 | note | Initiated by - PS
965b0cfd-d216-5c8e-8809-cdc0de6a7f41 | note | Approved by - PS
b962d637-e9aa-5562-b71e-79c077fc3e90 | note | Verification/Witness: HOL - W
a3db39d9-32c1-5a00-a7fb-28d48db0b6fc | note | Verifying Document - Electronic
5b528f62-34e2-58e6-815e-fb5414fc749b | note | Record Location - Batch computer
fd112218-a86d-56fe-8602-0f9007ca5737 | checkpoint | 1.2 - HOL QMS PN6.1
3b609834-fa06-55d4-8cd0-cacfb868e819 | note | Inspection Description - Record Plant Malfunctions
04c07292-181e-5bdb-8111-9ba04a90011e | note | Acceptance Criteria - All plant mulfunctions are to be documented
aea9e1ab-4f16-5471-9ea9-a4277a345348 | note | Frequency - Each Time
4bcdff02-027f-59e7-840c-0bc0962d7292 | note | Initiated by - PS
98280ffd-c0ec-5356-a8a1-de6b660b82ff | note | Approved by - AOM
f1c6d24b-5b40-564c-8bc2-e7806562b04f | note | Verification/Witness: HOL - W
8f124b17-a4c4-5dde-b618-227f1e40b0de | note | Verifying Document - Register
ec962c2b-72a0-5c25-a96b-4a2f098b53c0 | note | Record Location - AOM office
342318df-c5b1-57cc-98d2-56502aa5f8e7 | checkpoint | 1.3 - AS1379.3.3.2
2261224e-cd10-571d-a0ab-59ac2b4ce738 | note | Inspection Description - Weigh Hopper (Cem & Agg)
82ae748d-8021-51a3-b248-8c4a5e3f3eb3 | note | Test/Inspection method - AS1379
e06efce3-0121-5f53-b67c-d923f3c0475b | note | Acceptance Criteria - ± 0.4% of the Max. Scale Value
aa6ab432-ab8c-59e1-bff1-aba5445484e6 | note | Frequency - VicRoads Min. 3 Monthly
399fa8fe-81d5-511d-a735-cea7efe141c1 | note | Initiated by - PS
7ecef803-c0f1-5522-8ebc-e64f9073ccd1 | note | Approved by - AOM
6d6ed851-6c70-51cc-bf36-5f2cc76086c9 | note | Verification/Witness: HOL - W
85870595-d124-5eb1-8088-caf5f6adaefd | note | Verifying Document - Calibration Report
192385be-8cc9-511f-bf2f-ab939170b91a | note | Record Location - Google
8f189730-16dc-562c-8244-e99fc03abffc | checkpoint | 1.4 - AS1379.3.4.2
5b532b14-badf-53ea-aad8-13610672b158 | note | Inspection Description - Water Meters (Plant, Slump Stands & Trucks)
edb974ae-b9d0-55fe-9dc7-1ed8bcd5cec6 | note | Test/Inspection method - TRBE652973
4216efc3-7727-5fc9-bda8-331453c5d15d | note | Acceptance Criteria - ± 2%
45b897df-835c-5acf-9bcd-a87106d50105 | note | Frequency - VicRoads Min. 3 Monthly
cb184bc8-a986-5d31-b1a6-b22904df3ac9 | note | Initiated by - PS
a837287c-f051-5cef-97be-83ee664dc989 | note | Approved by - AOM
c3808748-d2f7-5f44-b833-3fb41b8c94f5 | note | Verification/Witness: HOL - W
ec824824-a32b-52e1-83fc-8c6c044e48aa | note | Verifying Document - Calibration Report
d6a1db43-9664-50d0-ae91-1d1e8c2216a9 | note | Record Location - Google
a2c93459-c8fe-5526-9725-ce55b11e23f9 | checkpoint | 1.5 - AS1379.3.4.2
f7e763de-1cf7-5be6-b977-0b3ec21f707c | note | Inspection Description - Admixtures
7257f113-7b5e-5517-9197-6fa4eabbadf7 | note | Test/Inspection method - BASF TM033
107b6b82-a1b3-5d9e-a90a-4a53e8fb73b1 | note | Acceptance Criteria - ± 5%
74cd3856-d407-58c5-9652-009768bffd21 | note | Frequency - VicRoads Min. 3 Monthly
33a9b1e5-0d1c-5fad-84fc-d1a08459a347 | note | Initiated by - PS
6a65c703-aa0e-59be-99b5-7400c71691aa | note | Approved by - AOM
9344f309-a5b0-5b1c-9480-d95b503bc764 | note | Verification/Witness: HOL - W
bc22657a-b306-5e6f-bf36-a6fd8b56b345 | note | Verifying Document - Calibration Report
056ca247-dce2-51f6-9c77-ec15673b6387 | note | Record Location - Google
b2b49c19-fb17-5e3e-bd41-38bd1fde4a01 | section | 2 - Cementitous materials
60b4bf12-aca3-51d3-b8a9-ab48b3f52f0e | checkpoint | 2.1 - AS1379.2.2
89275da6-0465-5e62-8e36-d04ca4b76f58 | note | Inspection Description - Type GP cement
23282475-8466-5ae3-97a1-6111eefaaa61 | note | Test/Inspection method - AS2350
588d428e-e1f3-543c-928d-cf8a461146df | note | Acceptance Criteria - AS3972 Table 2
942c42a1-c57d-5baf-a541-665ef510490a | note | Frequency - Cement Australia Supplied (as per AS3972 Clause 5.2)
af1a8ef4-fc18-5a0e-b703-de2e2ced3c1e | note | Initiated by - Supplier
da2d45a0-5f7a-5873-8267-ef844bfbb62d | note | Approved by - Tech Mgr
e6844906-2f9c-5bda-b9b2-26180e80a17f | note | Verification/Witness: Supplier - W, R
81c65be7-13f9-5e95-b447-d1c14d5cbad7 | note | Verification/Witness: HOL - W
500a7175-b576-59cc-abef-ff2ec7862a7c | note | Verification/Witness: Company - H
f707f541-a427-54af-8984-141816080ed1 | note | Verifying Document - Supplier test report
1643a055-3b71-5e4c-bfc0-d338cb7b8daf | note | Record Location - Tech Mgr office
e44c08d5-33f4-5f97-912d-d286e23f0854 | signoff | AUTHORITY HOLDPOINT
8f9a460e-8448-59e5-b2df-be1e037dc6b8 | checkpoint | 2.1 - BECA Cl 11.4.7, 11.24.5
7e3f15cc-e9fb-5a65-893a-375ff27a6784 | note | Inspection Description - Reference Sample
b8295b62-42c9-512c-b895-f7e14165375d | note | Acceptance Criteria - -
6247c27b-afe9-5fb0-8e02-5a424feb764b | note | Frequency - Plant Sample : 10kg / 1000 tonnes
d3e6c3a4-b367-51c5-93ae-608aa856ffb3 | note | Initiated by - Supplier
254de3e8-8a66-56e4-bf57-ac7601a18a8e | note | Approved by - Tech Mgr
fe4125e2-18ba-591f-a7d0-ee9716a69681 | note | Verification/Witness: Company - W
bc8a5893-2226-53f5-a6b1-2008a422b372 | note | Verifying Document - Record only
f1323379-b76a-52b3-8e14-25fea0d7d4d4 | note | Record Location - Tech Mgr office
bb025ecb-aea6-52c2-b32d-71450f87a789 | checkpoint | 2.2 - AS1379.2.2
33439117-724e-5950-bc43-2fcfdb604d6e | note | Inspection Description - Flyash
29bad1a1-3892-5f1d-9dd4-1272b961bdb5 | note | Test/Inspection method - AS3583
38e649b9-cf2d-51e2-95e2-fc590323a903 | note | Acceptance Criteria - AS/NZS3582.1 Table 1 - Grade 1
66331346-9de3-57b4-a751-8826155f5c58 | note | Frequency - Cement Australia Supplied (as per AS/NZS3582.1 Table 2)
0450bcf7-b261-5937-805b-686e17ffd645 | note | Initiated by - Supplier
e2ef16de-5fcf-5d9f-a3c7-4952b23bd1af | note | Approved by - Tech Mgr
65e036aa-fd80-5942-aab9-359a60786982 | note | Verification/Witness: Supplier - W, R
e2b3da04-acf3-500d-946f-d78e125a0670 | note | Verification/Witness: HOL - W
931cdb5e-47fc-5dc9-b82b-a0e970a68758 | note | Verification/Witness: Company - H
ff7bad1c-7fc0-55db-aace-c8e9fd136e86 | note | Verifying Document - Supplier test report
4219d34d-10f4-547d-a930-d564fa09a2ff | note | Record Location - Tech Mgr office
ed4e4f7c-28b8-57c8-b86f-66b1ce71146e | signoff | AUTHORITY HOLDPOINT
f1c81b6f-1209-55f3-a019-1e541e392a1f | checkpoint | 2.3 - AS1379.2.2
2ad2fa49-64a7-5261-8406-0e7c0529f8a7 | note | Inspection Description - Slag
947265eb-f55f-51c6-841c-514b73d001d6 | note | Test/Inspection method - AS3583
cfde5cd4-276f-5832-8548-f26348b73ca7 | note | Acceptance Criteria - AS3582.2 Table 1
e6847eac-f3fb-509c-8cc7-47a06fcda99e | note | Frequency - Cement Australia Supplied (as per AS3582.2 Table 2)
8b0adaca-df8b-5ed1-8abd-196615ee0253 | note | Initiated by - Supplier
d559e9ec-beac-5801-a9b6-41fdcac89f0e | note | Approved by - Tech Mgr
e47aa184-ce01-5c0a-bf64-8f5d9a6cd291 | note | Verification/Witness: Supplier - W, R
90c23712-674d-5a2c-be11-736bb7e41d01 | note | Verification/Witness: HOL - W
306c3c62-b3b0-5288-ba56-c8a29b6ae623 | note | Verification/Witness: Company - H
b6673083-e377-5b92-b7a2-34cdd6198fbe | note | Verifying Document - Supplier test report
cb2b4f39-2550-5973-b9b3-538f2b4670f7 | note | Record Location - Tech Mgr office
2090be1b-7fd9-5116-9b30-36decf7a68c8 | signoff | AUTHORITY HOLDPOINT
d96a8d82-973e-5a54-9fd9-6912feb16437 | section | 3 - Coarse Aggregate
0b71bfd6-f444-5ed2-9c2a-0f5ea47e3f4c | checkpoint | 3.1 - AS1379.2.3
1a8c117b-a752-5916-a5ce-b426f631942e | note | Inspection Description - Particle Size Distribution
2badb670-17ef-56b3-8338-5da843f9ad33 | note | Test/Inspection method - AS1141.11.1
6004f56a-7e7e-5568-9d4d-0fda6d9e5ea5 | note | Acceptance Criteria - AS1379.2.3
7e15badb-46b7-56c6-bfab-8778656a6726 | note | Frequency - 1/1000 tonnes
9e041410-b66c-512b-92c6-8d27e7411f06 | note | Initiated by - Supplier
eba55a77-0ab0-5436-82b1-00becd49158e | note | Approved by - Tech Mgr
bff9d7fe-05e0-52e1-a259-b4809bd5fb13 | note | Verification/Witness: Supplier - W, R
e017140e-90d9-565f-8492-9cf259be669f | note | Verification/Witness: HOL - W
b2484355-173d-5e84-bdda-ae87b4eda37e | note | Verifying Document - Supplier test report
8e9c8ee7-3404-5901-9c28-ed084c30ba93 | note | Record Location - Tech Mgr office
bf87235f-4852-55dd-ac36-e73b389d5f0d | checkpoint | 3.2 - AS1379.2.3
90a89ed1-074b-54da-ab43-9d31e898ef46 | note | Inspection Description - Flakiness Index
59996869-f8ca-55c7-afb3-73c55d972e17 | note | Test/Inspection method - AS1141.15
0cdc2a4a-072e-568b-b20d-6f6a70218d86 | note | Acceptance Criteria - AS1379.2.3
ed276801-9212-5213-82f0-c1aea7cf3664 | note | Frequency - 1 per month
6f42b9d2-01e2-50d7-a771-869c4f68d883 | note | Initiated by - Supplier
99df91ef-1b47-5dff-b241-e63b7f464041 | note | Approved by - Tech Mgr
fabd7f73-e5a9-5470-8fc2-5e12121fcc07 | note | Verification/Witness: Supplier - W, R
cf8188bd-ffa9-5ec8-b024-ced7c8850502 | note | Verification/Witness: HOL - W
6071c129-e1dc-5bf1-b8ec-a741604e226c | note | Verifying Document - Supplier test report
7649344e-9b58-569d-80a2-c53e7c5994d3 | note | Record Location - Tech Mgr office
75293781-92f8-597a-a5f2-9a7d61ce4029 | checkpoint | 3.3 - AS1379.2.3
d77a03fe-5c7a-5da5-b26d-3c76e1a5decf | note | Inspection Description - Particle Density & Water Absorbtion
f1b5c3de-5aa8-5b98-a644-9e9a31559c3c | note | Test/Inspection method - AS1141.6.1, AS1141.5
706cb644-832c-5f18-b582-7cd29201dc3f | note | Acceptance Criteria - AS1379.2.3
ef6aeaf7-56b6-5f3a-bd46-04e9c9ae5bdf | note | Frequency - 1 per 3 months
6761046f-11ff-5253-8296-d8ac3da12157 | note | Initiated by - Supplier
4e2bf9ee-b702-55a1-8d5d-ccb6295d1480 | note | Approved by - Tech Mgr
0bdbf743-cfd2-56e5-9d99-73dab69d6293 | note | Verification/Witness: Supplier - W, R
756f561a-06c6-5164-9409-b592af2cd80d | note | Verification/Witness: HOL - W
4194c6c4-f8da-5e91-b302-889ce7143aa3 | note | Verifying Document - Supplier test report
9a156953-26e1-5f0f-80f4-b112f16a4c01 | note | Record Location - Tech Mgr office
78181c15-11bc-5013-84d2-a4ec9c501a1f | checkpoint | 3.4 - AS1379.2.3
a9b42171-555e-5b35-8efc-210030104666 | note | Inspection Description - Los Angeles Abrasion Index Value
cf64a4f4-e5dd-5234-abc9-c66a9fa3bb4f | note | Test/Inspection method - AS1141.23
9497de55-dd23-5f18-9839-d735c6b2080c | note | Acceptance Criteria - AS1379.2.3
cfe06d4a-d1e4-5877-95bb-5b367cbeb78e | note | Frequency - 1 per year
6f484f8b-6bee-5a36-9c0f-49c7f4dab7ef | note | Initiated by - Supplier
4cf457ca-da7f-573c-98cd-729f2902a2a9 | note | Approved by - Tech Mgr
350a2201-473e-52de-88f7-b9aaf3194dcc | note | Verification/Witness: Supplier - W, R
294af989-6cb8-56ad-8b9e-ff5b570c110d | note | Verification/Witness: HOL - W
2601cee5-17e1-5a6a-bd3f-8eb17e890fe3 | note | Verifying Document - Supplier test report
7729f1aa-6f76-5ca4-9ccf-ac910409cbd3 | note | Record Location - Tech Mgr office
6a3a7aaf-efa9-5717-ab38-7f9e218de83e | checkpoint | 3.5 - AS1379.2.3
2ea03519-dbac-5426-b342-9ebef12327a9 | note | Inspection Description - Weak Particles
e2063494-f159-5047-a0b3-afe487d93b7c | note | Test/Inspection method - AS1141.32
bd320f79-0581-5dca-902d-0a2802a08cae | note | Acceptance Criteria - AS1379.2.3
6feebfc9-a096-581b-8e64-badcf4995ae8 | note | Frequency - 1 per year
2d40c2a2-eb46-51c7-b127-ba06ecad9a97 | note | Initiated by - Supplier
047280db-e63e-5a63-be4f-5a9689e53ef6 | note | Approved by - Tech Mgr
81194b8b-3b42-5a7b-bb15-296507742150 | note | Verification/Witness: Supplier - W, R
8f467c84-4c4a-5687-90b6-fcd919d0d606 | note | Verification/Witness: HOL - W
bb8ae132-1108-503a-beb7-5abad5420d28 | note | Verifying Document - Supplier test report
5d257d22-b264-5441-874c-873169d1241a | note | Record Location - Tech Mgr office
f53c62bd-04a5-533e-b171-a7352348ff69 | checkpoint | 3.6 - AS1379.2.3
7862026e-5234-5cd4-babe-170741560dea | note | Inspection Description - Wet/Dry Strength Variation
02910be3-8956-5aee-a905-345a02900d2b | note | Test/Inspection method - AS1141.22, AS2758.7
2453eec4-72dc-5d90-a914-ec7392d23a1f | note | Acceptance Criteria - AS1379.2.3
07e5a24f-1d0a-54db-8e4d-a58329faa5b2 | note | Frequency - 1 per year
71f61974-3f03-5854-b05f-2f35a6b613d6 | note | Initiated by - Supplier
58b77205-a3f5-529c-8fc5-b019f730aeba | note | Approved by - Tech Mgr
7d200daa-e924-5fcc-96ba-45d2427c4dec | note | Verification/Witness: Supplier - W, R
94bcc53f-5c91-5e26-8edd-0761081ac44f | note | Verification/Witness: HOL - W
70cf9164-a09e-527b-9641-fd90c939f98c | note | Verifying Document - Supplier test report
1e857470-6285-5d95-9ac0-5e7986219ff9 | note | Record Location - Tech Mgr office
83a0c381-226a-50d7-87b6-b3e025e4ef20 | checkpoint | 3.7 - AS1379.2.3
b463dc6c-6a7f-5d03-97b5-82b728dff5c2 | note | Inspection Description - Petrographic Analysis
1f9f802f-a09e-56a4-b9f3-e74f84bab64b | note | Test/Inspection method - ASTM C295
eedfbc46-e6d5-590e-9da1-eb543ac8ee4a | note | Acceptance Criteria - AS1379.2.3
83a90181-dbfd-55f7-9829-7b7480a99318 | note | Frequency - 1 per 2 years
44e063b5-4ac1-513a-a5f2-dcb89f30d3f1 | note | Initiated by - Supplier
09d38fe5-9784-5f59-b41b-7ec96c806188 | note | Approved by - Tech Mgr
3bb3982a-464f-582b-a837-8fc2aa6ffc9e | note | Verification/Witness: Supplier - W, R
67c73329-0ac8-571d-921b-6ebf494ebe95 | note | Verification/Witness: HOL - W
26fa76af-a295-597f-b2fd-6f4347c3c79f | note | Verifying Document - Supplier test report
7646f751-c2cf-5272-8240-7cfe5d45c67d | note | Record Location - Tech Mgr office
96127b49-2878-5c5c-afb8-3692ed0a25b7 | checkpoint | 3.8 - AS1379.2.3
b6c26665-5ac8-5e66-bb3e-0f5d9d3845b2 | note | Inspection Description - Sodium Sulphate Soundness
f3b58125-d5fe-5ef1-96f6-d0d159fc1f47 | note | Test/Inspection method - AS1141.24
c1e4fa64-6b6c-5e9e-bf37-7fa10b623c18 | note | Acceptance Criteria - AS1379.2.3
95448144-7b59-587b-830d-e74f9a3538a5 | note | Frequency - 1 per year
5261eded-37c7-51a3-b022-76899d6b282f | note | Initiated by - Supplier
43cf3a88-fee2-5c11-a303-610764a6089f | note | Approved by - Tech Mgr
becb2948-1558-5b62-9f21-332e6d2cc6fd | note | Verification/Witness: Supplier - W, R
9e2f1709-9d4a-5cd3-adaf-a04de8f283a6 | note | Verification/Witness: HOL - W
e7bb28a2-b3ef-5888-8cac-2615ce247c99 | note | Verifying Document - Supplier test report
d4b72f93-bc74-521a-b677-5a246cc356f4 | note | Record Location - Tech Mgr office
72370808-aa65-502a-9694-95fc4b916a1e | checkpoint | 3.9 - BECA Cl 11.4.6.2
772b14dc-db2d-5310-8e06-3eeb599c8cee | note | Inspection Description - Reference Sample
82468b8b-714a-5c37-a6df-cb0c6be997ee | note | Acceptance Criteria - -
366af996-8450-553a-bd47-bf28d24e5dd7 | note | Frequency - Once Only : 2 x 25kg samples of each coarse aggregate fraction
a2ded056-c7d6-5171-b6f9-3a17482d82e6 | note | Initiated by - Supplier
fdfcbd0a-98db-51e5-807c-afb2ca347437 | note | Approved by - Tech Mgr
e226a775-e113-5f96-b44a-0680cc11b5ad | note | Verification/Witness: Company - W
acaaa783-556c-582f-8f46-d97d6659a9d4 | note | Verifying Document - Record only
8de157b8-2b3c-5a84-ba39-83a0f5b7232a | note | Record Location - Tech Mgr office
b2563f1d-4aef-5fa3-9870-0c6a03784189 | section | 4 - Fine Aggregate
5fc44e36-7fa0-5d7d-a20e-b0d4a06a601c | checkpoint | 4.1 - AS1379.2.3
91a7f04c-6174-5cbd-81fb-8e809b5629ad | note | Inspection Description - Particle Size Distribution
a0095355-387b-5fdd-80c0-59a3228d2799 | note | Test/Inspection method - AS 1141.11.1
12406254-bfc4-593f-89aa-2d5a6583aa10 | note | Acceptance Criteria - AS1379.2.3
f01b2fc1-3e64-5b5e-8b61-e68890c10b7a | note | Frequency - 1/1000 tonnes
460289a1-f106-5554-915a-79af4262e6ab | note | Initiated by - Supplier
49f42c2c-1354-5d0d-bb68-b83a80606302 | note | Approved by - Tech Mgr
5cdd97fe-5016-54b0-b2cf-fa03557bbc67 | note | Verification/Witness: Supplier - W, R
462e47af-aac5-5f0b-9cce-bd4bb573bf9a | note | Verification/Witness: HOL - W
7008a2d9-0a29-597f-bfb4-12d0ed12c4e4 | note | Verifying Document - Supplier test report
a73a4a31-e837-5f97-b6cc-336eb3a0a470 | note | Record Location - Tech Mgr office
f19e05e1-9030-5629-8ef4-6a295bf9049d | checkpoint | 4.2 - AS1379.2.3
a479e826-a0c1-58a9-9c12-46b01790c724 | note | Inspection Description - Sodium Sulphate Soundness
ad4fed8d-fd24-5f65-a31d-8bed878b32c7 | note | Test/Inspection method - AS1141.24
2a14e042-2fc3-5bb9-8ca7-6990dc585985 | note | Acceptance Criteria - AS1379.2.3
32208901-2adc-5443-be69-df267f5d1085 | note | Frequency - 1 per year
024077bd-21f7-59ae-b227-e2854a87b0b0 | note | Initiated by - Supplier
d047ef0d-c0d8-5048-80ec-edaed8462bd6 | note | Approved by - Tech Mgr
545b60c3-9a61-53c7-8276-0dacae83b151 | note | Verification/Witness: Supplier - W, R
bc30ef70-2a5a-5f4f-b5db-5b079ab49bc0 | note | Verification/Witness: HOL - W
613e4bef-9be5-58af-bf3c-41b4c40f1feb | note | Verifying Document - Supplier test report
21c54219-2acc-5809-849d-007c0efcd879 | note | Record Location - Tech Mgr office
d475187e-ea0d-524e-ab0d-0d0880da5db4 | checkpoint | 4.3 - AS1379.2.3
bc956910-fa68-5041-b4dd-f7e4b9094652 | note | Inspection Description - Particle Density & Water Absorbtion
36d7d301-2c90-5eee-a4ea-4eb2aa424595 | note | Test/Inspection method - AS1141.6.1, AS1141.5
04f941df-938d-503f-9c1f-090c5e278c93 | note | Acceptance Criteria - AS1379.2.3
190b9600-7a5f-5522-8ebb-5282359aeb71 | note | Frequency - 1 per 3 months
64dfe3cf-39da-575d-a0e2-47bba7f1920d | note | Initiated by - Supplier
33084b4e-2b4f-5d20-99eb-ac33be4d24a2 | note | Approved by - Tech Mgr
c3174e94-e0e3-5f3d-ab66-0166c34c52f9 | note | Verification/Witness: Supplier - W, R
6192201b-ebff-5f79-b33d-d1d3cd8ad352 | note | Verification/Witness: HOL - W
6cc35bd8-be4a-5b18-b4ff-1c8484f1edec | note | Verifying Document - Supplier test report
70d64e6f-7c36-5f71-ac2b-1a70141f8abe | note | Record Location - Tech Mgr office
b34923f2-ce05-5a63-89b6-c19892d24abc | checkpoint | 4.4 - AS1379.2.3
5f86ec19-9421-5071-b572-9334f65a5c35 | note | Inspection Description - Petrographic Analysis
e0dbe218-dabb-5a8c-b24c-3c7436386b46 | note | Test/Inspection method - ASTM C295
60dcc288-cd44-5452-b9ce-0a8f77d1580b | note | Acceptance Criteria - AS1379.2.3
52fa2847-38d2-5d50-9a1c-81fc8080c9e3 | note | Frequency - 1 per 2 years
b48651d2-de84-5296-b25c-a53da4746b06 | note | Initiated by - Supplier
07df4faf-8ccb-5c64-bca7-73ff66277bde | note | Approved by - Tech Mgr
e8b23dbb-23a4-578a-b9fb-8a76d7747c70 | note | Verification/Witness: Supplier - W, R
b7441240-b060-5784-b22b-5bdd8062aa57 | note | Verification/Witness: HOL - W
8018a892-db82-53b3-bfb9-36ad591ac064 | note | Verifying Document - Supplier test report
d4c51f49-885a-56b8-a684-18f7369922ad | note | Record Location - Tech Mgr office
810d35c9-a489-52f1-b0df-7c70b4124cac | checkpoint | 4.5 - AS1379.2.3
f637c367-2a49-5804-9b9f-81e1b15e473a | note | Inspection Description - Sugar Content
872be669-cfda-539d-bef3-d05adbac06c5 | note | Test/Inspection method - AS1141.35
6041b2fa-59d6-598b-944d-988a0e06eb8e | note | Acceptance Criteria - AS1379.2.3
b640ca0b-a92f-5ac6-9eda-5a332a8f8cc0 | note | Frequency - 1 per year
f3895a18-2634-58d2-bffd-e7ec5329f6fd | note | Initiated by - Supplier
de40d2e8-169f-50a9-a913-89f3f8bc33a3 | note | Approved by - Tech Mgr
73fe4fee-ce58-5e47-977f-edc1ea66e2a6 | note | Verification/Witness: Supplier - W, R
8cd2ec01-e76d-564d-a1e9-a4fa8bd4baf2 | note | Verification/Witness: HOL - W
7a8df9f5-3483-5931-b767-c2517b0955d6 | note | Verifying Document - Supplier test report
5fb18956-3aba-5a1a-93b1-14e8132d6176 | note | Record Location - Tech Mgr office
0a3e5c3a-71b6-5949-aea4-3e0723b4e25e | checkpoint | 4.6 - AS1379.2.3
9a8c871b-3927-5c29-a314-74698e27a118 | note | Inspection Description - Clay & Fine Silts
784bf440-a5d9-58bc-b298-c6560028660b | note | Test/Inspection method - AS1141.33
23849356-ae11-5012-b18d-eef06b7cecbd | note | Acceptance Criteria - AS1379.2.3
b4fc7a27-eb5f-58cd-b509-688d39148169 | note | Frequency - 1/1000 tonnes
3fcd12b8-1091-58a6-9b68-f6699f433a06 | note | Initiated by - Supplier
11fbac60-ef98-51ad-a04f-44fae04669fb | note | Approved by - Tech Mgr
2ce00b08-45a5-55d6-b983-1bb2221780c4 | note | Verification/Witness: Supplier - W, R
e6118be6-3bee-5bcd-89ef-ccc0c5cec3cf | note | Verification/Witness: HOL - W
daa78a73-916c-552c-9deb-25c2c53dd136 | note | Verifying Document - Supplier test report
9b8e68de-ced3-502e-ad3a-e88a4192c08e | note | Record Location - Tech Mgr office
5d2b7abc-2be1-5b91-8db8-83e1dfcecd26 | checkpoint | 4.7 - AS1379.2.3
f6f14299-8296-54ae-94fa-61e22d6f1193 | note | Inspection Description - Organic Impurities
2d0e78af-5196-5838-ab1c-db807c1b22b4 | note | Test/Inspection method - AS1141.34
fef298e1-6611-5eee-aae7-356335b7fb52 | note | Acceptance Criteria - AS1379.2.3
47422149-e177-57a4-8116-9cdb10cf2844 | note | Frequency - 1 per month
c76e64ff-0f87-5bbb-83b4-2ec57d836947 | note | Initiated by - Supplier
86f9f2c2-7c0a-5ad1-ac13-3549d7b658f5 | note | Approved by - Tech Mgr
05e94dbf-f486-5f95-9f8c-4d1235413d66 | note | Verification/Witness: Supplier - W, R
96150f32-c3e3-5371-bfc2-aa61268a5c7f | note | Verification/Witness: HOL - W
bc7eacfb-5787-576a-9e3e-498bdfb2ee00 | note | Verifying Document - Supplier test report
9673972d-5e7c-5f9e-bdc4-d3994313a734 | note | Record Location - Tech Mgr office
d610d698-50c7-54dc-bbb0-a3a5195da543 | checkpoint | 4.8 - AS1379.2.3
0fd9ee91-a161-593e-8343-547b5ee63894 | note | Inspection Description - pH Value
28a6bfd6-6bf2-516d-a727-10b9712b7213 | note | Test/Inspection method - AS1289.4.3.1
ef2939e4-d143-5b7e-88c3-113bbaf9bacf | note | Acceptance Criteria - AS1379.2.3
31850176-3d8d-574b-a473-5140164eba5c | note | Frequency - 1 per year
feb1ac21-9126-524f-ab83-00b12020b868 | note | Initiated by - Supplier
b9d1defe-0cf7-5a62-b77c-2bbe0f346e9c | note | Approved by - Tech Mgr
1e7473b4-1fb0-5220-8b76-dda1f4803b71 | note | Verification/Witness: Supplier - W, R
a4e941c5-4923-5dad-95e8-492b28844597 | note | Verification/Witness: HOL - W
820e6ce2-1db5-5aa3-8585-7a63aa5687bd | note | Verifying Document - Supplier test report
e0e623d5-817f-5d1f-ab0d-3d99c95ff021 | note | Record Location - Tech Mgr office
36ae7dab-6136-5351-b7b5-6ddd1b071af4 | checkpoint | 4.9 - BECA Cl 11.4.6.2
a699308f-7f0e-5c35-8cf3-68cd8bce5732 | note | Inspection Description - Reference Sample
e8dd2da3-062c-5e66-a095-3721789f14ce | note | Acceptance Criteria - -
de751385-d2cf-59b0-9ade-d9e7a18d5da0 | note | Frequency - Once Only : 2 x 25kg samples of fine aggregate
8b516e56-c066-5d4f-a347-092d28be179e | note | Initiated by - Supplier
bbf06296-4832-5e89-94ac-22dccb679be0 | note | Approved by - Tech Mgr
4f1ad25a-7a3b-5c43-9e04-037e2a0a1a42 | note | Verification/Witness: Company - W
c22df78f-1138-5d0c-8bc9-5f2c8db3698e | note | Verifying Document - Record only
088dec74-7049-59e1-971b-7dbc7c0f4bfc | note | Record Location - Tech Mgr office
4ba8f446-d7ca-5cae-9321-342cea4afdda | section | 5 - Water
9248abba-5aa2-575b-ae02-45ef91bf702d | checkpoint | 5.1 - AS1379.2.4
efc3429b-9077-57db-8b17-438a429d0fb6 | note | Inspection Description - Mains water
2b0352df-726a-53e1-a469-d27ef6c8673a | note | Acceptance Criteria - Main complies
6ad14ccc-645a-57ea-a785-e3f9cff43ef8 | note | Frequency - Nil
33a58d6d-3f93-52b5-9fbb-5ef96287095e | note | Approved by -
42da8b0c-8014-5bd9-a73a-1013ebf1d1c7 | checkpoint | 5.2 - AS1379.2.4
6050ac90-f7d2-5d16-b7e1-018d7fb3543e | note | Inspection Description - Non mains water
18f0c1e1-fea7-5c85-bc4f-fb596794b0be | note | ~ Sugar
d42317e8-27cc-5c22-ba29-6815d01403e1 | note | ~ Oil & grease
9bd5d003-1f10-5256-8a71-a61f20620f31 | note | ~ pH
3272e43d-92ac-5639-8ebf-b3f90e39db5a | note | ~ Chlorides
c7d913e5-6184-5f2c-9c60-d0778b4be5e5 | note | ~ Sulfates
9a59e793-63b7-570f-9fdd-816a43d97ce0 | note | ~ Total suspended solids
ec04db76-54e5-5610-a7e9-514826b90894 | note | Test/Inspection method - AS1141.35 APHA 5520 AS1580.505.1
fc083733-280e-5437-8054-a6379a117460 | note | Acceptance Criteria - 100 mg/L max
4c78f8da-b910-589c-9175-8db8bd7ce72f | note | ○ 50 mg/L max
31b9d76e-f855-5163-aa8e-c9dccefa4f4f | note | ○ > 5
8625774b-50a0-55f1-8bc6-6b21bf216824 | note | ○ 500 mg/L max
d855d1ab-19d4-575c-8604-548e0b1f2b1c | note | ○ 500 mg/L max
7aa71ddb-5144-5846-a3f6-5b5784a40558 | note | ○ 2000 mg/L max
5e666e01-a75c-581a-9e60-90f2a3ba5bd9 | note | Frequency - 1 / 6 months
2b80f98b-9f39-5ad0-a1cf-39ccc89aac5a | note | Initiated by - AOM
0fb812ed-63ad-5a2f-9023-3bfc55c15def | note | Approved by - Tech Mgr
7776c732-147c-5674-ab90-74b7e023c2c0 | note | Verification/Witness: HOL - W
02cd6f1d-0d30-51c5-bfaa-f04d7aa2530d | note | Verifying Document - Lab report
02f8fe04-5380-54aa-95d3-693e0100fbe8 | note | Record Location - Tech Mgr office
82172cdd-75bd-5224-abe8-68e843bd97be | section | 6 - Admixtures
f91fd035-5479-576b-936d-9e6ada6f25c9 | checkpoint | 6.1 - AS1379.2.5
5a9a3039-b856-5dbb-bd8b-7200d9d24f52 | note | Inspection Description - WR Admixture general acceptance
d9bac8f9-cdfb-5f05-951b-69f7243c8317 | note | Test/Inspection method - AS1478.2
14f4a1a2-2822-57f6-8d1e-614baa13911f | note | Acceptance Criteria - AS1478.1 Table 2.1
bcd34a34-91bf-5490-80ad-c942cd1e15a3 | note | Frequency - Initial
4f415136-6b00-5405-a131-9f14b59a3ed3 | note | Initiated by - Tech Mgr
d98d6d36-272a-588d-ada7-66b459f8b9a9 | note | Approved by - Tech Mgr
78b48b48-3894-5ddf-a9e2-271741b8cc6f | note | Verification/Witness: Supplier - W, R
5f0f8b2f-9c28-55bf-95ee-c0928f582bd9 | note | Verification/Witness: HOL - W
a8fa61cf-702b-58ba-b831-01e13a4ac6b7 | note | Verifying Document - Supplier report
341fadab-bafa-5c68-bb82-9b4506cea225 | note | Record Location - Tech Mgr office
4e4a638d-2dd2-5211-a648-d67d85c14ba9 | checkpoint | 6.2 - AS1379.2.5
40be135b-821d-5d27-a5c2-15a6493c768c | note | Inspection Description - WR Admixture Uniformity test
c0597203-692b-545f-ba4d-cc293f0c1762 | note | Test/Inspection method - AS1478.2
4c2771b5-63fe-589b-98e3-ad10f202ca04 | note | Acceptance Criteria - AS1478 Cl 2.1.3
8ee3b20b-480a-513f-9737-795e2a60bcb3 | note | [Supplier specs for pH (+/- 1), Relative density (+/- 0.02), Non-volitle content (+/- 2%)]
aaeadb47-ba68-588a-9636-01eb680eaae2 | note | Frequency - MBCC Supplied (Each Batch)
9183ac6b-5f48-58ee-9bd1-f3574d0a64fe | note | Initiated by - Supplier
7aba0526-fb01-5191-b174-992245861299 | note | Approved by - Tech Mgr
6958eb3c-8a5c-530b-a38d-f190cfddfc1c | note | Verification/Witness: Supplier - W, R
b87f26c1-c35b-52cf-9665-56814f2d2d8b | note | Verification/Witness: HOL - W
2c905e60-a062-5f23-a260-21cd16357205 | note | Verifying Document - Test Reports
cad48da2-4e31-531b-9be2-0d8774711c84 | note | Record Location - Plant
cef5e708-184d-5b4e-8957-167b54d47b26 | checkpoint | 6.3 - AS1379.2.5
971f9dad-fcdf-5006-a7d8-59d02ae99e0d | note | Inspection Description - AEA Admixture general acceptance
c2f5feea-ffa8-5f2d-8e0a-5a72355b1b1d | note | Test/Inspection method - AS1478.2
f1c4ca3c-5d57-5694-b534-c54b254e640c | note | Acceptance Criteria - AS1478.1 Table 2.1
bbdcb664-0095-5321-b3a7-17d2f5b6e9c6 | note | Frequency - Initial
4dbf63df-2e5e-5f15-9728-7384abb8c54a | note | Initiated by - Tech Mgr
60699419-4f16-53e7-8bb7-22cb09c901a9 | note | Approved by - Tech Mgr
0bfe4df1-901b-5b72-b44b-211ace33d09a | note | Verification/Witness: Supplier - W, R
ed89ab92-3ff4-547b-9a8f-60c461d21aa0 | note | Verification/Witness: HOL - W
d6ed629c-4529-5435-8916-fa7d1f81fb12 | note | Verifying Document - Supplier report
1279fcca-41cc-5a08-b40d-dfa6d667a3ca | note | Record Location - Tech Mgr office
5ab4d9d7-2bbe-54c7-b7a4-bd3039c618b0 | checkpoint | 6.4 - AS1379.2.5
97edff47-9a2f-5a96-a91d-c99209efafc4 | note | Inspection Description - AEA Admixture Uniformity test
dbc1981c-c4ad-5e9b-ade1-2b55479799fb | note | Test/Inspection method - AS1478.2
7f272233-7875-5780-95ba-1d7bb91713dd | note | Acceptance Criteria - AS1478 Cl 2.2.3
13b47d1d-9ac7-5ad3-a465-3f7a1913a4a9 | note | [Supplier specs for pH (+/- 1), Relative density (+/- 0.01), Non-volitle content (+/- 1%)]
0f022f6a-904d-5876-904b-d66750fc52fc | note | Frequency - MBCC Supplied (Each Batch)
8d3af956-a914-5603-90ff-735099caf42b | note | Initiated by - Supplier
548b92e5-6718-538c-9b7d-9fd26515d47d | note | Approved by - Tech Mgr
31329bfb-1996-5f23-b81e-04171442d096 | note | Verification/Witness: Supplier - W, R
9ef2cdc5-4250-5b30-845a-a7b5e6d68413 | note | Verification/Witness: HOL - W
428e968b-2712-5af9-82f2-71065f8113d0 | note | Verifying Document - Test Reports
023053fa-86a4-5a7f-a8f4-6a58fa8c3b85 | note | Record Location - Plant
c7a9e9cc-e4f7-5ac5-ae90-c0930acd2ae1 | section | 7 - Transport
87c85bb4-1a58-56da-b8b1-d4b1c3d65ca0 | checkpoint | 7.1 - HOL QMS PN6.1
8602acab-3d14-53b4-9d19-2122a671fb55 | note | Inspection Description - Agitator blade inspection
fab122c6-09ca-5d09-b971-811c80aed791 | note | Acceptance Criteria - Concrete Barrel Solution - No excess buildup, No excess wear
69e4f90c-7429-5bbd-9365-28224629cf7b | note | Frequency - 1 / 3 months
b0d4b03b-c057-5fcb-81c3-cc6a989eec3c | note | Initiated by - PS
578f8000-e5ac-58a1-9469-8700e856a6b5 | note | Approved by - AOM
c34facf5-53eb-5972-8e9b-217aab3ef0a4 | note | Verification/Witness: HOL - W
45d843ba-c6c5-52d5-8afc-e9206ddfdf19 | note | Verifying Document - Inspection report
647f4bf8-e3e4-510f-b16e-e8227e672668 | note | Record Location - Plant
187e8e76-2885-5aa9-a78a-6539d1e1a50a | checkpoint | 7.2 - AS1379 3.5.1 (a)
7da0c1dd-5335-528a-b846-8713ea5a6763 | note | Inspection Description - Mixer uniformity test
db07f433-f819-5b57-8be3-65e069b2bc3e | note | Test/Inspection method - AS1012
b1b661f9-510a-5981-8c43-e4c18682bed0 | note | Acceptance Criteria - AS1379 Appendix A Table A1
2f07405d-f6e4-5588-ae98-df31f1a2ffd8 | note | Frequency - Initial for agi type
6ba29222-f6d7-5b5b-ab79-5c96a60fe9e9 | note | Initiated by - Trans
0d9d05bc-2de8-5720-9990-c08e638162ae | note | Approved by - Tech Mgr
ad482c10-7eec-588d-9904-c8746dec0930 | note | Verification/Witness: HOL - W
aa6ee9ec-4c79-538a-abb5-1c2775a053ab | note | Verifying Document - Manufacturer report HOL test report
b7893fb9-d6b8-54e7-9877-f2c5a013d719 | note | Record Location - Tech Mgr office
82d23ddb-a1eb-47d1-a0d2-701243a4e79d | checklist | FH-ZU2-QU-ITP012 - High Early Strength Lean Concrete Pavement Production - Rev 0 | itp | ITP012 - High Early Strength Lean Concrete Pavement Production
edc13f40-3e52-41b4-bd32-2185b2c2a11c | section | 1) Plant
a97e1d8b-341c-4100-8fef-4008139a4533 | checkpoint | 1.1 - Batch tolerances
b9943286-8c92-57b6-8049-dbdb04338ccf | note | Code / Spec Ref - AS1379 4.2.1
86ed0e80-443a-5fea-bdac-d56be1f3b475 | note | Acceptance Criteria - AS1379 Table 4.1
438fd021-7306-5e5b-85c2-a6c6da35918a | note | Frequency - Each Batch
991f71dd-1f32-5959-846a-8c657a14ee5b | note | Initiated by - PS
52dacf51-9d99-59ea-a2f2-0eff4322163a | note | Approved by - PS
0f36ef84-1915-54ff-befe-7b83b6322f0e | note | Verification / witness: Supplier -
5ed1d111-6563-5dce-b984-57648edd3b09 | note | Verification / witness: HOL - W
ef37a3e1-6b7d-5491-a4fa-8980d1fc1a53 | note | Verification / witness: Company -
81f94c7a-6d9d-560b-9e02-a6ecb4655c47 | note | Verifying document - Electronic
8c735506-9d18-5521-a82a-f0aaddc76ced | note | Record Location - Batch computer
c9cf40f4-9d20-5456-b00b-6575ee66c9f3 | date | Date Completed:
f72d9654-71c9-46a6-9383-c16c41657ced | checkpoint | 1.2 - Record Plant Malfunctions
fe5e3b38-fcda-55b4-bd5c-a8d47237cee7 | note | Code / Spec Ref - HOL QMS PN6.1
fd8dc4bd-0324-5423-ac5a-4c4fc3cfbdc3 | note | Acceptance Criteria - All plant mulfunctions are to be documented
fa562d49-2d3c-54a3-b504-abf4eb5e5c7c | note | Frequency - Each Time
a77816f3-1199-5280-87a3-b348fad9f61f | note | Initiated by - PS
2acd8d79-7e14-5bf3-8667-2a75277aac05 | note | Approved by - AOM
7ef783a0-3483-50ac-966d-6dbaffb65ca7 | note | Verification / witness: Supplier -
2340a1e6-0420-5658-8e73-7d486bcc1fe3 | note | Verification / witness: HOL - W
ed8034bd-4577-5e5c-9e78-fe782cf7d08d | note | Verification / witness: Company -
75bde53d-1704-555d-924b-d889c46e7f90 | note | Verifying document - Register
719e1c61-189d-5f8b-ace8-01a4b17e7a32 | note | Record Location - AOM office
16ef357f-fe6d-54d6-a477-722d60637304 | date | Date Completed:
6e321a29-a1a9-443a-ac3c-99a45d07f169 | checkpoint | 1.3 - Weigh Hopper (Cem & Agg)
8f8727e7-bb5a-58c7-babe-2a01b8e9aa85 | note | Code / Spec Ref - AS1379.3.3.2
77cb045b-bd2d-596f-b45a-b2fa9aa82ac4 | note | Test / inspection method - AS1379
b0a12989-e5a4-56c9-bcdd-199a675ed144 | note | Acceptance Criteria - ± 0.4% of the Max. Scale Value
4c829d85-4c34-5612-b7ed-e52d02c53364 | note | Frequency - VicRoads Min. 3 Monthly
861febb3-c911-5b32-853a-94698ce7913b | note | Initiated by - PS
8966815a-2b52-5a13-b454-e5b942003cbc | note | Approved by - AOM
7b665053-3076-5875-8d77-77bb185af44b | note | Verification / witness: Supplier -
402ac3d2-d7ab-5bf6-b77e-0d583d52e373 | note | Verification / witness: HOL - W
ed307eb9-8c24-5e11-988b-7b082b8e3621 | note | Verification / witness: Company -
cb38e24f-e083-5e4b-a9a9-fb8f7e5c1e1b | note | Verifying document - Calibration Report
9f4f4427-faa7-57bc-9a79-7d1fb2f67792 | note | Record Location - Google
987e736e-eda1-5a16-b3cb-91600626b098 | date | Date Completed:
ff794717-2dbe-4b63-886a-209589a07787 | checkpoint | 1.4 - Water Meters (Plant, Slump Stands & Trucks)
8737d837-cb76-5753-b12b-0f1c82033495 | note | Code / Spec Ref - AS1379.3.4.2
13907fc4-b467-5aa5-966d-634a8a1bde9c | note | Test / inspection method - TRBE652973
a5dabc9d-bd5c-56d4-8e3e-256d9016ea45 | note | Acceptance Criteria - ± 2%
59aa70a1-64a1-59d5-bb7e-1c53db6991a8 | note | Frequency - VicRoads Min. 3 Monthly
96a20af5-6096-5ac0-9ccc-02bce14a4426 | note | Initiated by - PS
cf97e23d-10dc-5d23-9ef5-5ac39f854645 | note | Approved by - AOM
d5f30f2c-9142-5be5-af17-4c69c8bcbbd5 | note | Verification / witness: Supplier -
44894843-f68a-56b1-a7ed-9e2a3734d130 | note | Verification / witness: HOL - W
1c60cf52-ec20-57a5-b04f-caea0692f527 | note | Verification / witness: Company -
b8b650c1-f80e-5863-a273-765098ab3fd0 | note | Verifying document - Calibration Report
671fb2df-5f1b-5ce5-8839-10ac711f29f1 | note | Record Location - Google
9ed791ab-abd0-5dfb-bf23-42518c4f3174 | date | Date Completed:
1c5e587f-7cb4-412c-9325-ea44b82aeb31 | checkpoint | 1.5 - Admixtures
dbc3652c-886d-5280-b661-09bb4dd05cf9 | note | Code / Spec Ref - AS1379.3.4.2
9d33f62f-3fef-54ef-9f0a-a4485ffdadf5 | note | Test / inspection method - BASF TM033
8fc3ef05-0cc3-50fc-9de4-a93e5cf484f5 | note | Acceptance Criteria - ± 5%
eb2b3ef3-112f-5f9e-8a02-dd9842a9961e | note | Frequency - VicRoads Min. 3 Monthly
dc8c6ef6-c267-5003-adc6-8b9a5c8dceee | note | Initiated by - PS
1765eb1f-111c-580f-9c76-475eb0f8ba0f | note | Approved by - AOM
6271488d-95b7-5a75-9308-43bcf4fd8ca3 | note | Verification / witness: Supplier -
a981b4b2-dc29-5de4-9a9d-209358a26b92 | note | Verification / witness: HOL - W
237a327b-545a-5b8a-88e9-7929885889e6 | note | Verification / witness: Company -
54bafa72-211e-5270-b8ad-095504023831 | note | Verifying document - Calibration Report
cfb54465-b38c-5646-b0fa-ad55e1019ab7 | note | Record Location - Google
a45981de-03ad-5c34-8f01-dfc4d7434eb9 | date | Date Completed:
44755269-56df-49f8-a9d6-fa3fac84acf1 | section | 2) Cementitous materials
5c4173fd-eb55-473e-bd54-9203a8887f3c | checkpoint | 2.1 - Type GP cement
abd9caf3-6de1-5b89-bf0e-af93c59d9b2a | note | Code / Spec Ref - AS1379.2.2
f527d512-9e4f-5f43-aae2-a35480a5e8a0 | note | Test / inspection method - AS2350
70fadb4a-2d8e-54bb-a193-eefc88327446 | note | Acceptance Criteria - AS3972 Table 2
6b750388-405b-59a3-b257-3767b2d2d3b6 | note | Frequency - Cement Australia Supplied (as per AS3972 Clause 5.2)
5a603310-b5d1-5c43-9f1a-21af3b7ed1ca | note | Initiated by - Supplier
17633baa-3e25-5ed9-9c8a-6f08b45a1924 | note | Approved by - Tech Mgr
56a56fec-353d-5dbf-9f3f-4948f301508e | note | Verification / witness: Supplier - W, R
8236fa2e-ab76-54d0-8114-8d626fbc4294 | note | Verification / witness: HOL - W
a63f8795-017b-57e7-ad6e-19d834fea97d | note | Verification / witness: Company - H
a620975f-eec0-5127-a7ba-f33524a88673 | note | Verifying document - Supplier test report
f0349a24-e372-5beb-a1d4-e3b389ab2ea8 | note | Record Location - Tech Mgr office
47764ccb-0b61-5953-9e73-bef1b35e915c | date | Date Completed:
cfaf8949-7e4e-4d2b-8a4d-a876d082c59a | signoff | AUTHORITY HOLDPOINT
1add049b-66b2-4e75-ac26-531062f481db | checkpoint | 2.1 - Reference Sample
25854f03-0728-59e8-baf5-79efe4f27226 | note | Code / Spec Ref - BECA Cl 11.4.7, 11.24.5
8eb96525-2c07-5fe0-a757-41120e367171 | note | Frequency - Plant Sample : 10kg / 1000 tonnes
305ff2f3-7d72-52ab-9416-a222915fe4b2 | note | Initiated by - Supplier
eeb149b4-4e4e-5da8-b274-99b9dd5ebd62 | note | Approved by - Tech Mgr
66bc2e17-426b-541b-9bcf-9cad10c9283c | note | Verification / witness: Supplier -
7e4fbcf0-248d-53d8-8d62-52196e66b15b | note | Verification / witness: Company - W
eced0314-0172-5a5e-9472-82020e1804e2 | note | Verifying document - Record only
a2348df5-c85c-54f0-886d-f8e90e63ce9a | note | Record Location - Tech Mgr office
9053c326-82bc-5f22-afa9-3083c2564b15 | date | Date Completed:
d2caa701-36a4-4898-9e08-8229fa96b7df | checkpoint | 2.2 - Flyash
35a50202-cbeb-552a-91e2-89ebb2419b6e | note | Code / Spec Ref - AS1379.2.2
196e0c95-307a-55d7-9158-bbe967f2143b | note | Test / inspection method - AS3583
881112d6-e264-56f6-afea-b62657d41ce2 | note | Acceptance Criteria - AS/NZS3582.1 Table 1 - Grade 1
9315388a-767c-5c27-affe-b8c84000936e | note | Frequency - Cement Australia Supplied (as per AS/NZS3582.1 Table 2)
81a16c49-3dc7-5dc0-9e53-78c677ca8d0e | note | Initiated by - Supplier
132c0c7d-551e-5948-a6b2-fe43cefc1790 | note | Approved by - Tech Mgr
65bdabf6-21ea-51d8-9ca5-7af837745e1f | note | Verification / witness: Supplier - W, R
14d8f749-0946-5114-8b8b-61d235d14e94 | note | Verification / witness: HOL - W
3253f6c3-e5d2-5fb0-9e03-6eb075c5b4b6 | note | Verification / witness: Company - H
01e627b7-84e4-557a-b6f8-e4158425f6b4 | note | Verifying document - Supplier test report
83c5c614-1db8-5201-a22a-74534600c133 | note | Record Location - Tech Mgr office
ae0e60c4-b12f-59f8-95ba-6260049ed66e | date | Date Completed:
ba8e3df9-e5c3-4fda-8d19-45ac6bc4bcde | signoff | AUTHORITY HOLDPOINT
9118d094-5b36-4aed-ba31-12b6aba78cc1 | checkpoint | 2.3 - Slag
b4d3bed5-111a-5b44-8fca-9583230a163f | note | Code / Spec Ref - AS1379.2.2
b6e05616-5f6f-59ec-b607-7af329169d7e | note | Test / inspection method - AS3583
6e99ddfc-5001-5c89-af73-a4e50f8dcfb0 | note | Acceptance Criteria - AS3582.2 Table 1
dce785c8-6fae-56bc-91d5-9908a5585c5e | note | Frequency - Cement Australia Supplied (as per AS3582.2 Table 2)
8dbf925d-b67e-58cf-ad91-c18d1295db7b | note | Initiated by - Supplier
5a350411-7449-5907-a527-80335836962f | note | Approved by - Tech Mgr
cc9ad5f7-b490-53e7-8cae-12f3b5c9eece | note | Verification / witness: Supplier - W, R
eed9fba9-3735-5ef2-a46b-2e7499ebff7f | note | Verification / witness: HOL - W
5a5f6935-dac5-5bd8-8a5a-ddc4893382ac | note | Verification / witness: Company - H
b835140d-975f-5a72-997d-e0916d3f6417 | note | Verifying document - Supplier test report
6057b23b-09f7-5197-b78d-fbc1207438c6 | note | Record Location - Tech Mgr office
9e9a3f08-79dc-5ffb-9afb-0dd603ada1d3 | date | Date Completed:
3375405c-09ae-412d-bc1e-c6c95858e421 | signoff | AUTHORITY HOLDPOINT
f9f313ab-5df7-4c5c-beec-376bf9901ed9 | section | 3) Coarse Aggregate
8386e72a-f117-4f99-aaf4-101e6367e4c0 | checkpoint | 3.1 - Particle Size Distribution
24abf56c-1fa2-5227-a967-b5f12fb2275a | note | Code / Spec Ref - AS1379.2.3
afe34448-4998-5d03-8fdc-f1e77a480e4c | note | Test / inspection method - AS1141.11.1
b369a75b-aa1c-5206-a034-b72081a88e64 | note | Acceptance Criteria - AS1379.2.3
db2bdf35-74da-515f-9eb7-a2761d4d7a5b | note | Frequency - 1/1000 tonnes
ee7d4c66-dcf5-5825-ab49-ef36066d1c3d | note | Initiated by - Supplier
df25e526-3f46-5822-b756-610881baa325 | note | Approved by - Tech Mgr
2317cbad-f96e-5abf-8a3b-a52819813ddf | note | Verification / witness: Supplier - W, R
b9b8a7f5-5d21-5ed6-a8a9-70d5674f9885 | note | Verification / witness: HOL - W
e9af74c1-a573-59b4-8eb6-73f189315af0 | note | Verification / witness: Company -
d4ab6bb1-e724-5653-9e3b-25f3289dd6ef | note | Verifying document - Supplier test report
667b1d8d-7279-5877-8a72-f02c2fb0da42 | note | Record Location - Tech Mgr office
7200c1c0-aedc-5096-858a-9d02f673796b | date | Date Completed:
05928d06-835a-4f40-bfe7-a766574f9e68 | checkpoint | 3.2 - Flakiness Index
fe0dd362-fd47-5b37-9520-88d0d47b6d2e | note | Code / Spec Ref - AS1379.2.3
bc9f6c7d-3fcf-5c40-804c-6de3e3877cbe | note | Test / inspection method - AS1141.15
6e163739-97ef-56d6-a587-d3f5f9075dfb | note | Acceptance Criteria - AS1379.2.3
a439f23d-e9b8-5e87-b876-d06b4c72c586 | note | Frequency - 1 per month
0d3e5d88-c116-568c-9130-67ee2da56187 | note | Initiated by - Supplier
3c340d15-04bf-5dae-a944-f9243f1f272e | note | Approved by - Tech Mgr
a82ba656-862f-515e-b307-9d83a696815d | note | Verification / witness: Supplier - W, R
72aefff8-3025-5e12-a91b-879f5a509e13 | note | Verification / witness: HOL - W
26792800-4226-50f9-bae4-58db968d7551 | note | Verification / witness: Company -
41c51e60-0787-5e53-8427-f7b8dbd83b71 | note | Verifying document - Supplier test report
32110826-f48b-5137-88bb-aaa7a059d9d2 | note | Record Location - Tech Mgr office
864c1dae-d55b-5584-80c1-ae8ddf2954b8 | date | Date Completed:
debe25b4-f429-4cad-895e-ef8c8d75baa7 | checkpoint | 3.3 - Particle Density & Water Absorbtion
66d4a083-122e-5d71-b1cc-35607ac603a7 | note | Code / Spec Ref - AS1379.2.3
f2274462-dd70-59d1-b18d-cc1632e914ea | note | Test / inspection method - AS1141.6.1, AS1141.5
9c147e9b-129d-5239-84d7-fa59ea82ca85 | note | Acceptance Criteria - AS1379.2.3
09388605-9785-5866-b21b-a656f7deacd5 | note | Frequency - 1 per 3 months
9d4c5e9a-b0b8-52ab-b56f-1412c984cbd6 | note | Initiated by - Supplier
92057d16-cbe9-5e0a-bd29-b201ff7d50b4 | note | Approved by - Tech Mgr
3573a764-b5de-5a2e-8e51-9a557df9b29f | note | Verification / witness: Supplier - W, R
2a14c62e-7293-5833-bd17-27b9113010eb | note | Verification / witness: HOL - W
7937b1f7-987c-5bd1-8c40-9cd0d60f553e | note | Verification / witness: Company -
290fbbe7-26ad-59a9-abbc-a218231eeffa | note | Verifying document - Supplier test report
5a31faa6-1e4b-56c0-ab7f-854044dffb52 | note | Record Location - Tech Mgr office
48aa82df-fd5b-58d2-8e60-cf86a2a3b592 | date | Date Completed:
7b33ed51-2ecd-45d0-b4da-8b43af1c20b6 | checkpoint | 3.4 - Los Angeles Abrasion Index Value
734675c4-069c-53ff-b9ce-bc14fabea4f2 | note | Code / Spec Ref - AS1379.2.3
fbd44e06-4c91-5dda-a175-a68eb3b195fe | note | Test / inspection method - AS1141.23
18f2bb70-40ce-5dcf-b3fe-1c91b4fae187 | note | Acceptance Criteria - AS1379.2.3
726b883a-3343-561c-b4b9-e1991dec7941 | note | Frequency - 1 per year
f101ba7c-18d7-566b-824c-83bdecdca52b | note | Initiated by - Supplier
96513496-d2cc-56d3-9505-59d43f913538 | note | Approved by - Tech Mgr
0b7bad7e-a33b-5e69-9f07-ffe3087536b3 | note | Verification / witness: Supplier - W, R
94c01655-29d3-5f3d-aafa-45a449d28160 | note | Verification / witness: HOL - W
ab45d0a2-a135-5bfd-b024-c39e393b6dec | note | Verification / witness: Company -
2a642e70-e572-5188-b997-3e332e6ff716 | note | Verifying document - Supplier test report
d4b01e58-4bce-53ab-bfbf-3136413dfb86 | note | Record Location - Tech Mgr office
bb4c3505-e86c-5d5c-a0d3-be86d3b2655c | date | Date Completed:
2b66769f-6cba-42fe-ba43-b4ad46ef35ab | checkpoint | 3.5 - Weak Particles
439cad58-f79a-5e7f-8fdb-fd199b7dac95 | note | Code / Spec Ref - AS1379.2.3
9387e032-2fc4-5238-906b-aed2a4b61c3d | note | Test / inspection method - AS1141.32
775e9ee4-5d68-5ab0-9fd3-92350a9bf4ff | note | Acceptance Criteria - AS1379.2.3
f417dc5c-ef2a-5fb7-87c2-db6088b87927 | note | Frequency - 1 per year
cfa8cfb9-85d1-5910-b710-decf5b159156 | note | Initiated by - Supplier
2decac55-f4bd-5f09-97af-40da04bad463 | note | Approved by - Tech Mgr
03bc8377-c14c-5be8-af44-2b2bb37f8875 | note | Verification / witness: Supplier - W, R
b2166747-199a-51f4-bbb4-ab89ab3f7cd9 | note | Verification / witness: HOL - W
b812baa0-fe2e-5398-afda-5496113e2c5c | note | Verification / witness: Company -
ed87ed9b-ae0f-583c-ae77-e23bd175af2f | note | Verifying document - Supplier test report
b70d9a9a-9ad0-5bb5-99cf-2486c56f4b37 | note | Record Location - Tech Mgr office
5c8bb934-9bbe-5c58-bf1c-96b2464223a9 | date | Date Completed:
d4356f01-ef51-407c-b2c2-b76fa841c474 | checkpoint | 3.6 - Wet/Dry Strength Variation
0d4bb3b7-c7e3-540c-94dc-c16374437bd3 | note | Code / Spec Ref - AS1379.2.3
9e8d7adc-1c35-5f5b-af26-08f9f41aee83 | note | Test / inspection method - AS1141.22, AS2758.7
b9276b80-8244-5861-94b1-3efe63e43974 | note | Acceptance Criteria - AS1379.2.3
bcbda685-4dd7-566e-8349-9545c0ba441e | note | Frequency - 1 per year
54490f29-1984-599a-a603-19191ac06ab1 | note | Initiated by - Supplier
191963d2-3b59-5cbf-80a4-faece6a8d21f | note | Approved by - Tech Mgr
03806560-000e-550b-acd8-e0129322de17 | note | Verification / witness: Supplier - W, R
80cec203-6e6d-5bc5-8aff-32aa454a398b | note | Verification / witness: HOL - W
e6381391-c899-55df-9b5d-5d6a5b4c4c6a | note | Verification / witness: Company -
e8fda191-ec1e-5129-b851-e6e565546e19 | note | Verifying document - Supplier test report
bf2daf6f-06f9-558a-8124-4fc0b631ba31 | note | Record Location - Tech Mgr office
9a5bba11-aba5-5b3c-9c3f-3b79c2f7ade8 | date | Date Completed:
3c7b6ed7-b8ea-48b7-ae09-c85377ca19ff | checkpoint | 3.7 - Petrographic Analysis
53c8293e-5da3-55c8-b611-497a45577359 | note | Code / Spec Ref - AS1379.2.3
b8ebd582-479f-599b-9545-378ca18be74f | note | Test / inspection method - ASTM C295
5202357e-23a2-5434-ab83-d7684284b69b | note | Acceptance Criteria - AS1379.2.3
16761214-a63c-5de9-95dc-3e5b6e817599 | note | Frequency - 1 per 2 years
bd187a6f-035a-5ef5-82dc-9affd03061eb | note | Initiated by - Supplier
d23cbde1-78b3-520c-8107-1acf381ae7e7 | note | Approved by - Tech Mgr
6cf61d7f-fed2-54a2-9c19-baaa9ab4b2de | note | Verification / witness: Supplier - W, R
99f11b19-545d-5d86-aa70-47d0b40a568b | note | Verification / witness: HOL - W
42f1d435-0e89-5208-a124-6117552e98ee | note | Verification / witness: Company -
469fb7af-7262-59d2-8d3d-5af09aacb83b | note | Verifying document - Supplier test report
ff056798-31d7-5651-956e-5d1879b491e6 | note | Record Location - Tech Mgr office
b8db1986-b065-529d-b3a0-4999e5c5b938 | date | Date Completed:
57f025f8-2d24-4ab0-9d0b-7b8f4c4dc539 | checkpoint | 3.8 - Sodium Sulphate Soundness
2b8cd169-086a-5087-981b-720a44c296c1 | note | Code / Spec Ref - AS1379.2.3
4383fe7f-3046-5a0f-b16e-8b7691e5b1d8 | note | Test / inspection method - AS1141.24
5794c874-0527-5251-a934-c288853c1f38 | note | Acceptance Criteria - AS1379.2.3
4fbdef96-4e39-52e7-847c-d58ca1007198 | note | Frequency - 1 per year
2cd4e689-e209-5709-9546-31e6e71e80ec | note | Initiated by - Supplier
0b044a2d-b8db-58b0-a4d8-a7116135d47b | note | Approved by - Tech Mgr
cd5646a5-011f-59fe-97e4-0021bf7276dc | note | Verification / witness: Supplier - W, R
8e558b51-da9d-5d9b-8679-47627b8587c5 | note | Verification / witness: HOL - W
e9e46ed8-e88f-5729-abac-83b988dca861 | note | Verification / witness: Company -
25848c49-acb7-5913-8b49-75393cee6310 | note | Verifying document - Supplier test report
b8bffa43-4346-5bd5-bf84-74b9fb37f436 | note | Record Location - Tech Mgr office
cf077a02-ccaf-5653-a87a-25c8b54fdec4 | date | Date Completed:
d9281a25-bd39-4fe3-aabc-c0c63de31a35 | checkpoint | 3.9 - Reference Sample
7e74408e-8e5b-5ce6-87df-f2ccff62b9d7 | note | Code / Spec Ref - BECA Cl 11.4.6.2
d1f7f0c0-e629-5792-a9f6-ad231dd04d96 | note | Frequency - Once Only : 2 x 25kg samples of each coarse aggregate fraction
320703a5-3379-5f50-ab30-738118fc9b14 | note | Initiated by - Supplier
9ae42a6a-b4fe-534d-8359-6e14bad864bc | note | Approved by - Tech Mgr
977fb99f-96e8-5a2d-ac68-0aa6dcb260a5 | note | Verification / witness: Supplier -
04459358-b523-5743-a11f-6269abfc2d43 | note | Verification / witness: Company - W
8394b42e-d4d6-5dcd-9b63-4311738d0908 | note | Verifying document - Record only
92f682c1-1f0d-5bff-9d5b-4d85f51d25ff | note | Record Location - Tech Mgr office
d245be3a-ad15-5e11-9b2f-f43e35a69781 | date | Date Completed:
c79db396-6d98-4852-8ff7-8527edb277f7 | section | 4) Fine Aggregate
f6163620-bd4d-42f7-8bac-05084565a8f4 | checkpoint | 4.1 - Particle Size Distribution
265dc824-7729-54f1-9932-8ed6e1b0f860 | note | Code / Spec Ref - AS1379.2.3
9011214c-9d41-5906-82df-59ed4cfcec8b | note | Test / inspection method - AS 1141.11.1
e6e0ef2f-e30c-5fc7-a767-4ee704235a9d | note | Acceptance Criteria - AS1379.2.3
7a169ac1-f15e-51a8-90f4-4caaf6699db7 | note | Frequency - 1/1000 tonnes
964cf094-7536-5970-a2aa-543759e52fa9 | note | Initiated by - Supplier
44911cd1-3cef-5b3c-916e-71e92d3e90b5 | note | Approved by - Tech Mgr
55538d17-c012-5f00-9adf-f65ae9d2ea21 | note | Verification / witness: Supplier - W, R
f95d52a1-582b-5ac7-aa4e-2816eb7a1946 | note | Verification / witness: HOL - W
612ea03f-b3bc-5eb4-98ee-7bca5d762238 | note | Verification / witness: Company -
846d54d4-94fa-519f-adec-3aee0b08298d | note | Verifying document - Supplier test report
b5f9f5eb-dd0c-51b8-ad70-277d070a5bae | note | Record Location - Tech Mgr office
fe8148f9-5938-50a1-b320-83e3d40cf663 | date | Date Completed:
8955db6d-dc83-4b7a-a6ab-e91ad4a401b3 | checkpoint | 4.2 - Sodium Sulphate Soundness
b28f07df-1ccc-5837-9f5f-6fa0906ab4c2 | note | Code / Spec Ref - AS1379.2.3
48615c85-086e-52cf-9364-cca6b4cb7d6a | note | Test / inspection method - AS1141.24
154b4160-0f10-509d-bfb2-bb993f72f295 | note | Acceptance Criteria - AS1379.2.3
f6f04c40-5a0b-524e-81f6-e6c51880f083 | note | Frequency - 1 per year
028ab878-6ede-5733-aa4b-6b128b1df54b | note | Initiated by - Supplier
e73118e9-dfdc-5bea-a792-3cb65bdbb13e | note | Approved by - Tech Mgr
cf5b7bc9-86a5-5601-af41-ea8123425a12 | note | Verification / witness: Supplier - W, R
17e5b110-1731-5258-a5fb-090d960b90b8 | note | Verification / witness: HOL - W
6c73d8da-8b23-545a-a7f6-47b7269c7026 | note | Verification / witness: Company -
3adf876a-d6b4-5fe8-b366-70210ea45d63 | note | Verifying document - Supplier test report
c7c2ec74-6ef7-59b4-989e-c3455cf0aa50 | note | Record Location - Tech Mgr office
d6ea75a3-9441-5015-88c4-9eb858fb7d9c | date | Date Completed:
0b9e8909-1ff9-47ca-948a-f3339329c1d6 | checkpoint | 4.3 - Particle Density & Water Absorbtion
dd920061-a60d-56e1-bb03-de880c7efb6f | note | Code / Spec Ref - AS1379.2.3
1e9b8f72-0598-5e9d-be5d-6bab30622be3 | note | Test / inspection method - AS1141.6.1, AS1141.5
739dbaa5-e143-5f7f-885a-22fdcdcd2b49 | note | Acceptance Criteria - AS1379.2.3
ca7536c1-a2a4-50c7-8069-5edfd58c667c | note | Frequency - 1 per 3 months
aa180572-4f03-5ce0-8b38-97d8eaaf3235 | note | Initiated by - Supplier
2c75d8f0-9eb1-53fe-bd1c-c314883a7ee3 | note | Approved by - Tech Mgr
452cc093-ec42-5a4c-846c-c8e837e7d310 | note | Verification / witness: Supplier - W, R
d7704e8d-58bb-53bf-a63f-a73da3a44fc5 | note | Verification / witness: HOL - W
db37dbc0-20a4-5a5e-bdb9-14c094e105e4 | note | Verification / witness: Company -
837d27e8-541e-5148-b677-e6905e98f134 | note | Verifying document - Supplier test report
9f7633c1-a1ec-5775-919a-30c3f7a57033 | note | Record Location - Tech Mgr office
5c240f65-c32e-544b-9257-fa81b62c8000 | date | Date Completed:
06e98540-1cab-40b8-85e9-0deb902673aa | checkpoint | 4.4 - Petrographic Analysis
e855bcc3-01c5-5051-86f7-a170413f5fbc | note | Code / Spec Ref - AS1379.2.3
a5a1e08f-007b-5eac-9aac-ec2578e0563f | note | Test / inspection method - ASTM C295
fa8f7394-839d-557b-907c-63a551301df7 | note | Acceptance Criteria - AS1379.2.3
83c1b91e-fb58-5f7b-9bba-fb245fb63597 | note | Frequency - 1 per 2 years
358f1ef1-e001-5d13-94ed-09093c8bb312 | note | Initiated by - Supplier
3d6eb783-82ee-5b27-bfb8-56a703c2e774 | note | Approved by - Tech Mgr
07861264-5199-515f-af5b-412e0b5ba11c | note | Verification / witness: Supplier - W, R
8f097f4e-ba9c-517d-bd26-bbe1aaa1dcea | note | Verification / witness: HOL - W
3a676df1-7e20-5218-9b7b-07b23f399ce1 | note | Verification / witness: Company -
bd7d7035-b7f5-58ea-a0ab-37d00493df18 | note | Verifying document - Supplier test report
159c93a6-92a1-5a25-b51f-81430f5a4bcb | note | Record Location - Tech Mgr office
4fda0539-34fd-5b59-bfd5-df0f566ced18 | date | Date Completed:
42f0f619-7b79-45a2-b23e-f64ab492b0fb | checkpoint | 4.5 - Sugar Content
8600aaa1-c6fd-58eb-a76a-bd087e951647 | note | Code / Spec Ref - AS1379.2.3
84832ebb-71eb-56c5-8d7f-766ff3d809bd | note | Test / inspection method - AS1141.35
b433c2d4-e502-55fb-a0b0-5f2cd97a600e | note | Acceptance Criteria - AS1379.2.3
eb26ce3b-ac28-5b74-9811-bc58db801733 | note | Frequency - 1 per year
3f906e54-1b9e-517f-8b63-6fa9974f3958 | note | Initiated by - Supplier
0122dd7e-6fa2-5e07-a0bf-bbf543eef85e | note | Approved by - Tech Mgr
fc01066f-c10e-5287-8cca-ba2594ffb3f6 | note | Verification / witness: Supplier - W, R
b622e21f-09b6-51e3-8a72-ff655913f630 | note | Verification / witness: HOL - W
ec4c4773-accf-5295-b3fd-684d4d7b379e | note | Verification / witness: Company -
c366cd37-a3c5-5920-8616-13543b256e28 | note | Verifying document - Supplier test report
9b8db1f8-d570-537c-980b-5b862025333f | note | Record Location - Tech Mgr office
69f4bafa-5820-54ab-97f2-5cd00ddf7029 | date | Date Completed:
7d76f84b-0be7-41f8-a32a-dea1046e8e54 | checkpoint | 4.6 - Clay & Fine Silts
b672ea4e-06a8-5d58-b5ca-eb8db359f158 | note | Code / Spec Ref - AS1379.2.3
64a39945-3dd5-52b2-98d1-25a61cef07b2 | note | Test / inspection method - AS1141.33
d3cbc6f6-beeb-5068-9d9d-979dd39aa4cc | note | Acceptance Criteria - AS1379.2.3
871c0dc6-70e6-5a6f-bfab-4d3711fcef08 | note | Frequency - 1/1000 tonnes
81843c1a-abbc-59f0-a5eb-0bc3e680b29f | note | Initiated by - Supplier
449618cc-37a0-59b1-ba94-d777af1d8d12 | note | Approved by - Tech Mgr
cf5fd661-bf27-54ba-98cd-7588246d297c | note | Verification / witness: Supplier - W, R
72320293-2db7-5750-b63a-b6098347fb54 | note | Verification / witness: HOL - W
2482b533-7703-5a9f-9d35-a5b8fb594b79 | note | Verification / witness: Company -
6a6c7254-8524-510c-8364-839fe45ac37a | note | Verifying document - Supplier test report
9b552528-b025-5608-bf95-8a7465e345a9 | note | Record Location - Tech Mgr office
e0e6842d-7550-5e08-9652-d696bd9cc4eb | date | Date Completed:
d9cd53bb-32cc-4407-9309-617159e9b43a | checkpoint | 4.7 - Organic Impurities
5161c61f-dcd4-5169-8d04-72fc82235d5a | note | Code / Spec Ref - AS1379.2.3
95494532-92fb-518f-80dc-a4042d710aab | note | Test / inspection method - AS1141.34
b0f2d7af-ded4-5e08-8ff7-a3849ed6102e | note | Acceptance Criteria - AS1379.2.3
d26135c0-61f6-5c20-8c17-4eccbce7b687 | note | Frequency - 1 per month
830624ad-97fd-5b84-9c21-3922e5bb27cb | note | Initiated by - Supplier
78857267-0631-5832-aad6-fd17b0d9f52a | note | Approved by - Tech Mgr
7be7e075-2280-5d2e-bdc1-3382df5b0350 | note | Verification / witness: Supplier - W, R
690b7cf1-61f5-5e18-9426-352586b28089 | note | Verification / witness: HOL - W
58705b69-dbdd-5e9d-8dde-7568763ecd77 | note | Verification / witness: Company -
70795400-5487-527a-8701-b902aabfc089 | note | Verifying document - Supplier test report
328abee1-4402-5fb1-80bb-9564fbeaa6a1 | note | Record Location - Tech Mgr office
6e5dd8bf-6205-5ea8-a53d-f2e752610998 | date | Date Completed:
9f04d081-0b0b-4ae3-af45-a04144b6fdf0 | checkpoint | 4.8 - pH Value
56f2d134-a7e6-5c8c-8f69-1a1464af6801 | note | Code / Spec Ref - AS1379.2.3
6a8a3800-e44f-55ce-bd88-0cccbd95ec58 | note | Test / inspection method - AS1289.4.3.1
b1ccb5b4-0755-51fd-b8af-5a46a55ecd5b | note | Acceptance Criteria - AS1379.2.3
9fd7e24d-98f9-5919-906d-53240467cfa2 | note | Frequency - 1 per year
b8dc4b55-5423-5dbd-ad94-e92ff8101f60 | note | Initiated by - Supplier
8845a840-848f-5636-a7c4-ec6a02c1618d | note | Approved by - Tech Mgr
b8af71a3-d20a-57ec-8268-3b81e318603d | note | Verification / witness: Supplier - W, R
58f4db40-8bfd-5774-9ac5-ae972e4ceddf | note | Verification / witness: HOL - W
d0bcbe4d-c059-596f-b251-17232551e0de | note | Verification / witness: Company -
f9d76d07-3470-51bd-ae49-81273530bc61 | note | Verifying document - Supplier test report
bca0a5da-6efe-5fc4-bfb3-0cac3fb0135d | note | Record Location - Tech Mgr office
a9605e53-c04e-57ec-8d06-549aaabae551 | date | Date Completed:
f3173211-2957-42f6-ba76-2671c221c52f | checkpoint | 4.9 - Reference Sample
18a7b16c-9934-5d17-887a-2c01d48f07d6 | note | Code / Spec Ref - BECA Cl 11.4.6.2
f55d8740-acc3-57c4-bdd8-eaa27f7d5b3f | note | Frequency - Once Only : 2 x 25kg samples of fine aggregate
89bd1f9a-225e-563e-8308-ffb084e13164 | note | Initiated by - Supplier
6675574d-9988-58c5-9258-8d628999d95c | note | Approved by - Tech Mgr
e3739c5b-e62d-5403-a5bd-265561b6a789 | note | Verification / witness: Supplier -
a5568099-95d5-519d-97ec-e8301d98610a | note | Verification / witness: Company - W
1e77db03-8f73-55f5-b4f0-5142a7d0f527 | note | Verifying document - Record only
de633890-e5f6-5a31-a2a9-377ab12aa5dc | note | Record Location - Tech Mgr office
8a073d03-11dc-52d9-9c1d-82f7801e6f95 | date | Date Completed:
bf1a24c6-0106-416f-950b-de106dee6f30 | section | 5) Water
e4958b36-5af1-486e-b025-504e4af7524b | checkpoint | 5.1 - Mains water
739f1a57-d6c3-5829-b3fc-67c7eba95a45 | note | Code / Spec Ref - AS1379.2.4
9c1aac09-c3ed-5038-96dc-c8d9c654828f | note | Acceptance Criteria - Main complies
1a48c4bf-0c18-5e7a-8428-0dccda502dd5 | note | Frequency - Nil
302bff83-a342-5613-b8f7-f283c3bfc9b4 | note | Verification / witness: Supplier -
708bd87d-1d39-5671-be1a-485e77e1a279 | note | Verification / witness: Company -
5c1261fa-bbfa-505e-a14a-0549c977b3fe | date | Date Completed:
a5e0eff7-dbe0-4141-ba6f-9d54b1dcb4a6 | checkpoint | 5.2 - Non mains water
0d7fbfe5-c3ce-58db-b635-76054b34aa32 | note | ~ Sugar
47cab301-998b-5630-a401-3b86738800a8 | note | ~ Oil & grease
4bf50379-2c7f-5306-b773-cc8c29bfd6c7 | note | ~ pH
6e36a87e-91c4-53a1-a938-967ae61edf3f | note | ~ Chlorides
de14b083-c518-5ac0-a9c4-c58ec7014128 | note | ~ Sulfates
2f254903-e15d-59ee-bed1-ebe7a94affbc | note | ~ Total suspended solids
56c067a6-c169-52c8-a97d-b47e0ff09017 | note | Code / Spec Ref - AS1379.2.4
a99c7530-35f5-53b9-a3a5-c6d411992ae3 | note | Test / inspection method - AS1141.35 APHA 5520 AS1580.505.1
c2c1a316-786e-59f9-a606-d331d89a5ead | note | Acceptance Criteria - 100 mg/L max
08eb84fd-635d-5849-acc4-9a724549c3ab | note | ○ 50 mg/L max
a7efaa1e-d8b6-5cee-880e-69abc504530b | note | ○ > 5
c28aa2b0-c947-5e7b-a546-c5f43b602a6b | note | ○ 500 mg/L max
be3c79eb-0730-53b2-be56-e8bad243b8bc | note | ○ 500 mg/L max
d9c4adf5-5bbd-5186-b475-e043bc1e9a66 | note | ○ 2000 mg/L max
6ff2960e-92aa-5575-82c3-31a1bae9bdf0 | note | Frequency - 1 / 6 months
3e83e77d-558a-5fce-9cdd-e45f9d8b1d91 | note | Initiated by - AOM
532b1225-d4fc-552e-8795-9f6621ee3a42 | note | Approved by - Tech Mgr
3990ee8c-dcce-5241-8e4b-48d16c466f91 | note | Verification / witness: Supplier -
2f2f7e12-6fd9-5b8a-9634-cf7b3d134657 | note | Verification / witness: HOL - W
947d78a7-ed4d-59dd-8ed0-bd752821a278 | note | Verification / witness: Company -
d367d6c3-7163-54d5-965b-5988967773fb | note | Verifying document - Lab report
89084002-7431-5b60-aeec-ae7f705223e2 | note | Record Location - Tech Mgr office
9b7da4ba-77a8-5ace-8e25-0425c8bf4f62 | date | Date Completed:
bee1cb3c-fbd4-4d98-bcdd-ffb71d631ce8 | section | 6) Admixtures
8e866bae-dbdb-4482-9bfe-fe14d9341d43 | checkpoint | 6.1 - WR Admixture general acceptance
32ef3038-b2c1-578a-b2c8-6694085d868a | note | Code / Spec Ref - AS1379.2.5
e017325c-d848-56be-b333-61bc6d70f0b8 | note | Test / inspection method - AS1478.2
27d4abdf-a1c4-514a-82ac-a06df84e52ea | note | Acceptance Criteria - AS1478.1 Table 2.1
548e1033-e7f8-5bbc-9441-4c40e02b4eb4 | note | Frequency - Initial
d8b661cd-9100-5050-82e3-69cd69a929f2 | note | Initiated by - Tech Mgr
5fecc664-07bb-578f-9bb1-00249a8a8bf0 | note | Approved by - Tech Mgr
53d4bfbd-a9a8-53e2-8ad3-e0725986c153 | note | Verification / witness: Supplier - W, R
9cc5e599-54af-5c7c-b721-f436b15681df | note | Verification / witness: HOL - W
7cdfa390-80cd-5b82-9cff-e7fe73e6c7e6 | note | Verification / witness: Company -
fde02f4d-a38b-5603-9fb7-2b2b54215e6c | note | Verifying document - Supplier report
776cb84a-69fb-51fe-ab89-556b762b5b3f | note | Record Location - Tech Mgr office
4c92f3e5-b31e-5d63-9ffb-1ca5e021d092 | date | Date Completed:
c17536c6-7ad8-4161-a7dd-29cfe776155c | checkpoint | 6.2 - WR Admixture Uniformity test
2c96429b-7f7e-5f06-a32b-0ca65a94f24a | note | Code / Spec Ref - AS1379.2.5
2c33913d-50e1-5756-bf33-6edb9c8ed1b2 | note | Test / inspection method - AS1478.2
13ab7c5b-6508-572e-9cca-329274694d39 | note | Acceptance Criteria - AS1478 Cl 2.1.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.02), Non-volitle content (+/- 2%)]
fec106eb-ec39-5813-b403-ea3e51a1af50 | note | Frequency - MBCC Supplied (Each Batch)
ac27d7f1-b1ba-53bd-9193-c9d0fd57aac4 | note | Initiated by - Supplier
e4ea178a-8e9b-5569-92ee-c234b6aea117 | note | Approved by - Tech Mgr
a5eae0a1-642f-5aa2-a3b4-4721cfe67ba8 | note | Verification / witness: Supplier - W, R
7c61e25b-4b9e-5de4-8a9d-053dfbe310d5 | note | Verification / witness: HOL - W
f634618f-5e9c-5b35-87e2-1548c067c3fd | note | Verification / witness: Company -
6b310bec-dd12-5009-989c-a1adcca405d4 | note | Verifying document - Test Reports
c3b2942c-9a41-54fc-ad52-bbac9ad78fa5 | note | Record Location - Plant
13d3f9b3-5b4a-538d-81e8-40d63d377249 | date | Date Completed:
3677ac7b-a4ca-479c-b299-e4ed16fdf049 | checkpoint | 6.3 - AEA Admixture general acceptance
fbce964f-1cfd-5107-8bc8-8fdefbc6d69a | note | Code / Spec Ref - AS1379.2.5
d56e860a-5276-501a-8505-adea39917cdf | note | Test / inspection method - AS1478.2
410ea710-5bea-509f-aa4f-c68f36291e2b | note | Acceptance Criteria - AS1478.1 Table 2.1
0784fea4-6565-582a-b9da-73354ba0f81d | note | Frequency - Initial
0c1e90ea-0f71-5e19-bafb-4c38e2ea49fe | note | Initiated by - Tech Mgr
6a5784e4-0abc-5ea3-9419-610d3dd4931d | note | Approved by - Tech Mgr
7f52bebd-ac54-5711-8e2f-3cd3b6a309a6 | note | Verification / witness: Supplier - W, R
45eb6dde-dea7-5cb6-a70f-6edb25a963d3 | note | Verification / witness: HOL - W
154437f7-f37f-5ff2-905d-db3aa8b8a7bd | note | Verification / witness: Company -
17ab35b9-9666-59b1-ab2d-34d5580b9ae1 | note | Verifying document - Supplier report
7a2898a4-837a-53e2-aa5a-a2daa226db39 | note | Record Location - Tech Mgr office
0dfa31e7-6d19-541b-a653-1b5cfbf20d8c | date | Date Completed:
68ea1408-52cd-41a9-8f92-700b5f1177e9 | checkpoint | 6.4 - AEA Admixture Uniformity test
768545db-b25e-54df-99ec-1ba4c59149d4 | note | Code / Spec Ref - AS1379.2.5
1d859487-c514-5ba8-a84a-188ebdc00426 | note | Test / inspection method - AS1478.2
01944d28-b580-5795-90d3-ea8b4ce4e9f5 | note | Acceptance Criteria - AS1478 Cl 2.2.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.01), Non-volitle content (+/- 1%)]
e38cfe13-3b6f-5153-b648-fe59e662ae48 | note | Frequency - MBCC Supplied (Each Batch)
149c03b5-05d3-5ad4-986a-183e16824b5e | note | Initiated by - Supplier
e13aec75-a0c6-52c6-a861-33f12da6b6ad | note | Approved by - Tech Mgr
a2432470-f9ef-5b01-b1ac-2876cc12d7b4 | note | Verification / witness: Supplier - W, R
44155c7c-1adf-53b7-9f61-0ca66cfe69cf | note | Verification / witness: HOL - W
fa80b449-a508-5c99-8067-340238a4138b | note | Verification / witness: Company -
44612794-0a2d-5c7c-9d77-98544694ecd7 | note | Verifying document - Test Reports
821ce458-c0de-5a9b-8070-5f367babf404 | note | Record Location - Plant
a7eac26a-2e36-52a8-9a0e-a2e0c5da0da3 | date | Date Completed:
7885c182-92fa-4d9c-8284-ca8dc0aea61d | section | 7) Transport
2025ed9a-440c-45ac-959c-3b46641c5fb4 | checkpoint | 7.1 - Agitator blade inspection
0154cb5f-044e-5adb-8d26-2b17f9b3f064 | note | Code / Spec Ref - HOL QMS PN6.1
4c66916e-4dd6-5472-8225-7ed70b32fb26 | note | Acceptance Criteria - Concrete Barrel Solution - No excess buildup, No excess wear
f8cb1f7b-f014-5eca-ab14-35ad04c8781a | note | Frequency - 1 / 3 months
0bd6d022-3a40-5cf1-a4fd-c74222c60ae9 | note | Initiated by - PS
578c5f96-41de-594b-874c-6c933302d006 | note | Approved by - AOM
8f372499-cd98-5674-a730-0049322f439d | note | Verification / witness: Supplier -
965221ca-0b26-514b-b825-5a08ec59a134 | note | Verification / witness: HOL - W
60a21f04-3371-5fae-b9ed-94dd11c67075 | note | Verification / witness: Company -
07058526-ae29-5d1d-8e1b-66d4dc1990fe | note | Verifying document - Inspection report
33d32fd8-2585-58e6-a97f-b78c6d2aeedc | note | Record Location - Plant
72829e5f-45f0-54a3-b932-05d8b1ed1fb6 | date | Date Completed:
eba9820f-0ec4-4fa6-9f86-0a4c24f21205 | checkpoint | 7.2 - Mixer uniformity test
11b82338-3d53-50b7-8033-497387529f5b | note | Code / Spec Ref - AS1379 3.5.1 (a)
e2364057-d541-54b0-9eee-afc4da035004 | note | Test / inspection method - AS1012
00d60fda-a8cd-5adb-8215-0de259032427 | note | Acceptance Criteria - AS1379 Appendix A Table A1
9e532a9a-337d-50e9-9a24-93c9729cb56e | note | Frequency - Initial for agi type
807626fe-ed64-52e8-9892-9637d88c262a | note | Initiated by - Trans
19c89b18-5b56-5bb3-b40e-ecfbcdc29f6c | note | Approved by - Tech Mgr
75b2fc1e-4532-5976-97b0-57af251ababd | note | Verification / witness: Supplier -
be6a21f8-3a5a-5cfe-9992-b45f3ce95497 | note | Verification / witness: HOL - W
2447e2f5-5480-53b9-8dde-bbfbee0193e6 | note | Verification / witness: Company -
c9f02420-9128-5266-9f24-660b3693d41b | note | Verifying document - Manufacturer report HOL test report
bc113c25-9c7a-56e7-b459-716193e1c06b | note | Record Location - Tech Mgr office
96027749-61bb-568d-bc85-cdd4478538b5 | date | Date Completed:
87901550-6417-4b8e-8442-3b1539f23c56 | checkpoint | Final Inspection
6991fea1-3028-55b4-9395-ecb1e4d1da0d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
20dfdf9b-e685-541b-9396-f33c964fd08c | textbox | Print Name:
e3cff430-b5a2-5528-82ca-020210bae7b9 | textbox | Position:
ef54da13-444d-52b8-8e14-4f34e0a2a092 | date | Work Completed On:
20576092-0f9b-5cec-87f2-cbce8fdc3611 | date | Date:
e6b8a30d-eb8a-5bbc-8c38-65aad60ce48a | checklist | FH-ZU2-QU-ITP013 - PCC Pavements - Rev 2 | itp | ITP013 - PCC Pavements
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
2907e598-3fa6-573d-bd16-0574524c85dd | note | Frequency - Prior to commencing works
b9918449-71ab-57a3-8fb9-16b7aa22b72c | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
e00f65c1-9d2f-5be2-a812-fb0d735c5f0c | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fcc655b9-fbb7-56a9-a250-a3e6ddfcdac9 | note | Reference Documents - Current Revisions in Aconex or ACC
7c8e2404-1102-5ee8-a17e-bf5965da5090 | note | Inspection/Test Method - Verify
bbf512ae-8c96-50fe-ab8e-041fb46b2033 | note | Record of conformity - This ITP signed
50155e9b-2035-554f-a3b9-dc1292319b1d | note | HP*
c857cb14-757e-552e-a08f-8d2f33488cba | note | Responsibility - Project / Site Engineer
7985f0ba-6f2a-53e3-86b8-8d2bb4b8fa9e | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
f76991b4-2e34-58da-a5a7-07c02f17fe3d | note | Frequency - Prior to commencing works
c651df4c-8e29-5d2d-9375-da49ffe74cdf | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b636c8-8a77-5c74-8d2b-2a67f6f57838 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
396ec348-d33a-5b4c-8f22-e1c5c2acb765 | note | Inspection/Test Method - Visual Inspection
7cf37097-e48c-53c0-8bbf-4d645002a09d | note | Record of conformity - This ITP signed
811f2fa4-250a-5ede-9e06-77ba08912d60 | note | HP*
3d378ac4-0b26-56cd-9c2f-4fba1d62a6ed | note | Responsibility - Project / Site Engineer
91cced02-0c77-52ba-9865-19bd3dc69329 | date | Date Completed:
7e28438e-f51f-55d2-9f71-e8c9c5437afc | checkpoint-no-value | 1.3 - Mix Design Report Submission and Approval
4507ccca-25f6-5ce8-996e-f117534195a8 | note | Frequency - Prior to commencing works
5b39bd65-bb88-5915-86f4-2d1b0165bfb7 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results submitted in a report to the Contract Administrator for review and acceptance prior to full trial mixing.
98bbfa8e-9bff-5a20-994c-001991a18233 | note | Reference Documents - Beca Spec 002 - 11.5.3
85cbfe58-d6b7-5804-b260-f5c730fa1f47 | note | Inspection/Test Method - Verify
a862afaa-1ec6-58ad-b24c-6eacb2fca986 | note | Record of conformity - Aconex Reference
cb6a07a3-cb1d-5b7a-a016-a5b1ac8a4d5b | note | HP
ab6e881a-aab1-5c9a-9521-b29a5139afc2 | note | Responsibility - Project / Site Engineer, Principal’s Representative
2d313683-5885-50c2-9eb2-66762b61c470 | note | Date Completed: 01/06/2024
3211cacc-9c39-5b9a-9514-0f07b88fe014 | note | Principal's Representative - BecaCPL-GCOR-000846
05fade62-fb69-5838-88b0-d4e2cca8452e | signoff | AUTHORITY HOLDPOINT
1d417a20-1781-524c-8f26-32728ee4d344 | checkpoint-no-value | 1.4 - Job Mix Formula
8b89fdfc-d9d1-527e-8a5a-973029e07bae | note | Frequency - Prior to commencing works
7614f9ac-8801-59ee-a747-c145e86ec76c | note | Acceptance Criteria - The Job Mix Formula must state the mass proportion of all ingredients per cubic metre of concrete. The allowable limits in the Job Mix Formula (when compared to the agreed theoretical concrete mix design) must be in accordance with Table 11-2 of BECA 11.5.4 (see notes section).
57149b72-6f59-5d04-86e7-4525b9b35b55 | note | Reference Documents - Beca Spec 002 - 11.5.4
b51a7841-f170-5d47-8f36-c8cd85564a64 | note | Inspection/Test Method - Verify
503bc281-5ed7-58d1-aa06-fb549f758ad5 | note | Record of conformity - Aconex Reference
93011ee0-68cc-5e96-bafe-17d75aa2198c | note | WP
5375edff-176c-5d66-988f-1c14a5004c0b | note | Responsibility - Project / Site Engineer, Principal’s Representative
71a389be-f505-5ac1-9f06-a680d8c8848e | note | Date Completed: 30/05/2024
e0d8cbf6-790b-5a21-8182-cc284a5187fa | note | Principal's Representative - BecaCPL-GCOR-000839
ea2ed3cc-4240-5302-a62f-08cf18713d1a | checkpoint-no-value | 1.5 - Production and Construction Trials
e5fdbc46-719d-5942-8304-c39bd3e2059a | note | Frequency - Prior to commencing works
19475a37-83f9-5590-bea2-9dc4e0ea4477 | note | Acceptance Criteria - A production and construction trial must be completed as per the requirements in the specification.
1b130452-3c22-5b57-96d2-d425c83968d6 | note | ○ The results, control procedures, construction methods and completed trial pavement will be presented for review and approval by the Contract Administrator.
468ed8d3-72e9-5e5e-9e7c-4cd84000cb62 | note | Reference Documents - Beca Spec 002 - 11.6.1 to 11.6.4
4077b7bd-82bc-5ac9-8abf-482efd9b2c4b | note | Inspection/Test Method - Verify
df708af5-9f11-534c-af7d-32a465b86af9 | note | Record of conformity - Aconex Reference
528f6782-a3f3-5bce-bf62-414e8a0aa3b5 | note | HP
08bcb58d-ea03-5f6c-8d87-068ee9a666c4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a044b821-045c-516d-806b-4adbf19eae93 | note | Date Completed: 19/08/2024
3f498654-9c27-5215-b0b9-26044de9c986 | note | Principal’s Representative: DCWC Mgt-GCOR-009917
73453e67-147f-57a2-8c4e-a327bf10ac4a | signoff | AUTHORITY HOLDPOINT
e5f4e390-d859-5bb8-8754-88a6610c4a41 | checkpoint-no-value | 1.6 - Curing Compound Material Submission
9b855dfe-dcaf-5780-a60c-3107674b9ed2 | note | Frequency - Prior to use of curing compound
83186ab9-3183-5a0d-8af9-d95cee37cc97 | note | Acceptance Criteria - Membrane curing compounds shall be a white pigmented type confirming to AS 3799, Type 2. Wax based compounds shall not be used.
f420a157-3565-5505-8230-a10228b203ee | note | ○ No compound shall be used without written approval by the Contract Administrator.
25cd7b38-ee48-596d-b07d-17fa9f379210 | note | Reference Documents - Beca Spec 002 - 11.4.11.1
60e9e8c5-b8ed-5bd9-a26e-3382693460cc | note | Inspection/Test Method - Verify
c0fd41e0-1e99-5cb1-b48f-4c618b1231d9 | note | Record of conformity - Aconex Reference
725ec045-95ca-572c-9b4e-9c371e3ec53f | note | HP
f35c5635-fb93-5f33-b60d-c63641ec0278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
696d3ed0-b889-5758-aec5-19902ec4d780 | note | Date Completed: 22/05/2024
a818c49e-eaec-5a25-8530-c20a4d5b18bd | note | Principal's Representative - BecaCPL-GCOR-000791
cae769b2-61e3-5ca9-9808-11d45f78e1b4 | signoff | AUTHORITY HOLDPOINT
ba929a80-28cc-56d4-987f-a6898a2999b4 | checkpoint | 1.7 - Impermeable Blanket Material Submission
761302c5-7075-519c-9d7b-694b9d82823c | note | Frequency - Prior to use of impermeable blanket
b5091c95-16c2-5ef1-a417-df9805b7c0ab | note | Acceptance Criteria - If required to be used, impermeable blankets shall comply with the requirements of ASTM C.171.
db67cc05-0893-5f00-99ff-d92e8f8fca9b | note | ○ The blankets shall have sufficient strength and weight to meet the required conditions of service and shall be approved by the Contract Administrator before use.
46bd5aaf-a712-5584-9956-c7ddf7e3671b | note | Reference Documents - Beca Spec 002 - 11.4.11.2
40d7a594-43f0-57e3-8f8e-430fd5f4061f | note | Inspection/Test Method - Verify
6af78c57-3fbc-5181-a1c9-23ad09bdf0ba | note | Record of conformity - Aconex Reference
bb338aed-f7e8-569f-995d-e97baa3ee2b6 | note | HP
4768e536-db22-57da-8f25-3e8dfeda92eb | note | Responsibility - Project / Site Engineer, Principal’s Representative
fdd17bfc-d0c1-55b5-88b6-5f825b05769a | date | Date Completed:
6c2414bf-bba4-528f-9da8-08464c25f39d | signoff | AUTHORITY HOLDPOINT
5885abc0-a77e-5d54-803d-3fd1515e6818 | section | 2.0 - Pre-Placement Activities
16ee8263-a125-5876-ab26-79db8c104fdd | checkpoint | 2.1 - Formwork Installation
65a8de96-f184-5a0b-af0f-2fd24a991fb5 | note | Frequency - Prior to placing concrete
1f1a7b28-fea3-5aa9-b6c2-a714d1d257f5 | note | Acceptance Criteria - Formwork must rest firmly on the base to eliminate gaps and ensure no leakage of concrete will occur during placement.
a5ca7930-6074-5fd1-9a44-03273fc974f8 | note | ○ Formwork must be secured into position and locked together during placing, spreading and finishing of the concrete.
1e88b2e3-5eaf-5da0-8afd-bc24150e6b21 | note | ○ The top of the form must not deviate by more than 3mm from the required level.
2f868783-cb5a-598f-8cfa-65f1caec0add | note | ○ The form face shall be vertical and not vary more than 6mm from the required alignment.
31c77cba-682b-53dc-87ae-5baea14f37a7 | note | Reference Documents - Beca Spec 002 - 11.8.1.1
6ef34b37-ea17-5ff3-ae4b-e99491dfaaaf | note | Inspection/Test Method - Visual inspection
a9ebca94-422a-50d0-83cf-12869d540e0b | note | Record of conformity - This ITP signed
f249917f-23af-5d15-86c4-a29b6426d2d9 | note | WP
5b8afdc5-c63f-53f0-a861-23a7b328949e | note | Responsibility - Project / Site Engineer, Principal’s Representative
7409513b-e0b7-52ca-8954-8936dd8759d3 | date | Date Completed:
fd1f1b65-94f0-536d-a050-a134453028a2 | checkpoint | 2.2 - Pre-pour checklist
ab32c07d-9a9d-53ce-b9b5-123154b34553 | note | Frequency - Prior to placing concrete
18c8a68c-2470-5f7a-a086-63658f6c6540 | note | Acceptance Criteria - Completion of the pre-pour checklist: CL013A – Pre-Pour Checklist which details various checks required for formwork, reinforcement, joints and the pour area.
b28cd113-7abb-5137-9cf8-2b694ff03494 | note | Reference Documents - Beca Spec 002 - 11.8, 11.10, 11.13
be572c26-123b-5025-998f-2abc96f9640b | note | Inspection/Test Method - Visual inspection
d984894d-908e-5b6f-ad12-8ad9faed8fba | note | Record of conformity - CL013A, This ITP signed
d8b6310c-914c-575c-865b-9033ff0b5181 | note | HP*
7a14446c-e20a-5723-ad87-0f7c48d3e202 | note | Responsibility - Project / Site Engineer
ae723b76-57c3-5197-94af-ab6ad7d4b3a6 | date | Date Completed:
ca0fa0ec-49b6-5c2d-9237-de158062e778 | checkpoint | 2.3 - Pre-pour inspection
0d5d906e-fcbc-570f-9189-0a7d6e0ee14a | note | Frequency - Prior to placing concrete
36f2b982-f113-5f64-af91-09c84a5c2070 | note | Acceptance Criteria - The area in which concrete is proposed to be placed shall be inspected and checked immediately prior to commencement of placing.
95f8d6ff-6ebc-58a5-82a5-cc48c697c8d9 | note | Reference Documents - Beca Spec 002 - 11.9.1
ec12b8e5-7bac-50e6-a482-57ff3e913491 | note | Inspection/Test Method - Visual inspection
4a0db4bd-ded3-57d5-a929-3ed0243e8d0e | note | Record of conformity - This ITP signed
851d29f9-48e1-59c4-915c-64990356ff5b | note | WP
74492460-66c9-548e-ae28-8c4b837302a0 | note | Responsibility - Project / Site Engineer, Principal’s Representative
39c274b1-0ec0-570d-bc94-d540fdbfb401 | date | Date Completed:
d9388486-1250-5ff8-b9ad-8d44105f357b | checkpoint | 2.4 - Weather Forecast Checks
d43c1ab9-5201-5007-b19e-cb14e0ad0be0 | note | Frequency - Prior to placing concrete
0a8b717f-0ec7-5292-8236-466654675c31 | note | Acceptance Criteria - Check the weather forecast for unfavourable conditions (rain, wind, hot weather or cold weather) on the day prior and immediately before confirming
ed0bef5e-c778-5d14-9786-2791f8899413 | note | Reference Documents - Beca Spec 002 - 11.9.5.1
c980c01d-b749-5c67-a48b-015656e8fe01 | note | Inspection/Test Method - Verify
5740e4c3-89c1-5bdd-a073-809a08fe31b8 | note | Record of conformity - This ITP signed
a2371590-dbcb-552a-9f00-aa021e745a5c | note | HP*
20538a2e-8184-5d34-a5e7-dbca391524b0 | note | Responsibility - Project / Site Engineer
10ba42c8-0df4-561f-89da-75552b10f2ca | date | Date Completed:
cd1921f5-0447-55dd-a906-346b6c56d7e0 | section | 3.0 - Placing Concrete
4ce1dbde-921b-5f12-92f2-cb172108eb2c | checkpoint | 3.1 - Place, Spread and Compact Concrete
7665b879-a2be-524d-ac3e-ecf0582e021e | note | Frequency - Each concrete pour
723f9130-2ba8-5f32-8090-706d2a025af7 | note | Acceptance Criteria - Concrete placement must be at a rate appropriate to achieve a consistent high quality resulting pavement.
80257cee-5638-514e-a8ff-24d1c99ba788 | note | ○ During placing, the concrete must not drop freely by more than one metre onto the base of the paving lane.
ede5d52d-6d18-5925-a3b4-ed8eb0fbe3a1 | note | ○ Concrete shall be placed uniformly over the width of the slab and in a way to minimise segregation.
fb7bb21a-0517-5585-8cba-f749e3db01cb | note | ○ Concrete to be adequately compacted by internal mechanical vibration.
47ad46e2-d1bd-59d1-992d-bbe52b4d9cbd | note | Reference Documents - Beca Spec 002 - 11.9.1, 11.9.4, 11.11.2.1
638de61b-8375-576b-9262-504c09b1a131 | note | Inspection/Test Method - Visual inspection
39a74bcb-e849-515c-9206-afe7bbf2cd12 | note | Record of conformity - This ITP signed
73d72013-09b1-5d43-9fe7-bab4cde0554c | note | IP
bc0e21bc-775d-5d51-b0cb-529089e2bd84 | note | Responsibility - Project / Site Engineer
4fad147d-594c-5d20-96cf-f52b3f9b9d35 | date | Date Completed:
01340969-6666-50d8-81f7-9de3ba0476a1 | checkpoint | 3.2 - Concrete Deliveries
8246b40e-a538-5ae2-a7e5-ff27722c2f97 | note | Frequency - Each concrete pour
ff9bb630-b1de-5601-afdb-7766627168d9 | note | Acceptance Criteria - Each concrete delivery to site is to be recorded on CL013B – Concrete Pour Record Sheet.
c719bd61-97e4-5c4c-84ed-af3fe5c02149 | note | ○ Concrete shall be placed within 90 minutes from the time of batching and before the concrete has attained its initial set.
fb71dde1-c897-5894-867b-60edb818ef6e | note | ○ The pour location, direction and order to be recorded on CL013C – Load-Batch Traceability.
04107314-7b34-53c4-8165-e6655e2e25de | note | Reference Documents - Beca Spec 002 - 11.9.1
1ad59df4-04e9-5aaa-acc6-fcecf0a20d1e | note | Inspection/Test Method - Verify
3945ca57-c77b-5137-bdc3-c380e553e0df | note | Record of conformity - CL013B CL013C, This ITP signed
b03e5d32-467f-5422-9751-5cd135c27c28 | note | IP
45e148b9-6d9b-5f88-a000-ad7e6419a0c2 | note | Responsibility - Project / Site Engineer
ba507cfd-70e3-534c-bfd9-36d529c0cfe7 | date | Date Completed:
a8846c82-3dab-5b97-8463-d576a7c411cc | checkpoint | 3.3 - Evaporation Rate
620b32c5-666d-5ac5-9d40-c190badf7dab | note | Frequency - Each concrete pour
65d8d07b-bb3e-5b85-89c1-9dcc1f61a1be | note | Acceptance Criteria - Concrete must not be when the evaporation rate from the surface of unprotected concrete is in excess of one (1) kg/m²/hr.
5245a27c-ae3a-572e-82a2-c0a5168e075d | note | ○ When the evaporation rate exceeds 0.6 kg/m²/hr, precautionary measures to prevent plastic shrinkage shall be taken.
1f0914c8-b9e4-5490-8cb3-4394352605b4 | note | ○ Evaporation rate to be recorded on CL013D – Rate of Evaporation.
a658725f-486e-574f-83ff-b8cc2eb40700 | note | Reference Documents - Beca Spec 002 - 11.9.5.2
1f4e2277-f1ef-5141-bc8f-dd05fc26f7a0 | note | Inspection/Test Method - Verify
f76b01c6-bd98-5ff3-9e87-82bc36a34708 | note | Record of conformity - CL013D, This ITP signed
3e4d1077-a8f0-5a0f-9fa6-30268bc119ef | note | IP
acaccec8-ef2c-51a4-a20c-aef89753f903 | note | Responsibility - Project / Site Engineer
cb08b5a5-0abd-51b0-8c20-fdbdb49bb359 | date | Date Completed:
6bde1751-12a1-5704-bd61-b45ba632ac70 | checkpoint | 3.4 - Hot Weather Concreting
744e946e-f126-5621-9e7e-a4972f3ef9ba | note | Frequency - Each concrete pour
a1e7bd7d-1f73-5185-bd3f-77e0967bec30 | note | Acceptance Criteria - Undertake additional precautions when placing concrete in hot weather.
7d9e13d6-291a-5804-8258-3aaced05a93f | note | ○ Ensure the concrete is placed at the coolest temperature practicable – the concrete temperature should not exceed 32°C.
78f48efa-0ae5-5dc1-8f31-3313b3109889 | note | Reference Documents - Beca Spec 002 - 11.9.5.3
d831f3f8-c332-5686-bda4-38c911c66549 | note | Inspection/Test Method - Verify
10d0b85b-3d61-5194-8f9d-e39d2c381564 | note | Record of conformity - CL013B, This ITP signed
4807115e-733f-50c1-b298-52829bceea88 | note | IP
37c77533-2901-5453-b540-56df0c72adc4 | note | Responsibility - Project / Site Engineer
60155a52-54ab-55ff-9c03-8d923452d239 | date | Date Completed:
0a674bc7-9c0b-59d4-b89b-165fe5156d0a | checkpoint | 3.5 - Cold Weather Concreting
b46d4377-743b-5e2c-9a62-72656b686c51 | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
7fe02ad8-3085-5f3a-ad2a-0d86841ffc75 | note | Acceptance Criteria - Cold weather concreting applies when placing concrete when the temperature of the air, aggregates or water is below 10°C.
d01a9e14-2976-5bf7-af7e-f001c89aa7a4 | note | ○ Placement of concrete can only proceed if the ground temperature at the concreting site is greater than 5°C and the temperature of the concrete is not below 10°C.
14bec05b-75b6-5cbd-8313-7107a72b00fb | note | ○ Refer to checklist CL013E – Cold Weather Concreting for ground temperature records.
2c83eea4-ede8-58de-8a96-8fdc2ca50a2d | note | Reference Documents - Beca Spec 002 - 11.9.5.4
5400d6da-e277-5552-934d-295719475b4a | note | Inspection/Test Method - Verify
0cf4e0f5-f7b0-591c-a4bc-a74cc1925e3f | note | Record of conformity - CL013B CL013E, This ITP signed
f7ee5f93-57e9-570b-80b5-7e193fd5587f | note | IP
4121e0e9-6a3c-5dea-90e4-8dea93d0437c | note | Responsibility - Project / Site Engineer
16188178-5de4-56d5-bf57-fb2443ec071b | date | Date Completed:
bce17218-2b32-50e2-99bf-8851b7031e92 | checkpoint | 3.6 - Concrete Surface Finishing
b26ed40c-f7fe-5c69-a471-0ad5980c219a | note | Frequency - Each concrete pour
3dd3cb8a-4d02-5a4b-a302-32045875d4e6 | note | Acceptance Criteria - Finishing operations shall compose transverse finishing, longitudinal straight-edge finishing, floating and broom finishing, in that order.
53be0521-6bdd-50fc-b99c-5d2a91eb7f37 | note | ○ Finishing operations must be started immediately after compaction of the concrete and completed as soon as possible but not later than 90 minutes from the time of batching and prior to the concrete attaining its initial set.
2ba31877-3f8d-5551-bf43-08e177e81c36 | note | Reference Documents - Beca Spec 002 - 11.11.2.2
e09b32d0-416e-5346-9c9b-1220537934c9 | note | Inspection/Test Method - Visual Inspection
6e7e4584-a8b0-595f-a24d-de612f1127a2 | note | Record of conformity - This ITP signed
ad934164-50ae-59cb-98b2-675b58179b25 | note | IP
699e0910-0d47-5413-9c83-c52b19be34c6 | note | Responsibility - Project / Site Engineer
6abdad8c-dc11-55fd-8218-36822687b6ab | date | Date Completed:
d4da5116-30ab-56c9-b1eb-849f5003fc96 | section | 4.0 - Sampling and Testing Concrete
43ff8655-1595-5766-8438-ea3569c93eaf | checkpoint | 4.1 - Slump
e7dc755c-ff25-50ee-96af-ff0dab3dcd19 | note | Frequency - 1 test every 2 trucks
9fbac8e6-40ae-5a64-ae00-e85f95490dd9 | note | Acceptance Criteria - 60mm +/- 10mm
1e1c2738-c8ef-566d-b4ef-c0a06b1b95d1 | note | Reference Documents - Beca Spec 002 - 11.24.17, BecaCPL- GCOR- 000846
631b6b02-f4ee-54f6-aab2-f4606e4be2b8 | note | Inspection/Test Method - AS 1012.3.1
6e0d6122-3d83-517b-9fb4-9810dfb73c77 | note | Record of conformity - NATA Test Certificate
3799165a-793c-5f52-9e99-1bc8e66aa85d | note | TP
f33f7e7f-5c6b-5a6f-90b3-368d440763fa | note | Responsibility - Project / Site Engineer, Laboratory Technician
edc8ffe1-57f1-5325-886e-40e630995883 | date | Date Completed:
df8751f1-b783-5ced-bb43-a84f6efb9e3e | checkpoint | 4.2 - Temperature
0c42cd12-866c-585a-869b-e826adc3da04 | note | Frequency - 1 test every 2 trucks
92d7b2a7-237c-52b8-badd-e661cea05acb | note | Acceptance Criteria - Minimum 15°C (except in cold weather concreting where minimum is 10°C)
1ac66703-6f4b-5503-a481-2cd5bf33c432 | note | ○ Maximum 32°C
065863ac-e20e-5236-a611-2c120f585201 | note | Reference Documents - Beca Spec 002 - 11.24.16
867d37cd-753b-5c5e-baa0-37d9c5934684 | note | Inspection/Test Method - AS 1012.3.1
ecc7394e-9e35-58b5-b477-c08cd31a0447 | note | Record of conformity - NATA Test Certificate
be4204fb-85e0-5c77-a84d-bf595ef132ea | note | TP
0b169908-fbcd-530e-a69b-735905db5c2b | note | Responsibility - Project / Site Engineer, Laboratory Technician
dd04c20d-b5c7-5091-8993-9cb5aee071da | date | Date Completed:
2ffe1a6e-8b66-57f5-bbd8-0c2e46eccdea | checkpoint | 4.3 - Flexural Strength (7 day)
506d83af-a213-50cf-bd4c-086b494c9637 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
d1c99a14-cafa-596a-96d4-30a78dab4373 | note | ○ After 5 lots: 1 Beam per 75m3 or part thereof.
4a796ae1-7593-5083-acbc-16b5ce896c8d | note | Acceptance Criteria - Results for information only
f079ae4f-0da6-55dd-8f57-d175df0f1741 | note | Reference Documents - Beca Spec 002 - 11.24.10
6f6c0f31-b5d0-51b0-b720-0309c7e52034 | note | Inspection/Test Method - AS 1012.11
909c13bc-855e-5784-919c-3711ccbebb19 | note | Record of conformity - NATA Test Certificate
85fe830c-74ec-52ff-b129-4a3ed94a9760 | note | TP
0c8466ea-46f8-563c-980b-4ccf33c2a639 | note | Responsibility - Project / Site Engineer, Laboratory Technician
7d92ade6-8787-586c-a9f9-909bcaec1671 | date | Date Completed:
f5e85626-3e87-51d9-b123-8dbe71828123 | checkpoint | 4.4 - Flexural Strength (28 day)
68bc7023-086e-52c4-a527-072e730877c5 | note | Frequency - First 5 lots: 2 Beams per 75m3 or part thereof.
25a96de9-b8aa-5d12-9823-ba69d74ca852 | note | ○ After 5 lots: 2 Beams per 75m3 or part thereof.
dc2be2b2-4f0f-552f-8dcf-b7bab6ae9120 | note | Acceptance Criteria - Mean of the pair of beams > 5.0 MPa Individual beams > 4.8 MPa
6f64e51f-d32c-5c63-8e3a-7d51f1de2841 | note | Reference Documents - Beca Spec 002 - 11.24.10
34161891-b4e6-5856-a5cd-40d95a043493 | note | Inspection/Test Method - AS 1012.11
3af3ca24-1695-54ac-ae7f-fbc32c179aab | note | Record of conformity - NATA Test Certificate
0da54949-117b-58bf-b3cd-c3583c3829b3 | note | TP
a3663f3b-081d-58c3-91a7-c63a62d9874a | note | Responsibility - Project / Site Engineer, Laboratory Technician
7eddf880-425d-5c79-88c0-4b9f42dd923a | date | Date Completed:
9e886210-4b93-5748-a95e-ad183ab45c95 | checkpoint | 4.5 - Air Content
beb5fad9-719b-5f31-9ca2-bbe8fea2632b | note | Frequency - 1 test per Lot
cce2068d-7751-5d08-b115-9c85be983a61 | note | Acceptance Criteria - 3% - 5% ±1%
cce38939-39dd-5930-b456-e385fde10ce4 | note | Reference Documents - Beca Spec 002 - 11.24.8, 11.24.9
4f873026-9a91-58f9-bd7f-32975b9c9630 | note | Inspection/Test Method - AS 1012.4.1 or 1012.4.2
96ae24eb-2d77-5f28-89c2-4f1dc3ced80b | note | Record of conformity - NATA Test Certificate
f0e67256-3950-55e7-a7f5-ff9fb9edfb96 | note | TP
c7616360-f69d-5c7a-a9a4-e385f182e23f | note | Responsibility - Project / Site Engineer, Laboratory Technician
eed76a32-8847-5b9f-bcd9-7ac60e6b2939 | date | Date Completed:
9ad6888c-fa3b-5efb-b8a6-dea67ddcb735 | checkpoint | 4.6 - Mass Per Unit Volume
249ca4b9-5f12-5647-bd16-61bb71132964 | note | Frequency - 1 test per Lot
914a1061-d7db-5862-80b3-2dc51c3bbd66 | note | Acceptance Criteria - Results for information only
d61bce60-4427-5438-a778-ac44dd2b9ac6 | note | Reference Documents - Beca Spec 002 - 11.24.9
56516493-bebe-5e10-94d5-968d50da156a | note | Inspection/Test Method - AS 1012.5
89fec65b-8936-51e1-b966-5a9bc9bb695e | note | Record of conformity - NATA Test Certificate
cea769a3-8529-5654-8e6d-9695b25c878c | note | TP
813e7f85-510e-53fa-b17a-6671485216dc | note | Responsibility - Project / Site Engineer, Laboratory Technician
7655c7ad-d1c4-5ddf-a170-5835f574c71f | date | Date Completed:
784088d9-4c0a-591a-bcd5-f66d2ffb7819 | checkpoint | 4.7 - Wet Analysis
343a3167-cf90-59c7-bf56-10568edf0ef9 | note | Frequency - 1 test per Lot
ed0a84e9-18b8-512b-89eb-0fa090f32c09 | note | Acceptance Criteria - Results for information only
a23c85d7-48fb-5dca-accc-8001ad078bf1 | note | Reference Documents - Beca Spec 002 - 11.24.9
b0493a50-ceb7-5173-b70b-785e23524ab0 | note | Inspection/Test Method - AS 1289.3.6.1
715add53-bd8f-5fd2-a2b2-69d474fbef00 | note | Record of conformity - NATA Test Certificate
79d6b9e1-35e3-5868-a636-e5b774e97e92 | note | TP
d74d9e31-040b-53aa-8098-f3eafa8096f7 | note | Responsibility - Project / Site Engineer, Laboratory Technician
c49d4dd6-001e-5b3d-acf4-c27d4f3d7767 | date | Date Completed:
21046b26-0f7a-50ea-a8d4-20fcdb40c85b | checkpoint | 4.8 - Concrete Core Analysis (Density & Compressive Strength)
44ef0abf-113d-5a24-b205-4a368131b77d | note | Frequency - First 10 lots: 6 cores per Lot
8dda6e55-4e3f-5481-a80c-36712dd44c50 | note | ○ After 10 lots: 1 core per 75m3 or part thereof
f698075e-11c4-5bff-b6a4-f3df2e4eb701 | note | Acceptance Criteria - Cores must be not less than 120mm diameter.
f121d421-0622-5526-b970-29ddf62c3769 | note | ○ Calculate the degree of compaction by comparing the density of individual cores with the average density of flexural test beams (exclude beams whose density is less than 97.5% of maximum theoretical density). Refer to notes section for acceptance requirements.
93ff3a2a-1e34-5537-a2c0-92305264f999 | note | ○ On third of the cores taken shall not be tested for density but shall be tested for compressive strength and results submitted for information purposes only.
8998f956-5b2b-5eba-abc6-3cc8f555afbd | note | Reference Documents - Beca Spec 002 - 11.24.12
81946f43-f32b-5770-847b-fca603623b71 | note | Inspection/Test Method - AS 1012.12, AS 1012.9
c579b5f9-7653-5159-950f-b218a132b5a9 | note | Record of conformity - NATA Test Certificate
d065c9e2-e7de-5724-81b2-3ff5c52b422c | note | TP
9d2eceff-0e85-554e-8aa1-6229bdbf671a | note | Responsibility - Project / Site Engineer, Laboratory Technician
59c3b69c-68da-5505-8ce0-3f8a9ece2c03 | date | Date Completed:
782b8ec4-e2e7-589a-bdec-0fe6bc056628 | section | 5.0 - Post-Placement
cf47b8f0-f88a-54c2-b407-91f44e2a654f | checkpoint | 5.1 - Curing
d935de30-5a7e-5f55-8a4c-05bb1a5194a1 | note | Frequency - Each concrete pour
0b1553ac-4ec0-5a8e-8d8f-f4260aefd946 | note | Acceptance Criteria - Concrete shall be cured by protection against loss of moisture and rapid temperature changes for a period of not less than seven (7) days from completion of the finishing operations.
40e0f672-c0b1-5de3-939a-86d62221b715 | note | ○ Curing of the concrete shall comprise an initial mist curing followed as soon as possible with continuous wet curing with hessian matting for the duration of curing period.
a2c4a646-91dd-5a03-97cb-f09b867f8363 | note | Reference Documents - Beca Spec 002 - 11.12.4
8441d7a4-4ca1-5d1d-b5a9-8246823633f8 | note | Inspection/Test Method - Visual Inspection
5ecbc6a7-bdf6-5d88-b7fb-dfe592caf6cd | note | Record of conformity - This ITP signed
da2577af-fbbe-5cc3-836f-f2db59d57582 | note | IP
d887255a-6945-5b74-8988-38edbf9405af | note | Responsibility - Project / Site Engineer
586a76b4-cd49-5ad5-9eb3-335564e3ab27 | date | Date Completed:
aa609089-ea6f-521a-b2a7-7cd41a2d5d49 | checkpoint | 5.2 - Cold Weather Concreting Concrete Protection
b72a3ea0-9cf3-54a7-beec-14b61b7a485d | note | Frequency - Each concrete pour during ‘cold weather concreting’ conditions
bf428b0e-8c96-580d-9b28-a5f2c3a1450c | note | Acceptance Criteria - The surface of the concrete must be maintained at a temperature of at least 10°C, for not less than 72 hours after placing and at a surface temperature above freezing (0°C) for the remainder of the curing period.
f9469610-5e96-5a78-922e-b7dee55d8e29 | note | ○ Concrete surface temperatures post-pour to be recorded on checklist CL013E – Cold Weather Concreting.
a429a458-d908-5b2c-ac3a-8f1ba931df5e | note | Reference Documents - Beca Spec 002 - 11.9.5.4
4f84e7fa-b264-5dfe-bca2-9a95248c0896 | note | Inspection/Test Method - Verify
410a28c0-f2e4-5be6-9d42-669ddbe29548 | note | Record of conformity - CL013E
71518393-0ca3-58de-b30c-7e807bd704e0 | note | IP
148e7960-cfe8-5c7b-a158-389cc3f3c208 | note | Responsibility - Project / Site Engineer
bc31c826-5b56-59c5-9460-f2f09b4366fc | date | Date Completed:
82b7f08a-ab9e-5a58-be5c-738ceda7b9f1 | checkpoint | 5.3 - Inducement Saw Cutting
ba74ad63-a217-5659-8789-4213c2ef4104 | note | Frequency - Each concrete pour
9d64d094-2296-50a1-b47e-7ab9a78b0e8b | note | Acceptance Criteria - An initial 3-5mm wide saw cut to a depth of T/4 to T/3 where ‘T’ is the concrete thickness (generally 150mm) is performed along transverse contraction joints as early as possible post pour.
125b6f42-2b3a-58fe-b46a-92a76549fb7a | note | ○ The concrete must harden sufficiently to permit cutting the concrete without excessive chipping, spalling, or tearing.
1a776220-10f0-5a53-b868-97fef033431d | note | Reference Documents - Beca Spec 002 - 11.13.5.2
30288578-007f-585f-a161-4929011df0c2 | note | Inspection/Test Method - Visual Inspection
377ff993-cbe6-50a7-aa30-10d2d23a7839 | note | Record of conformity - This ITP signed
2b2e9676-0d95-5bfb-9060-7ae0fcc14764 | note | IP
ac9e5c42-5d54-51f0-92a6-47743e8b6671 | note | Responsibility - Project / Site Engineer
ec669d6c-1236-5ce8-b376-bbfb38d60b30 | date | Date Completed:
1415f254-48b2-52a5-8aea-2df0d8845449 | checkpoint | 5.4 - Formwork Removal
4c9f9ded-2540-5aa1-a9b7-1549da9de3ad | note | Frequency - Each concrete pour
c89af9fa-9c3c-5b89-9507-b7f0b4112f66 | note | Acceptance Criteria - Forms must remain in place at least 12 hours after the concrete has been placed (but no longer than 48 hours).
28e65d8a-e481-5fae-b3c1-156e31999afd | note | Reference Documents - Beca Spec 002 - 11.8.1.3
a1b1af8d-5887-5e45-80c8-c711f63c9273 | note | Inspection/Test Method - Verify
f4445baf-2265-5b77-9a96-a3717922e231 | note | Record of conformity - This ITP signed
5d0613f6-7e0b-5386-9b7c-f4e76151a0d6 | note | IP
6d4b2aac-9612-5e27-a9cf-153d627386ae | note | Responsibility - Project / Site Engineer
18f2ef5c-d133-5162-88cf-ce695de1233a | date | Date Completed:
69489b9b-1e23-57b3-b09f-8b123c4734fd | section | 6.0 - Completion
8fa0b7c0-e1be-5bfb-a603-8cd013fc6298 | checkpoint | 6.1 - Surface Smoothness Testing
55e7de99-3c61-538a-a173-cbdebe5c1754 | note | Frequency - Per Lot
0c6efdae-61ee-505e-af82-1add84557269 | note | Acceptance Criteria - The finished surfaces of the concrete pavements shall not deviate from the testing edge of an approved 3.5m straight-edge more than 5mm longitudinally and 5mm transversely. No ponding of water is permitted.
32222931-7dbf-5c57-a8be-fb36823b71be | note | ○ Points exceeding tolerances and any observed areas of ponding water will be recorded on ArcGIS.
8789dc0b-3a2a-58b2-89a8-c6643a4d1cac | note | Reference Documents - Beca Spec 002 - 11.14.3
9d59607b-536c-51a3-b9b8-f275e3994b93 | note | Inspection/Test Method - Visual Inspection
d920b062-aab2-5cc1-8472-ec4909ccab24 | note | Record of conformity - ArcGIS, This ITP Signed
2d893d27-0cfb-5e97-acd3-5a846b45f93c | note | IP
168e7066-b2f9-5912-8c30-42b0df934b3f | note | Responsibility - Project / Site Engineer
4799c1ed-759e-577d-acbc-1c9e9a389eb2 | date | Date Completed:
91cbcdd4-c964-5ba9-81ea-9199af3ff529 | checkpoint | 6.2 - Pavement Surface Levels
f7b31f9b-21d2-5bd8-8aca-6bac5928cc2c | note | Frequency - Per Lot
445217a3-704d-54d0-91f1-f47b50e14278 | note | Acceptance Criteria - The Contractor shall take levels on the finished pavement surface at the corner of each slab.
986af59c-af1b-54e1-b235-cc9960654cdb | note | ○ The finished surface levels taken shall be within ±5mm of the design levels shown on the Drawings.
54cd0821-1456-58c9-9edb-34ea1dfb4396 | note | ○ The levels shall be measured to an accuracy of 2mm.
2479533d-2d5a-5645-94a5-2f3915c91011 | note | Reference Documents - Beca Spec 002 - 11.14.2
7d131307-0cf5-5fb5-a872-6605679b0156 | note | Inspection/Test Method - Verify
30637c20-3975-54ca-b8e5-98e5838a8c78 | note | Record of conformity - Conformance Report
91934272-5c06-53f9-bced-b8f5a45c58a2 | note | SCP
942d3878-1a64-50ba-9f33-700d3f5365a2 | note | Responsibility - Project / Site Engineer, Surveyor
c89333bd-fc10-5caf-a06a-0387ff3ec9a7 | date | Date Completed:
4ea2f5f4-1037-54b8-98fd-5a7f56de6983 | checkpoint | 6.3 - Protection of Slabs
e0a272cc-8031-5c13-94e7-2c52940c54d6 | note | Frequency - Per Lot
ca4200e7-3811-542f-9623-95ab15582db2 | note | Acceptance Criteria - Concrete pavement must not be trafficked until 7 days old or early strength results are obtained. Steel tracked or steel wheeled equipment is not to be used.
d0d67642-8c06-5e46-8e83-6af9a4ec16ed | note | Reference Documents - Beca Spec 002 - 11.17
1981dabb-a7d4-56cc-a815-bb0ec0aac791 | note | Inspection/Test Method - Verify
d9f99ce0-fd9f-523d-b3b0-028767f2b5d5 | note | Record of conformity - This ITP signed
536c33e3-9e33-5297-a415-b849c3716a6b | note | IP
a9977ffb-173a-5f9c-a3fc-11de956a432f | note | Responsibility - Project / Site Engineer
5f06486e-2a73-588f-a366-13292ebceedf | date | Date Completed:
2c5ed52b-149f-5ba6-86ad-1a18b9ce8a73 | checkpoint | 6.4 - Defects to Slabs
3f516d19-5afa-50e8-8656-411903a8c112 | note | Frequency - Per Lot
150631ea-1856-53df-a83c-9a9317be8056 | note | Acceptance Criteria - Check for any nonconforming defects (cracks) in the concrete slabs.
94aceb5c-6f5d-54f3-bdd1-ca5bc232a8a3 | note | Reference Documents - Beca Spec 002 - 11.19
ec7e76c9-dc53-5142-98bd-3df83042df78 | note | Inspection/Test Method - Verify
ff40cd6d-cd44-56b9-a6a1-b07d689665dd | note | Record of conformity - This ITP signed
d109b0da-565c-5772-9e5b-2c8a5ff335e3 | note | IP
36bc9767-f10d-5220-8856-df85756fe6b7 | note | Responsibility - Project / Site Engineer
c9833f31-e161-56f7-9594-e08d707687aa | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
6ec667d0-0f8f-5ddb-9183-5e7d582c3f27 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality/System Procedures and verifies lot compliance with specifications.
d2e6550e-c607-57f6-87e4-4aa671b9d4d2 | textbox | Print Name:
870a6224-29d1-5697-b7e0-a4aee1ba336c | textbox | Position:
3b5d58b4-9d81-5add-bb5f-d6993954ebd6 | date | Work Completed On:
94480ab5-0fac-571f-9c29-dad8053606d3 | date | Date:
ad2d1791-ffd6-5f4a-81da-08ea1abbcf2a | checklist | FH-ZU2-QU-ITP014 - Sawcutting & Joint Sealing - Rev 0 | itp | ITP014 - Sawcutting & Joint Sealing
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
fbd6ef58-7046-5030-bc38-d0da69c3974d | checkpoint | 1.1 - Check for Correct Documentation
79bd05d0-9a65-5949-b1aa-d4a42fc4e829 | note | Frequency - Prior to commencing works
31adfb6e-d09a-5768-8b5b-c2053849fb88 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
5d8b007b-08f3-5787-8929-bf98bc3e325d | note | ○ Current revisions of these documents to be obtained via Aconex or ACC
fee07b74-ed1e-5be5-bf5f-59b71136dd74 | note | Reference Documents - Current revisions in Aconex or ACC
da8dd3cc-19e3-5726-b492-cba5176eab7e | note | Inspection/Test Method - Verify
b231cc0c-dad8-53ec-b88f-e9c0bc8f723f | note | Record of conformity - This ITP signed
7235dad4-6d0b-59a9-8eed-fbebbba2a3c3 | note | HP*
5c7ff4ef-cb14-595e-b46d-97dfd87a16cd | note | Responsibility - Project / Site Engineer
3e94d70a-74f0-5061-98da-8624cc10e016 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
3303edab-5b66-5af1-b8d1-22ab8495cee9 | note | Frequency - Prior to commencing works
be859a16-d2c6-53c3-9eda-012f04d455a3 | note | Acceptance Criteria - All necessary measures and controls are being implemented in accordance with PSP, EMP, TMP, JSEA, SWMS & WP
dbcba871-bf73-5749-8b4e-72cae0e93402 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
a0786763-a24a-554c-b4b4-6fc9d456cccb | note | Inspection/Test Method - Verify
d3393572-6931-512b-8426-8ac8490b3c40 | note | Record of conformity - This ITP signed
18970737-ee7c-5380-85c4-295e20dbdb59 | note | HP*
ac463377-a89f-5219-a70a-255e42583d57 | note | Responsibility - Project / Site Engineer
1e1c368b-64cd-5b5b-a437-b6e79ffd73ad | date | Date Completed:
6388a249-3345-585a-b094-a82a42091183 | checkpoint-no-value | 1.3 - Materials
104cfd90-1f66-5422-ba65-37d3da17529b | note | Frequency - Prior to commencing Works
04426826-43e9-5e13-9ab8-c8fd7051ae59 | note | Acceptance Criteria - Joint sealer shall be Dowsil 888 silicone joint sealant or approved equivalent.
d6909b33-132b-5a99-9c4d-9d6f19d6a2c7 | note | ○ Manufacturer’s instructions shall be provided to the Principal’s Representative prior to works commencing.
196df762-12b9-59fd-a43e-07f70198a115 | note | Reference Documents - Beca Spec 002 - 11.4.15 & 11.13.7
ec797054-95f2-4c19-80dd-7f72509b3664 | note | Aconex reference: FHPL-TRANSMIT-001667
8015b1e2-15af-5303-b7fc-371f61f1f555 | note | Inspection/Test Method - Verify
36243bbf-6174-5952-8558-8d07c07db877 | note | Record of conformity - This ITP signed
1c190af6-c392-51f3-a584-d381a85854fd | note | WP
1c777fe5-4e59-5b43-9ad5-8a5f0e3b41e7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
6698d47f-e594-55af-80d0-56df63c69cd8 | date | Date Completed:
62cb0e25-66ef-5565-83f6-0dac7af7e013 | section | 2.0 - Installation
80fb73ed-9148-5be9-84ce-96314adc85d5 | checkpoint | 2.1 - Define Area of Works
295d7320-011a-559c-a972-4aed72dd5c8d | note | Frequency - Prior to commencing works
c1de4dee-b4bc-55c7-90e3-f8968bd9f205 | note | Acceptance Criteria - All joints shall conform to the details and shall be constructed in the locations shown on the Drawings.
5939cd03-4fd1-5d3d-82f6-15ba24074494 | note | Reference Documents - Beca Spec 002 - 11.13.1 to 11.13.5
722d964b-67c3-5d03-ad10-f925c6693338 | note | Inspection/Test Method - Verify
63562468-3c10-533c-bd0c-8b100a446611 | note | Record of conformity - This ITP signed
c1528537-18cf-598f-b010-d783ae5d9fb6 | note | IP
0a85ca7f-f949-53e8-8449-464fb9998035 | note | Responsibility - Project / Site Engineer
8ceb191f-f8d6-5a46-8a48-8d31b0754533 | date | Date Completed:
9ad22714-45c3-594f-bafc-69cb92633a96 | checkpoint | 2.2 - PCC Curing
31744c6d-8b9e-5970-ba1d-a84974b2d5c0 | note | Frequency - Each Lot
230244ca-7f00-5c06-964a-22aed6882ccb | note | Acceptance Criteria - In areas where sealing works are planned, confirm PCC has been cured for a minimum of 7 days prior to sealing.
f93d14d2-c38d-5953-8a9c-76b4355bcc0c | note | Reference Documents - Beca Spec 002 - 11.13.7
3e1be03d-3f7e-59a2-8fc5-5da68d188d6e | note | Inspection/Test Method - Visual Inspection
d4439ab2-6542-58e0-aa12-6ef6c03afed2 | note | Record of conformity - This ITP signed
ed398638-07e7-5a6e-b3d2-236d2382808d | note | HP*
f36e53b7-aa1e-5d8b-840b-da3b6b51c409 | note | Responsibility - Project / Site Engineer
d18e00cc-bf4f-59b3-be8c-05e630d9b96b | date | Date Completed:
f9a30c12-b07c-5b7a-a70a-74c6dc3b696e | checkpoint | 2.3 - Cleaning of Joints
54a84945-1e69-597f-b3da-e8f0613d560c | note | Frequency - Each Lot
8d1e99cf-2220-5158-a456-6350bb440f3a | note | Acceptance Criteria - Joint faces shall be thoroughly cleaned and dry prior to sealing. This shall be approved by the Principal’s Representative.
76b748eb-a640-5b9f-abff-577239a7e83d | note | Reference Documents - Beca Spec 002 - 11.13.7
3f303229-fda5-55cd-80a2-1ec9c63f5bc3 | note | Inspection/Test Method - Visual Inspection
5029e114-3f54-5c3a-957a-b36a2e35ad46 | note | Record of conformity - This ITP Signed
a4970c7c-ab86-5b24-b946-10cfe343ba20 | note | HP
dd3d86b2-47be-5f2e-bb01-be9bb380d7c0 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a3590dfe-3c4f-5768-b7ae-73cb1bc9d759 | date | Date Completed:
ba83cded-4d09-50d7-a949-2a60a3a7c8c2 | signoff | AUTHORITY HOLDPOINT
9a279428-8bb3-5f72-acd3-3d377212d952 | checkpoint | 2.4 - Backing Rod Install
825ca411-5727-5ec3-ab0c-19d7c3092ad8 | note | Frequency - Each Lot
7905221d-1424-5c4b-b9c7-3761007aa3b9 | note | Acceptance Criteria - Backing rod to be installed to depth shown on the drawings.
4c33455f-d134-56b9-bd91-914522f6aaa4 | note | Reference Documents - Beca Spec 002 – 11.13.7
d2303ef6-434e-5eb4-a00e-a4ee33374713 | note | Inspection/Test Method - Visual Inspection
64a37ad5-f09b-52f9-b76b-c67f1920410f | note | Record of conformity - This ITP Signed
847a7d15-8584-5e8d-ada6-d4c079607b83 | note | IP
be167dd5-d048-5341-927a-74ada804837a | note | Responsibility - Project / Site Engineer
da094bf1-5076-5913-93c2-aaf21e393771 | date | Date Completed:
0439dd16-c209-52bc-9c79-8b4362871d01 | checkpoint | 2.5 - Sealant Install
5e294b05-1fc6-567f-850a-edc8fc6ef83d | note | Frequency - Each Lot
9e69eab8-128a-5236-9b3c-14420c4b12dc | note | Acceptance Criteria - Sealant to be tooled off to correct recess. Excess sealant to be removed from the surface of the concrete.
5318b95d-2c17-5177-be5b-77c7e07c7f66 | note | Reference Documents - Beca Spec 002 – 11.13.7
66de4527-e36e-5cf2-8bbb-f15f283e02da | note | Inspection/Test Method - Visual Inspection
165c9f15-ca4b-5e66-a171-a5fa68fd6053 | note | Record of conformity - This ITP signed
723c8b20-6353-5b5a-b67f-425d9e2bc5d0 | note | IP
873f9e41-1b9d-5139-aede-4a5e8a601dc0 | note | Responsibility - Project / Site Engineer
99785c1a-a191-5411-9d83-66073b0d8f49 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2032242e-37a0-5afc-b658-cf9d20792b14 | note | This is to verify that the final inspection has been carried out in accordance with the Fulton Hogan’s Quality Procedures and Project Quality Strategy and the product is hereby certified to confirm with the contract specifications:
86eb545f-008f-5daf-9ba8-17e663686c8b | textbox | Print Name:
98c0cebe-8793-50d3-959c-8570dee248eb | textbox | Position:
6d2a49ff-3315-51d0-aca3-72cedec50543 | date | Work Completed On:
7347a2ab-2fd0-59f3-ba1f-0f8ea233c1f7 | date | Date:
3e319325-9222-45dd-a810-5c248b1c1af8 | checklist | FH-ZU2-QU-ITP015 - High Early Strength Lean Concrete Placement - Rev 0 | itp | ITP015 - High Early Strength Lean Concrete Placement
dfbc0e0a-0cb2-49ec-94fc-753028b5d0c2 | section | 1.0 - Preliminary Activities
6712e7e7-b913-4cad-a29c-d541f7808afb | checkpoint | 1.1 - Check for correct documentation
7944f4f4-2a7a-5b80-aa50-6767d0d2a5e8 | note | Frequency - Prior to commencing works
f78851a2-a7c1-5009-8726-89dff85b0b83 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
bd0154f6-5203-5aee-9602-24cd92746f32 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
737d535a-d507-5293-aee6-e96722b043f8 | note | Reference Documents - Current Revisions in Aconex, ACC
2a9991a1-400e-52d2-a532-7c07c7c0f57f | note | Inspection/Test Method - Verify
6c4719c8-cfd5-5c14-8b15-4824ff243cd5 | note | Record of conformity - This ITP signed
019d1d84-5721-5b7f-a59b-8509ce6e90b9 | note | HP*
e6cf1f99-cbf2-58eb-9268-b1748e0f9127 | note | Responsibility - Project / Site Engineer
8349b8d3-a86f-5134-93be-469508f9ce73 | date | Date Completed:
c2beb12b-988d-46c5-99a1-f440f3242bf0 | checkpoint | 1.2 - Implementation of all measures and controls
432a4e6e-49ef-58ed-a8a7-792bf669b352 | note | Frequency - Prior to commencing works
77347a37-aaa7-50b9-b751-d3da9b490b48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
48b83619-aa46-5c5d-8f2c-cbd47ffd2b35 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
9ee7ac61-d46f-5209-9d46-a57bee5b6b9b | note | Inspection/Test Method - Visual Inspection
f2e279a5-f5d7-512a-9af9-61084ae4e1a0 | note | Record of conformity - This ITP signed
3b4c2eb5-4c7b-537e-a5a1-d528932c95b8 | note | HP*
ef2e5bba-dce8-51f0-a266-d8cb8d4e8862 | note | Responsibility - Project / Site Engineer, Site Supervisor
368187d3-5373-5a5b-9483-ec1d6809aa93 | date | Date Completed:
3d6b455e-7ff5-4469-bd24-cc6f221f9106 | checkpoint | 1.3 - Plant & Equipment Check
c131f583-5e95-53f8-8e87-f799b68dcd9b | note | Frequency - Prior to commencing works
c87e5796-f7d5-5b43-a828-389c557654eb | note | Acceptance Criteria - Plant and equipment items used in the Works shall be appropriate for the intended purpose and shall be maintained in good and serviceable condition at all times during which they are operating.
2508810e-4f7a-5111-9299-e2166eb1baad | note | Reference Documents - Beca Spec 002 13.3
2acf9b97-26ae-50ab-b157-0579f2313003 | note | Inspection/Test Method - Verify
40d5b898-284e-598a-9d79-7f6d5ec8ecbb | note | Record of conformity - This ITP signed
dba5bad5-efb6-5bd2-82a4-a771a148fb1b | note | HP*
477374f2-efd5-54d6-9b29-5f492eb70a16 | note | Responsibility - Project / Site Engineer, Site Supervisor
61d9259b-8795-5c12-b319-472fe87b587f | date | Date Completed:
2b718a27-b6f1-4b3d-b17c-ca03606fe914 | section | 2.0 - Production and Construction Trials
682b747b-5a82-4c22-81d8-df8c9c975ef7 | checkpoint-no-value | 2.1 - Mix Design
690fb887-aaf5-5226-9877-6b127492e350 | note | Frequency - Prior to works
a9f9ff38-7b55-5999-a385-0e900bf245c5 | note | Acceptance Criteria - Theoretical mix design and preliminary trial mix results to be submitted to the Principal’s Representative for review and acceptance prior to full trial mixing.
ef34d970-9ec5-569b-b469-92d280482227 | note | Reference Documents - Beca Spec 002 13.5.1
dbc726aa-9b61-50e0-9236-cf4018222388 | note | Inspection/Test Method - Verify
7ec50637-b5d7-5df8-b9b8-e5ea03059f97 | note | Record of conformity - This ITP Signed / test reports
2082d925-a5e5-5f6d-aed5-63a4acdf504f | note | HP
fe96dc1b-a0de-5c7e-844b-aa56582e1472 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2f09bb8-e62f-5e1b-a563-1758942f5573 | note | Date Completed: 13/09/2024
58ea452f-e285-5a95-9e6e-51546848526b | note | Principal's Representative - BecaCPL-GCOR-001171
6cc29a56-28fd-41df-82bf-5caacf9a0054 | signoff | AUTHORITY HOLDPOINT
d5308491-7824-4983-88a3-fe3bc5cf80e8 | checkpoint-no-value | 2.2 - Mix Design Report
1902e885-fe4b-5de8-bb33-b97d18928d62 | note | Frequency - Prior to works
99825237-1513-5b47-a4f9-14cdb6fbd36d | note | Acceptance Criteria - The theoretical mix design and preliminary trial mix results to be submitted not less than seven (7) working days prior to full trial mixing.
fefed4a2-c7a1-5821-9d41-c085c23a9c29 | note | Reference Documents - Beca Spec 002 13.5.2
c7a78384-dfc8-51f5-9036-0840ca99f8f9 | note | Inspection/Test Method - Verify
86e01fb3-8fa8-5538-8987-f640cec437ed | note | Record of conformity - This ITP Signed / test reports
7bdda105-e475-52a5-9ffe-6e50afbeffd8 | note | HP
67104860-a283-5f86-bd09-b8b1e3ec176f | note | Responsibility - Project / Site Engineer, Principal’s Representative
155e5b71-3c9c-57d3-a4b8-b5b060abd230 | note | Date Completed: 13/09/2024
52723341-65e8-5ae5-870c-17371d770fef | note | Principal's Representative - BecaCPL-GCOR-001171
fa88cff8-8569-4928-81b7-80bd21d6cd80 | signoff | AUTHORITY HOLDPOINT
9d264ec7-add2-4523-9072-8300d10e3b7b | checkpoint | 2.3 - Mixer Uniformity Test
39fbdbd6-5d06-5d8e-ad5a-d02c35330554 | note | Frequency - Prior to works
2feafff9-77db-59b5-ac91-4f22dd3efc47 | note | Acceptance Criteria - Mixer uniformity tests shall be undertaken on the fully operational mixing plant at least seven (7) days prior to undertaking production trial and submitted to the Principal’s Representative.
c16eb7fd-72c0-5540-ba90-0ea9e0f0c32d | note | Reference Documents - Beca Spec 002 13.6.1
264b4f9e-78d2-549a-8abe-4a07fc9c04da | note | Inspection/Test Method - Verify
e0edec82-428d-5bc1-a745-56f0bc2ba6c9 | note | Record of conformity - This ITP Signed
b3680153-cce4-58fe-b2e3-f758c7903ae3 | note | WP
35194a59-3a43-5c36-842d-5c56cd2b61aa | note | Responsibility - Project / Site Engineer, Principal’s Representative
63e223d4-8c2c-5ce1-97e4-5c41c3794a37 | date | Date Completed:
1de4b53c-11e2-48b5-9a89-4d47793e3511 | checkpoint | 2.4 - Production Trial
d25a798d-8df3-5b3a-b5c9-c5cf88574f2d | note | Frequency - Prior to works
c52d8fae-5752-57cc-92c3-f68a7a6b7be9 | note | Acceptance Criteria - A production trial must be completed as per the requirements in the specification.
fb197d40-b81c-5a53-9f40-7a0848d671dd | note | ○ The results and control procedures to be presented for review and approval by the Principal’s Representative.
5b529e85-01fd-5471-85a3-cc7e0065022e | note | Reference Documents - Beca Spec 002 13.6.1
563c748f-2c3e-57c6-b5f2-f00ee0a1b924 | note | Inspection/Test Method - Verify
be1949fb-49bb-5210-b8de-d94a7d613739 | note | Record of conformity - This ITP Signed
415d955e-e8e5-54ec-ae80-2ddbd50e9806 | note | HP
2f9850dd-98ac-526d-8d4e-d21e020f7fa8 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4755571d-c41f-544b-97b4-80e8972d5ec0 | date | Date Completed:
41999afb-0e79-4922-a9bc-679bb1454545 | signoff | AUTHORITY HOLDPOINT
7e751069-aa7a-4226-9427-79d195756c82 | checkpoint-no-value | 2.5 - Compliance
1aaea2fb-0862-5079-ad10-7925bdd82753 | note | Frequency - Prior to works
0c8dbc77-ecc3-5b9e-b0f2-008c10230ada | note | Acceptance Criteria - Provide evidence to Principal’s Representative of concrete supplier demonstrating compliance to AS 1379 or is a third party accredited to AS 1379.
d84f4476-71ff-56cf-a3c4-4fef572eba5b | note | Reference Documents - Beca Spec 002 13.7
7101cd85-203e-5797-8cb6-5d817d1f2179 | note | Inspection/Test Method - Verify
c001f072-6adb-5fd8-9486-4e1925866f82 | note | Record of conformity - This ITP signed / evidence documents
f6694ee0-d210-5607-9700-c4e65ea9a4a0 | note | HP
50edde23-2933-56b0-b478-d16c475f2595 | note | Responsibility - Project / Site Engineer, Principal’s Representative
ed00a9df-0ce8-57ec-8ac4-acf65c95455d | note | Date Completed: 13/09/2024
cf51fd12-128c-538b-bde5-9e64cbf7c0ce | note | Principal's Representative - BecaCPL-GCOR-001171
e4318980-a89a-498d-ac9a-9280f991a23b | signoff | AUTHORITY HOLDPOINT
b4e29d90-5665-43d5-998a-f0fff578eb70 | section | 3.0 - Pre-Placement Activities
3809d3b0-56fd-4685-b8b4-1e09ae8a3836 | checkpoint | 3.3 - Surface preparation
9d5e19e6-7aa0-5a95-8111-4e454dd24bec | note | Frequency - Prior to works
e3bd3171-cd44-5af5-9a7e-d1d1cccfb054 | note | Acceptance Criteria - The surface must be clean and inspected by the Principal’s Representative prior to placing.
169928af-7fe9-5337-b889-23f4ba40159c | note | Reference Documents - Beca Spec 002 13.8.1.5
0c8ab2dd-d061-527c-847a-f6b344f10af4 | note | Inspection/Test Method - Verify
94d79d16-dfb7-58d5-bf0d-f4214fc52a30 | note | Record of conformity - This ITP signed
01ea45ac-e65d-5f54-affe-9e98b567dfda | note | HP
e349923d-b6f3-5ab3-a104-2b91a2c06302 | note | Responsibility - Project / Site Engineer, Principal’s Representative
cd097b79-d737-5421-b4e2-334bdf0dfbc5 | date | Date Completed:
74e2efbd-a79c-4ce3-b24d-e90583b74c08 | signoff | AUTHORITY HOLDPOINT
5262d2f8-2f71-489b-b857-ca06cb282b87 | checkpoint | 3.4 - Weather Conditions
6caf6fec-cfa2-56aa-a829-c287a6af9ba6 | note | Frequency - Prior to commencing works
45ba7fd4-3722-5daa-b9bf-55c6f4468e68 | note | Acceptance Criteria - HESLC shall not be placed when the shade temperature is below 5°C or above 35°C.
8a5364ea-2313-5bac-9a1f-9b293dcb7b95 | note | Reference Documents - Beca Spec 002 13.15
49c4d3f1-eae2-508d-b3f1-9d3296c9d2f0 | note | Inspection/Test Method - Verify
06f3d9a4-1c58-5464-8272-ec125f9b63d9 | note | Record of conformity - This ITP signed
b0297096-a032-5d1e-b7f2-fd073dfa4e21 | note | HP*
54f874d9-6831-5c9f-a6e4-7eedd5a12ce2 | note | Responsibility - Project / Site Engineer, Site Supervisor
97547145-88dd-5914-aa8a-56cbbd362bdd | date | Date Completed:
a1407878-971c-458b-9a7e-de1ab5605e91 | section | 4.0 - Placing Concrete
0507a2ed-1c43-4e70-890a-8f1142b40462 | checkpoint | 4.1 - Place, Spread and Compact Concrete
198a3453-4bf6-5ca5-b68f-444692cf8198 | note | Frequency - After completion of works
7680b5f8-0138-5407-8a54-42d62336f866 | note | Acceptance Criteria - Compaction of HESLC shall commence immediately after placing and shall be by internal vibration.
97aa61b3-6a5d-5c15-a4dd-875663f53968 | note | Reference Documents - Beca Spec 002 13.10
b4162197-ce02-56b8-8c14-c8d61ad0a7ec | note | Inspection/Test Method - Verify
a8b66a92-9486-5c8c-a5c7-3d825ce53d43 | note | Record of conformity - This ITP signed
94e3dd4a-c354-55d2-913f-91cb96ebf710 | note | IP
b2e5153c-0b85-5df3-9590-26439120c522 | note | Responsibility - Project / Site Engineer
be46e53f-2abd-5b7f-bbcd-0cb4f0d7ae63 | date | Date Completed:
3922c64b-5eb2-409d-b3b7-b403d2905d30 | checkpoint | 4.2 - Slump
e268e261-039f-583e-a796-c3c0bf173246 | note | Frequency - 1 test every 2 trucks
8d013726-3126-5a3a-95fa-5cfb8364b328 | note | Acceptance Criteria - 100mm +/- 20mm
be6c938b-6766-5da8-8a53-2be35de8289e | note | Reference Documents - Beca Spec 002
1779ad00-433b-5aec-b466-6a6f45219e24 | note | Inspection/Test Method - AS 1012.3.1
7a9d68bd-236f-5fb9-8b9f-8e5476f56534 | note | Record of conformity - NATA Test Certificate
babc4247-da89-53f6-8be8-c40801383605 | note | TP
bbd92bf4-d2fd-55eb-85ed-1fe463b3414f | note | Responsibility - Project / Site Engineer, Laboratory Technician
f761a99a-8c40-58fc-99c2-693dd338ce9e | date | Date Completed:
f4f6a52e-67cc-420f-b926-0e4b3d172c8d | checkpoint | 4.3 - Temperature
14c5c469-01dc-578b-aaf1-d632d8466bc6 | note | Frequency - 1 test every 2 trucks
0b5ee5cb-be0d-56ac-9466-d13a1e639996 | note | Acceptance Criteria - Minimum 10°C Maximum 30°C
6fd17808-4107-5121-8e61-0190ae37fedc | note | Reference Documents - Beca Spec 002 13.15
414c748b-c490-59e4-82aa-499c77e8ecfb | note | Inspection/Test Method - AS 1012.3.1
eb8c0ad9-0dc6-5995-9dfe-a3b79a59b855 | note | Record of conformity - NATA Test Certificate
1c3ce3f0-279e-5678-95cc-b61bb6b94424 | note | TP
13107dce-39a0-51d2-bc57-88e0fa901d33 | note | Responsibility - Project / Site Engineer, Laboratory Technician
9eee4560-09ce-57b6-98d8-dd5ac6709ee5 | date | Date Completed:
66240731-3b85-4826-8867-0188c1b6708b | checkpoint | 4.4 - Density of Cylinders
1dcad014-72b0-580c-896d-cad6cdd3b8ca | note | Frequency - 6 cylinders per Lot (same cylinders used for compressive strength)
b4d23261-a7e5-5e93-9668-f23a3aacedf6 | note | Acceptance Criteria - Results for information only. To be used to determine density of cores.
a9a32d5a-2cf4-54be-8603-320e9a2699f3 | note | Reference Documents - Beca Spec 002 13.17.3.6
08f6dbdb-93ec-5a8f-8ba0-6da359bf7d1d | note | Inspection/Test Method - AS
c80d4005-469d-5dc2-8e83-3a0b5846f89d | note | Record of conformity - NATA Test Certificate
9e4aa837-c55a-5e6e-b38b-55177c77dd50 | note | TP
4e697d4c-5c94-59fa-b889-6a2ad547bb54 | note | Responsibility - Project / Site Engineer, Laboratory Technician
3780cf11-63bb-5b7c-82ca-b48480d3dd2c | date | Date Completed:
16cfd622-7461-4109-b108-e0f0ef57be08 | checkpoint | 4.4 - Compressive Strength (7-day)
d7318c78-b9c2-5888-9999-e7d6257abcf2 | note | Frequency - 4 cylinders per Lot (same cylinders used for Density)
86980492-a652-5124-8380-c1b078c46f6a | note | Acceptance Criteria - Mean of the 4 cylinders to be minimum 10MPa and maximum 15MPa.
d079095e-5bd2-5047-b991-83f0460c0502 | note | Reference Documents - Beca Spec 002 13.5.1, 13.17.3.6
c2e00e97-b9a7-5c6e-ae69-55eca92b6446 | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
ed217bc4-1326-53d5-bf1a-2259e992356b | note | Record of conformity - NATA Test Certificate
04c09162-9be2-59c0-a507-2d76bf9194c4 | note | TP
3146a27d-074f-5de3-afa6-704c297ef0c3 | note | Responsibility - Project / Site Engineer, Principal’s Representative
d3ab9044-ef99-5639-9017-2712987f9d54 | date | Date Completed:
cbe4abae-ff1e-478d-b434-3d0fe258f8b0 | checkpoint | 4.5 - Compressive Strength (28-day)
14d20435-e543-5925-b31d-61c96e0754e5 | note | Frequency - 2 cylinders per Lot (same cylinders used for Density)
c4f7131a-fd02-500b-89df-74d7c4827700 | note | Acceptance Criteria - Each sample to be minimum 20MPa.
111b6e38-baf1-5917-9948-a981684b25b2 | note | Reference Documents - Beca Spec 002 13.17.3.6
3b7af89a-2fd2-5582-acc9-75f4d6356f5d | note | Inspection/Test Method - AS 1012.1, AS 1012.8, AS 1012.9
21b83c28-2f3e-578d-bb60-d738036d51e7 | note | Record of conformity - NATA Test Certificate
55d40b35-fd58-5994-8633-3b1846c3e7de | note | TP
0958e6a3-2480-5148-9acc-2707aa8a3eac | note | Responsibility - Project / Site Engineer, Principal’s Representative
322f68d4-95cd-513c-828a-8a12e623888e | date | Date Completed:
b55478d7-beb0-4753-bf39-36b977686a22 | section | 5.0 - Post-Placement
e1ecbfa8-be77-447c-b41f-91a19770aa03 | checkpoint | 5.1 - Construction Joints
f5716e6a-c228-5890-b1fc-6f41bf60ed17 | note | Frequency - Each Concrete Pour
822e004a-cfc8-5701-80c2-b38124bbbd4f | note | Acceptance Criteria - At the end of the day’s works, the HESLC to be feathered out and cut back before work restarts to give a straight, vertical face for full depth of layer.
991e214b-a324-5a1d-8826-35595e7047ce | note | ○ Edges of construction joints shall be painted or sprayed with bituminous emulsion.
9b5838f4-e83f-5d78-a095-9153083db635 | note | Reference Documents - Beca Spec 002 13.11.1
71a40074-8816-5dbb-b8b9-74e7e39b2fb3 | note | Inspection/Test Method - Verify
4ece3e36-a3f0-5e1d-a5f2-d7cef8123b47 | note | Record of conformity - This ITP Signed
38eb2330-8653-515c-9658-2ef5bf5bbc69 | note | IP
b47ea37e-416a-52f4-aaa0-3f28030725a1 | note | Responsibility - Project / Site Engineer
2ad772d0-d82a-544b-b176-7c8f8cd09edf | date | Date Completed:
22888a47-37bf-439a-aa02-1d55dcedade4 | checkpoint | 5.2 - Saw Cut Joints
d844226a-0d5e-5911-ba9a-9f573347673c | note | Frequency - Each Concrete Pour
c1d75f63-edfe-5dc4-a80a-df9412220ffd | note | Acceptance Criteria - HESLC to be sawcut into maximum slab spacing of 5m x 5m. Where pavement width is less than 5m the spacing shall be reduced to obtain slab dimension ratio of maximum 1:1.25.
0274fc1d-a0a1-5c41-b3a1-e58cc2d31cf4 | note | ○ Sawcut to be approximately one third of the layer depth.
a3a692db-5ed4-555c-9df7-2fbfbc1cb6fa | note | Reference Documents - Beca Spec 002 13.11.2
d81f8a7c-3cce-50fb-b821-afe2351f9aba | note | Inspection/Test Method - Verify
0cfdc788-f9ed-5373-9584-c0df96e6f26b | note | Record of conformity - This ITP Signed
9fa58922-7e05-5e5d-8dd9-78ada9d6e23e | note | IP
d562e3e3-50e8-59b5-913e-b8d3ab586c46 | note | Responsibility - Project / Site Engineer
389162fe-6238-54d5-ad14-e21bbe7f3f34 | date | Date Completed:
95953ac6-73b9-49dd-9d69-0640ad1e9571 | checkpoint | 5.3 - Layer Thickness
cea64afc-f762-5e98-9681-6e015b522cb6 | note | Frequency - Each Concrete Pour
b4148477-3aa8-5151-a5de-cf735bb73aaa | note | Acceptance Criteria - Finished surface of the HESLC to be picked up by a surveyor to determine the thickness of the layer.
83c7ed0d-1cdc-5db7-a534-8dbafa9d7d5d | note | Reference Documents - Beca Spec 002 13.17.3.4
a0ad0340-a950-5d9c-be86-bc34d632d744 | note | Inspection/Test Method - Verify
b8e3e630-4b57-5cc8-a59b-1ddec90966ed | note | Record of conformity - Survey Report
0e9c8a07-3c0b-53e7-8f93-fe4d7efaa67f | note | HP
9d171493-7d25-5ee3-a152-aa5861210ad6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91943864-c9ac-5d94-b206-486c43219ac1 | date | Date Completed:
68f9d247-c764-41be-a855-17a6e87826f0 | signoff | AUTHORITY HOLDPOINT
31e8d669-82ee-4911-acf0-3f5040c60faa | checkpoint | 5.4 - Core Analysis – Density
8a32859c-6326-5a94-bfad-3c1b77f0c7bf | note | Frequency - Refer to markup in notes section
93b111bc-6750-536d-b57a-b167d9a3e7ed | note | ○ Aconex: BecaCPL- GCOR- 001038
3cc692e1-73c5-527a-885d-2c57b23acba5 | note | Acceptance Criteria - Cores shall be 120mm diameter.
f644fa61-c994-5fc2-8df1-492456b372fe | note | ○ Calculate the field density by comparing the density of individual cores with the average density of four (4) compressive strength cylinders taken.
b1eddd99-d299-58fc-9453-d33aaefaaf2f | note | ○ Field density to be not less than 98%. If the density is less than 98% then a Hold Point to be raised for the nonconforming Lot.
9676ae89-d884-5414-b875-8640a92ab949 | note | Reference Documents - Beca Spec 002 13.10.1, 13.17.3.6
8c142d85-2d87-5fba-bcaf-b81cf7214dbc | note | Inspection/Test Method - AS 1012.12
699297c0-a312-5aaf-8494-759917f169c4 | note | Record of conformity - NATA Test Certificate
96dab2b9-b40c-59ca-a412-382d18e893d8 | note | HP
360145fd-647c-5054-9656-c4ba6b553063 | note | Responsibility - Project / Site Engineer, Principal’s Representative
666d2443-3749-5d7a-9a1c-0e472a7d14bb | date | Date Completed:
ece3e311-0c3f-4fba-8f66-ecb2ca20e876 | signoff | AUTHORITY HOLDPOINT
19706174-acba-4f32-a556-9d706fc7e282 | checkpoint | 5.5 - Testing Records
063e25ab-0b06-5f4b-aada-48c43a54a028 | note | Frequency - During works
920f3643-3897-547a-9edc-a08af95f34f2 | note | Acceptance Criteria - Within three (3) weeks of completion of the Works, the Contractor shall supply two (2) copies of a report detailing the results of all quality control and testing undertaken.
d9ef0c7f-0d58-516c-8678-ca24c8756a61 | note | Reference Documents - Beca Spec 002 13.17.4
6c35228b-0aa6-54e5-94c2-f2e8784f97f0 | note | Inspection/Test Method - Verify
4c883190-17eb-5617-8001-1c778157c280 | note | Record of conformity - This ITP Signed
e68bc714-671d-5ed5-a051-d8179d95a353 | note | HP
8b8e84ca-616c-59fc-a610-56eeb0503ed9 | note | Responsibility - Project / Site Engineer, Principal’s Representative
1895af9d-ad24-553e-b0e3-93a6ef5f869c | date | Date Completed:
4a36c140-21b2-4a2b-a784-0bc385adbb65 | signoff | AUTHORITY HOLDPOINT
d711f7e7-c7d5-479f-be7c-4355519473d9 | checkpoint | 5.6 - Protection of Layer
24b8d90e-66b7-58b0-9f36-b3ae516dbb09 | note | Frequency - Prior to placing subsequent layer
485c7c4a-6d49-5efc-b6db-01b933afb611 | note | Acceptance Criteria - The Contractor shall protect the HESLC from damage until surface layers are placed. The layer shall not be covered by any further pavement layers under it has been accepted by the Principal’s Representative.
79615dd0-439e-585a-809f-a38198c4a0ff | note | Reference Documents - Beca Spec 002 13.16
297329e7-d81f-56b8-86c1-51f357a9bb22 | note | Inspection/Test Method - Verify
17eade7b-1b04-5cb6-984c-a27b2470e231 | note | Record of conformity - This ITP signed
75dae2b9-d1bf-5796-8a8e-dede46d87257 | note | HP
68d21345-fb7c-5b5f-bc54-aba360ab5f9d | note | Responsibility - Project / Site Engineer, Principal’s Representative
da4a7eb1-e932-5eac-ae88-e84ab23f68f1 | date | Date Completed:
22ceabd1-017f-4aa0-8cea-6d27a135d9eb | signoff | AUTHORITY HOLDPOINT
363ad996-7d75-43a6-aaf5-3344a19cc577 | checkpoint | 5.7 - Removal and Replacement of Defective Pavement Areas
3d0d5f43-8940-51d8-a952-03bed5b29970 | note | Frequency - After completion of works
bdce08f2-e264-5753-8632-35a84e07a7a1 | note | Acceptance Criteria - If required, defective pavement areas shall be removed and replaced as specified herein with pavements of thickness and quality required by the specifications.
5fe8f3a8-d4f6-5512-98d4-d9d20c24efd4 | note | Reference Documents - Beca Spec 002 13.13
bf2d7e60-a9a4-5b2a-8fba-714f41a1b796 | note | Inspection/Test Method - Verify
fe6a6ce0-8a8c-5a7b-ab9b-619775918fbf | note | Record of conformity - This ITP signed
db99968f-a872-5fd5-92bc-a381d79af903 | note | HP
76f382d2-7b39-544d-9219-e8db84c0c486 | note | Responsibility - Project / Site Engineer, Principal’s Representative
7c4db7a6-e8d3-516d-ab5b-f2c780fe2e77 | date | Date Completed:
a9bb2736-b53f-4e46-a4d2-82b7952032ca | signoff | AUTHORITY HOLDPOINT
d4b3bc14-209d-4ad8-a59b-994cf644c80a | checkpoint | Final Inspection
fb09fa88-8452-58fe-9547-4a9286c54640 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
c968d22d-31b1-58c7-bbdd-ee3958476419 | textbox | Print Name:
77552f1a-bb76-5cf3-a1fd-d5ec1f4d22fb | textbox | Position:
70826dfb-3325-56fe-b490-9de374be0465 | date | Work Completed On:
253be1d8-576f-5155-a005-1f7e75432430 | date | Date:
02f54b75-6d21-4c45-bcc5-2740fdfbccb8 | checklist | FH-ZU2-QU-ITP017 - Asphalt Production - 14H Mix - Rev 0 | itp | ITP017 - Asphalt Production - 14H Mix
f86777f9-a770-4934-a24b-541bc96183de | section | 1.0 - Production of Asphalt
eaaec954-116d-4024-87db-232a2a30ee5f | checkpoint | 1.1 - Temperature
2136a98f-0f15-5f52-85c7-06d7028892b8 | note | Frequency - Every loaded truck or at intervals of 15 minutes if more than one truck is dispatched in 15 minutes.
e26f2526-7f2a-5df3-9364-36f41f40718b | note | Acceptance Criteria - ≤175°C
68626ca3-b1c7-5a27-a698-395cb41050cb | note | Reference Documents - Section 407.11(a), 407.15
2abcfc10-e37c-5778-b206-1113eefbbd80 | note | Method - Thermometer
0251ebb7-b7fc-5bc0-98fc-7c23769607e9 | note | Record - Load inspection sheet / docket
d036dbfb-a5e3-5dd5-8486-2e3efa8d4ddd | note | Responsibility - Plant Operator / Technician
88336bbf-a546-5acd-bd41-83c71158ad15 | date | Date Completed:
02b6066e-899d-439a-949b-bf2d3ec2a824 | checkpoint | 1.2 - Temperature
79a510f0-dd9b-58d2-8556-dfe630b98371 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
920a332e-20c5-532e-beb8-53a249d0da72 | note | Acceptance Criteria - ≤175°C
716ca1ed-929b-5061-80ff-5b1fa73e56d6 | note | Reference Documents - Internal
fce07e83-4571-51fd-9a57-b44fc79d50f5 | note | Method - Thermometer
5a440112-749a-586a-888b-be44fb68dd59 | note | Record - Load inspection sheet / test report
e2987813-6e2f-5985-a6ac-262145909a8f | note | Responsibility - Technician
59387d15-698d-5b0d-a743-e95deca5b8a0 | date | Date Completed:
743a8212-06f3-426a-a48f-e99cdecb310e | checkpoint | 1.3 - Visual inspection for segregation, uncoated particles, separated binder, excess binder or overheating
1018d5ac-5d5f-59ff-9719-9e106c2ca447 | note | Frequency - Every loaded truck
2ae6731c-f507-5d24-bdcf-a9be66dd32f1 | note | Acceptance Criteria - >95% coarse aggregate coated with binder, no obvious separated binder or uncoated particles
0c1149d4-90aa-5652-801f-03844b21b09f | note | Reference Documents - Section 407.11 (b)
adfe9b46-8eea-5c12-9109-db5859473831 | note | Method - Visual check
10402f32-95fa-5554-883b-a881b5bf552d | note | Record - Load inspection sheet
d2106aff-5e01-584a-9213-6f8f39e37029 | note | Responsibility - Plant Operator
cfd97c38-5421-5620-b1e4-4c96a69d1469 | date | Date Completed:
040d8861-3f13-47d8-ab6f-7de1efd2e105 | checkpoint | 1.4 - Visual inspection for segregation, uncoated particles, separated binder, excess binder or overheating
a0a3cd7a-8969-57f0-b6a6-f2afa58ca70d | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
58a1b18f-43b5-5782-8950-822e412047b2 | note | Acceptance Criteria - >95% coarse aggregate coated with binder, no obvious separated binder or uncoated particles
2ecac746-9770-52be-957c-2856fe99250e | note | Reference Documents - Internal
1a4c19c5-e9c1-502f-aea6-81c810e62c27 | note | Method - Visual check
250ca365-f8fe-5c62-b2d1-01a23e1baae4 | note | Record - Load inspection sheet
4e8a0022-37b3-5eab-9bf5-e441ce13cc92 | note | Responsibility - Technician
767bcba7-e694-574e-9bb2-33ee214d854c | date | Date Completed:
d78471cf-c969-4471-928b-c942877fdcee | checkpoint | 1.5 - Maximum density
02444fba-2830-54bb-a705-ab1583a61bc7 | note | Frequency - On every production day
74334de1-e815-5bfb-ba81-3b67c6d6ca11 | note | Acceptance Criteria - ± 35 kg/m3 of its 6-point rolling average
65f1c12f-22c0-507b-bfb8-0bb6ac8f984b | note | Reference Documents - Section 407.11(e), 407.15
a123ccd7-18f7-5523-aa3b-7c9103a7fc6f | note | Method - AS2891.7.1
9ef899f2-fffa-5675-89dd-74a9925b4bc0 | note | Record - NATA-endorsed test report
aa50b84a-8988-5a34-b4a3-e914bc380ae0 | note | Responsibility - Technician
27d00282-d869-5768-a3a1-3cb441453f77 | date | Date Completed:
9530b9eb-8080-49ad-9361-898907e44dbb | checkpoint | 1.6 - Binder content
d5c44728-de7b-56e1-855e-7132303988d9 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
4093e520-9d53-5a08-a182-7516042f0d97 | note | Acceptance Criteria - ±0.3% of mix design specification
b00a84b8-7aa1-5e4b-b901-b5a198eaa074 | note | Reference Documents - Section 407.10, 407.15, 407.11
dd8ab117-c9a8-524c-81e9-d173e9ff402e | note | Method - AS2891.3.3 or AGPT/T234
8b6ffe09-c588-5b80-b826-7a1bbfd2b339 | note | Record - NATA-endorsed test report
6d97f0fd-6496-5194-9a83-17f5d888cca0 | note | Responsibility - Technician
df8027cf-71ed-57f1-9f23-ac47475ea03f | date | Date Completed:
b29a3f10-60ef-48ca-a517-26fc00581ffc | checkpoint | 1.7 - Full sieve analysis
f0673b06-a08c-5b88-9219-306a17a575b2 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
1c0c29a2-9aa6-55d5-8694-2f7c3d001351 | note | Acceptance Criteria - See Table 1 of this document
b62f08c9-2498-58db-b7ff-6c1c4882336d | note | – – – – – – – – –
ad595973-74f5-559f-8826-1c783fafd1f9 | note | Table 1: Production tolerances for mix grading (Table 407.101 in DTP Section 407)
1986e833-45bb-5d3d-bfb7-0734c5f003d5 | note | Sieve size AS (mm) ¦¦ Size 7 ¦¦ Size 10 ¦¦ Size 14 ¦¦ Size 20
a562349c-9085-51b6-97aa-5c2969948449 | note | – – – – – – – – –
750b82b3-32bf-5faf-91b5-d1a2f4954f90 | note | 37.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
63bbcf48-8dc4-5e00-9708-fe1412642bf7 | note | 26.5 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ Nil
feff2b7e-4e12-5cdf-a6ba-579ab2e97326 | note | 19 ¦¦ Nil ¦¦ Nil ¦¦ Nil ¦¦ ± 6
309ca4e4-d840-5f85-b6fe-28aecd1ccad3 | note | 13.2 ¦¦ Nil ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6
4e5e2d66-ef24-5631-929a-709514186e50 | note | 9.5 ¦¦ Nil ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
61f2e34a-5c7a-5b05-9751-9c286908d8ac | note | 6.70 - 4.75 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6 ¦¦ ± 6
d5026ce2-fc7c-5121-88f8-cad462df8a5e | note | 2.36 – 0.600 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5 ¦¦ ± 5
4d6a97d1-0796-5cc4-a5e9-8e2ba8104595 | note | 0.300 – 0.150 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3 ¦¦ ± 3
f99a305b-efb0-53e1-92c0-1f24f9fe98c1 | note | 0.075 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0 ¦¦ ± 1.0
5a9d41f4-d17e-5767-b2c9-da52f87f5a97 | note | – – – – – – – – –
b57ad8a8-eee3-5246-8447-20280811450f | note | Reference Documents - Section 407.10, 407.15, 407.11
646a96cf-e543-562d-9a24-918a99a87666 | note | Method - AS2891.3.3 or AGPT/T234
c6a0205c-ae02-5244-82e2-8f57d4b75a7c | note | Record - NATA-endorsed test report
29eeeffa-264f-51d2-b315-51044e0fd4ff | note | Responsibility - Technician
3d932bf7-07d0-54d7-87ae-45508e749800 | date | Date Completed:
763b54f1-29b7-4eaa-bac1-52b4bc08f122 | checkpoint | 1.8 - Moisture content
863688e9-5ca2-5f3a-9a41-3585e2198bb7 | note | Frequency - DGA - One test per 250 tonnes (or part thereof) if lot is >40 tonnes
5bd2c25d-e131-50c2-a5c1-637769a96ab7 | note | Acceptance Criteria - ≤0.5% moisture
2645a2de-a383-5afc-8501-45b50203adf6 | note | Reference Documents - Section 407.11 (b)
f3fb828c-12b7-546e-9438-2a91b5723f9d | note | Method - RC 211.01
5a4cf3ae-3975-59bf-8852-70fe1e08e5c2 | note | Record - NATA-endorsed test report
286f3db1-4a4b-5d83-9a79-524eb1cb5792 | note | Responsibility - Technician
a68a7adb-9b0c-55d8-870a-5ca2bc037fab | date | Date Completed:
1090299c-4a54-4d52-b60f-93012ebb2b05 | section | 2.0 - RAP Testing - RAP Level 1 and 2 (as per Table 407.121 Section 407)
2671db02-eef4-4e14-89d7-ec6052cca18e | checkpoint | 2.1 - Moisture content of RAP
fa4b27d3-15c6-506c-a591-d59718edc1a1 | note | Frequency - One test per 500 tonnes of RAP
569097ff-6fed-5066-b163-48d6b1d87dfc | note | Acceptance Criteria - Not exceeding the maximum moisture content acceptable for the asphalt plant nominated in the RAP Management Plan – Fulton Hogan Infrastructure Services. Any materials with moisture content greater than the nominated moisture content should be allowed to drain before being utilised
4d99a431-c908-5185-b14a-6bc6df2aa691 | note | Reference Documents - Section 407.13(c), FH RAP, Management Plan Section 3.2
2aca144f-9ec3-57d1-a4c4-7ce0f939f963 | note | Method - AS2891.10
b4f62afa-b0ac-5586-ab28-431dc27f1d12 | note | Record - NATA-endorsed test report
d1c25ef9-c694-5a0a-b1db-d5c3b7f9f616 | note | Responsibility - Technician / RAP Yard Supervisor
c7d86439-f754-5e47-af6c-b941c93dc36c | date | Date Completed:
6f582191-4b15-445c-a3ac-b0a7071367d4 | checkpoint | 2.2 - Binder content of RAP
31ba157a-abad-5cf8-9799-db4b3b34fd2a | note | Frequency - One test per 500 tonnes of RAP
7622cb69-d19a-50f2-953f-a94324340172 | note | Acceptance Criteria - ± 0.5 of target binder content
f27ecee2-29b3-5371-a504-1932adef6c00 | note | ○ 1 out of 10 consecutive results is allowed outside tolerance
edfb08bf-fce3-5257-afe0-62d8a94c7708 | note | Reference Documents - Section 407.13(c), 407.11
d82a0091-a207-54f1-be61-9d791adf5d16 | note | Method - AS2891.3.3
a345f482-d7b1-543f-9b56-8c2f19432367 | note | Record - NATA-endorsed test report
ae4ced9e-da1b-5cf9-b76b-df1790026fb0 | note | Responsibility - Technician/ RAP Yard Supervisor
9f1500ff-b0fe-57bb-95ad-2c2ac811d418 | date | Date Completed:
0b835721-220f-4456-a337-c8ec984de7c2 | checkpoint | 2.3 - Sieve analysis of RAP
62e86c66-0fe2-5ded-a7e2-b67de9c29e39 | note | Frequency - One test per 500 tonnes of RAP
b95bc3aa-cc43-5446-86cc-bc51c5570192 | note | Acceptance Criteria - See Table 2 of this document
bac122dd-9df9-57c0-afe8-1515bb54f248 | note | – – – – – – – – –
7efaf993-0f42-5347-b4c1-5a3f5d57311b | note | Table 2: RAP grading tolerances (Table 407.131 in DTP Section 407)
2e960692-6314-51c8-b9f7-68854cead5ec | note | Description ¦¦ Tolerance (from target grading) ¦¦ Allowable number of results outside of tolerance
8d77efa3-47d6-5346-9f34-f86b3093bfc8 | note | – – – – – – – – –
015e08a4-383d-5476-9d79-a6aaaa04dc01 | note | Passing 26.5 mm sieve and larger ¦¦ ± 10 ¦¦ 1 out of 5 consecutive results
96e479ac-1008-570a-99a3-ed582b426d6f | note | Passing 4.75 mm to 19.0 mm sieve ¦¦ ± 8 ¦¦ 1 out of 5 consecutive results
c02f4821-aa32-5c9f-a7b6-fbe8d7242eff | note | Passing 1.18 mm and 2.36 mm ¦¦ ± 6 ¦¦ 1 out of 5 consecutive results
75f728e5-4a9a-55e0-9007-ce97ab775d89 | note | Passing 0.300 mm and 0.600 mm ¦¦ ± 5 ¦¦ 1 out of 5 consecutive results
cd8d2ed2-5fc0-59b3-91a5-17264ce1ed7c | note | Passing 0.150 mm ¦¦ ± 3 ¦¦ 1 out of 5 consecutive results
9d255828-626a-56ff-810b-8ca4f640b4d5 | note | Passing 0.075 mm ¦¦ ± 2 ¦¦ 1 out of 10 consecutive results
4f29aa99-6ce8-590e-b1b0-895c58a2fe7b | note | – – – – – – – – –
1e3611a3-90df-594f-8bf4-8394902af3bf | note | Reference Documents - Section 407.13(c)
0a914e54-db27-5b23-9713-dc16c30e2673 | note | Method - AS2891.3.3
9b5e61aa-9fe1-5b70-bc66-4b2be2389863 | note | Record - NATA-endorsed test report
5682ed41-dfdc-5f26-8a7a-29957d686185 | note | Responsibility - Technician/ RAP Yard Supervisor
9ea1785d-de8f-5d23-8fcb-3f6e4d31e9e7 | date | Date Completed:
9021a7a2-e8e4-4164-a22e-154398838c07 | section | 3.0 - RAP Testing - RAP Level 2 (as per Table 407.121 Section 407)
a70a1afc-6796-4f98-a60c-b1322b06c88a | checkpoint | 3.1 - Binder viscosity
c9b859f2-2f52-526e-b046-dfd87f11dff2 | note | Frequency - One test per 1000 tonnes lot of RAP used for Level 2 mixes as per Table 407.121
638e570c-ad4d-51cb-9036-cce9b4bc8d16 | note | Acceptance Criteria - Viscosity of the blend of virgin and RAP binder shall fall within the range in table
57787fb8-7372-531d-abdf-3e0e09d1b881 | note | – – – – – – – – –
0b8c88ac-b440-5647-a9ba-da4a4e6ccc73 | note | Specified Binder Class ¦¦ Binder Blend Viscosity Range (Pa.s @ 60°C)
b2e34c0d-c16e-5e62-b89b-4ec57bc22a0d | note | – – – – – – – – –
a8c51968-b615-5b12-a5ea-5a9cbf3ba3d1 | note | C170 ¦¦ 170 – 240
ea70d51e-d6bc-5d05-8821-6ff2b17b71d8 | note | C320 ¦¦ 320 – 500
ef9cbafd-cd29-5ab5-b40f-f967279f213c | note | C600 ¦¦ 600 – 880
099695d9-d773-5540-9ee9-4cdb0b41adf3 | note | – – – – – – – – –
e9422418-3469-5762-a057-29d7ca81f80e | note | Reference Documents - Section 407.13(e)
dcab2c91-298e-5731-9c9e-3858ffc3c7af | note | Method - AGPT/T192 or AS 2341.2, AGPT/T193
d3aa5934-9e09-546f-9635-9462a80030ef | note | Record - NATA-endorsed test report
a8a5d9f8-2092-59bf-9ca1-4ea03e650e0a | note | Responsibility - RAP Yard Supervisor / Laboratory supervisor
3ee7ecb4-1890-539b-9896-1db869c75f4f | date | Date Completed:
7a651e5a-b4a3-4d04-9949-cff44d93eb3c | checkpoint | Final Inspection
2d1d16f5-5a8f-5846-878d-ffe1d9a36f89 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
3bd77594-0b9a-56f2-9d5f-cf6a79df486f | textbox | Print Name:
527695d8-93f9-50a2-abf0-56dc7bfce049 | textbox | Position:
1adf7434-14bc-5860-92a1-759173af3782 | date | Work Completed On:
095a949d-a150-58f5-8b0c-171799497afb | date | Date:
5214819d-f3e5-42f9-9366-0a431b043e3f | checklist | FH-ZU2-QU-ITP018 - Asphalt Placement - Rev 0 | itp | ITP018 - Asphalt Placement
9f2884d8-204c-4a8d-8a71-c6e6449c515b | section | 1.0 - Preliminary Activities
f9f9bade-be5c-4e37-9b6f-87558c7464d8 | checkpoint | 1.1 - Check for correct documentation
a5f9aed7-8e63-5dda-9f83-59b1caf55907 | note | Frequency - Prior to commencing works
62caa993-c7b0-5913-ac1d-d31314032ddf | note | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
57a4295e-8bd6-5c03-92d4-379b93c11fa3 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
fb9ae8ff-8531-572c-9794-d1245faeae5e | note | Reference Documents - Current Revisions in Aconex or ACC
d3ea8f0f-7f2e-5f67-ae22-0da0e0523b54 | note | Inspection/Test Method - Verify
3aa525f1-e8c3-5b2b-beb4-fe2bd8f50e49 | note | Record of conformity - This ITP signed
11bb45cb-f28b-524c-b7f4-105132e67009 | note | HP*
78324ebd-00a9-5887-bd39-689ae15436c2 | note | Responsibility - Project / Site Engineer
c71ae7c0-25e9-5c3c-80c3-9f3aa604f96e | date | Date Completed:
1b0d1945-ba45-49a1-bc53-a2c6293444f9 | checkpoint | 1.2 - Implementation of all measures and controls
b68c1335-9ce2-5ac6-94fc-a2752ff12ea9 | note | Frequency - Prior to commencing works
1b6eb168-ef14-543d-8908-f5a6d134139e | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
df3f696c-f4c5-5025-ab6c-982cf912fcef | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
da5647da-699b-5876-b8fe-f39669d4cab8 | note | Inspection/Test Method - Visual Inspection
0548f38b-76c7-5d93-8856-121e4f8636cd | note | Record of conformity - This ITP signed
0c394852-2286-5f12-ad60-a4d52ee11dd6 | note | HP*
b1024191-3b75-5777-9b53-075e00e18054 | note | Responsibility - Project / Site Engineer, Site Supervisor
516afb68-8bdf-5654-8b8d-23388ae689e3 | date | Date Completed:
108cd8a0-6efd-4313-89c5-c1008ebeb015 | checkpoint | 1.3 - Plant & Equipment Check
b042bd38-3294-597e-92f2-cc1403ca2c8e | note | Frequency - Prior to commencing works
051f61f5-5ff2-5606-ba22-ca18522f21ef | note | Acceptance Criteria - Asphalt plant & equipment meeting the requirements of Project Specification.
48f08a81-f61a-50d0-bab9-26102264dde4 | note | ○ Pre-Start checks completed by operators of plant and equipment. All plant and equipment are acceptable for use. Any faults are reported. Standby equipment in place where required.
74d44a80-c7a4-55b3-a0b5-3c32b28ba157 | note | Reference Documents - AfPA Sec 7.1 Cl 91-100
2a1ccd91-733c-5faf-a811-4f132cb811b1 | note | Inspection/Test Method - Verify
022476df-5970-565f-b0a6-0aead13c9076 | note | Record of conformity - This ITP signed
b6103524-bb1a-51cc-9f50-7222fc0f4327 | note | HP*
8283dd86-33c8-5e69-b1dc-a1990bba54b3 | note | Responsibility - Project / Site Engineer, Site Supervisor
db4cb085-a78d-5ed0-86ca-f8c0812b85d6 | date | Date Completed:
0c3e6d21-8357-46e2-848b-15fe6a08b1fb | checkpoint | 1.4 - Tack Coat Material Submission
bf603bbc-8b9a-5609-9c31-24241ba39f7c | note | Frequency - Prior to commencing works
7542c7a2-bac8-55d2-a2b4-12fa0c17b7b3 | note | Acceptance Criteria - Details of the proposed tack coat and test certificates shall be submitted to the Contract administrator for review.
c1d6a3c7-51ff-5df8-b763-4eaa8513b64d | note | Reference Documents - Beca Spec 002, 9.4.1, 9.9.1
3f504c9b-03e6-5e29-8d1e-dd15d83572d3 | note | Inspection/Test Method - Verify
fd0ab66c-99df-5d4d-bcca-df381b2a263c | note | Record of conformity - Aconex Correspond ence
035dfd60-95c4-5688-8116-afff433c2dd0 | note | HP
4fff7910-1b74-5a0a-a10a-8af5a3f88971 | note | Responsibility - Project / Site Engineer, Principal’s Representative
3f20c2e4-acd6-5c46-b2cf-8274b8debc4a | date | Date Completed:
0e5a3f03-50e9-48ac-9206-8bd253c7af2f | signoff | AUTHORITY HOLDPOINT
4953225d-5ded-4192-97fc-21a96922a99b | section | 2.0 - Tack Coat
84bc005b-5e84-4d02-90ec-b11c2423a625 | checkpoint | 2.1 - Surface Preparation
47766e02-13e2-5cf9-949f-d9989cb75713 | note | Frequency - Prior to applying tack coat
b69269c7-9b38-5d4d-9f9d-fdd746b6e0eb | note | Acceptance Criteria - Immediately before applying the tack coat, all loose and foreign materials shall be removed from the surfaces to approximately 150mm beyond the edge of the area to be coated.
8598bb11-aa76-558e-8ec4-469626fea4c4 | note | ○ Tack coat must not be applied on a wet surface, or when the surface temperature is below 5 degrees Celsius.
8e5f6818-1379-5010-a8da-54b575cf5f73 | note | Reference Documents - Beca Spec 002, 9.5
a9f35569-5ae8-5b49-8339-88f474b7086f | note | Inspection/Test Method - Visual Inspection
c7adcae1-e616-5408-b0d5-cba668ad0083 | note | Record of conformity - This ITP signed
ff7d2081-f834-5ba8-970d-795e4aa5f8dc | note | HP
6801e94d-4647-5de5-b39e-d6451b1f9b61 | note | Responsibility - Project / Site Engineer Principal’s Representative
87c9411f-3137-5c10-8215-53bd51008a0c | date | Date Completed:
2a78a280-0174-461e-81e8-0f3926f5db41 | signoff | AUTHORITY HOLDPOINT
3fd7c619-20bf-40f9-9f01-fd2fb7595208 | checkpoint | 2.2 - Weather Limitations
c2a26f77-89f6-5fbb-b122-d418d308c7ba | note | Frequency - Prior to works
eadca574-9ef9-5a8f-bc24-1120ee28f823 | note | Acceptance Criteria - Tack coat shall not be applied on a wet surface, or when the surface temperature is below 5°C, or when the weather conditions would prevent the proper application or adhesion of the tack coat.
fec2bef3-c907-522c-b743-69fc7f4347b4 | note | Reference Documents - Beca Spec 002, 9.7
f901a7c3-7b05-5fc2-92a9-a008f77bd9e9 | note | Inspection/Test Method - Verify
671c43c2-4458-5f70-b0b8-852e1915d8fb | note | Record of conformity - This ITP signed
9370743f-41d9-5cc9-97b9-1ab0fc841db8 | note | HP*
e7f22c4b-8163-5d1a-96c8-4b11dcd4d120 | note | Responsibility - Project / Site Engineer, Site Supervisor
65ee4d3f-d779-580d-a277-bb8b8776c26e | date | Date Completed:
e46bd571-7112-4706-b2b3-2d357f0f9db2 | checkpoint | 2.3 - Application of Tack Coat
ef0cfcc9-1da0-50b0-b3f4-7b4274abe427 | note | Frequency - During Works
6a3523b1-20ec-55cf-b2ad-3f6b38afc9a0 | note | Acceptance Criteria - Tack coat must be applied to the prepared surface at a rate of 0.2-0.3 L/m2 of residual bituminous material, calculated at 25°C.
d869ee84-c759-57c5-a131-73ea86fff1cc | note | ○ Vertical faces of milled and excavated existing pavement must be thoroughly tack coated by hand lance or other method.
7d2587a3-26cd-58b1-b82c-36ed591a89a3 | note | ○ Tack coated surfaces must be protected from construction equipment trafficking to the extent reasonably achievable.
6d4dfb3e-ccc2-50a8-a987-933bc740eebd | note | ○ Asphalt paving must not commence until emulsified tack coat is substantially broken over more than 80% of the surface of the paving run.
53ad700b-f6d1-5d22-9382-331bbdb8c1dd | note | Reference Documents - Beca Spec 002, 9.9.3, 9.6, AfPA Sec 10.3 Cl153-156
a2538ff4-291c-58ba-a121-5252afaa2ad0 | note | Inspection/Test Method - Verify
4f2d60a1-00a6-5951-8702-849c76a20b49 | note | Record of conformity - Spray Rate Record Sheet, This ITP signed
679563c0-0697-519c-81fe-754fa5acc007 | note | WP
5cc1ec7a-434b-5737-82c9-b7243c0f60b6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
e2d25fa6-6833-5d61-a723-54a4e5a00bb9 | date | Date Completed:
64658685-fe27-4cdd-ac2b-4549a7330c9a | checkpoint | 2.4 - Test Certificates
a9a27fd4-abdd-55e4-b628-8556a7264c61 | note | Frequency - During works
ea3f92ac-7f6d-5770-b520-e1f4082498fa | note | Acceptance Criteria - If during the progress of the work the Contractor desires to use other materials or materials from other sources or materials produced from the same source using method of production different from those originally agreed, new samples shall be taken and tested and the results shall be submitted to the Contract Administrator.
810325e0-6ac2-5c81-872c-2b59960d405d | note | Reference Documents - Beca Spec 002, 9.9.1
2bf44c31-b1c7-53bc-9d70-80f6a53d8372 | note | Inspection/Test Method - Verify
de741aeb-88bd-5092-a94d-c31c91b612c5 | note | Record of conformity - This ITP signed, Test Reports
b8c777fc-0cc4-5934-ac6c-ffa5b957dc28 | note | HP
c84bbd9e-5aaa-5cb0-a7ec-460b5d7bef4b | note | Responsibility - Project / Site Engineer, Principal’s Representative
c42c3400-4221-5ffc-8501-61cf1d41b774 | date | Date Completed:
31f66bbc-f152-4adf-a435-516b83d5180f | signoff | AUTHORITY HOLDPOINT
e2542c4c-923f-4bc0-9f2a-f62375759b49 | section | 3.0 - Hot Mix Asphalt Placement
4ba75adf-7760-45bb-bb6f-355827c08a53 | checkpoint | 3.1 - Construction Trial
b84d28a8-9929-5d70-97ff-0e53d10f2b2c | note | Frequency - Prior to commencing works
4a17730b-d2bf-5cad-8d96-683cf8140c42 | note | Acceptance Criteria - A construction trial must be completed as per the requirements in the specification.
c5772dad-ba86-5906-8dc2-e89e0a85ca84 | note | Reference Documents - AfPA Sec, 8.3 & 8.4
e6511b96-c544-5242-bf12-12564331e895 | note | Inspection/Test Method - Verify
c465d417-fa23-5b16-9644-7448e5707044 | note | Record of conformity - Aconex Reference
5ebc8428-cf20-5234-8445-d1c3b84bb012 | note | HP
2d827f24-bba3-54dc-89ea-c194c2cd0ae7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b8e798a4-b66e-5aae-a948-b342729a707b | date | Date Completed:
37ee13db-6271-4db5-96fb-a829a16ee48d | signoff | AUTHORITY HOLDPOINT
5df4a6be-d7f6-4f8e-9d1b-509eca6c9074 | checkpoint | 3.2 - Ambient Conditions for Placing
79839c47-2778-51bc-86d9-fd04a46d1e58 | note | Frequency - Prior to placement
c2838b20-7eb8-5a2b-b2d9-e61b4457693d | note | Acceptance Criteria - Asphalt must not be produced and constructed during weather, or expected weather, that may be detrimental to the quality of the finished asphalt surface layer(s).
bc654fdd-f7b9-5290-8c58-718e4fedb8b3 | note | ○ If required, where the existing surface temperature is below 15°C, the Contractor must develop and submit cold weather construction procedures for the Contract Administrator approval.
d73b971c-0d21-59af-9adf-0dbe751cc05b | note | Reference Documents - AfPA Sec 10.1 Cl 145-146
09f2a1d3-41d7-547a-85ca-7e75c1d9869a | note | Inspection/Test Method - Infrared Thermometer
55b086f1-c840-5443-b5be-c5b98739870c | note | Record of conformity - This ITP signed
73f0e451-f488-5e78-8bd8-07f9e6e6cbfc | note | HP
14286aa6-2b9a-5dcf-802f-e0b1f5365bae | note | Responsibility - Project / Site Engineer Principal’s Representative
5b5620cd-5938-5f07-986d-05d56fbd3ce7 | date | Date Completed:
d34b09a5-878a-41bc-899d-f558efdff5ab | signoff | AUTHORITY HOLDPOINT
15e52648-fbe7-4534-b4b4-46fe42c3932e | checkpoint | 3.3 - Surface Preparation
79e3704d-42f4-5643-8fb8-729e37e6326d | note | Frequency - Prior to placement
3ce9eecb-71b2-5e1a-8f8e-1c7d03133187 | note | Acceptance Criteria - The surface on which the asphalt is to be placed has been jointly inspected by the Contract Administrator and the Contractor, and it is agreed to be suitable.
fd35128b-8025-5291-88b5-5a87bb4468f4 | note | Reference Documents - AfPA Sec 10.2 Cl 147
84e8b29c-c59b-51a3-9526-afa88ef46280 | note | Inspection/Test Method - Visual Inspection
4983c872-056d-5676-a87b-609a7b4f0aa0 | note | Record of conformity - This ITP signed
1f503468-09a6-5523-b76f-27db8e2f5976 | note | HP
d41d03ea-96de-552d-9569-834480f7b52b | note | Responsibility - Project / Site Engineer, Principal’s Representative
9232169d-ad2c-574a-935c-862b37671421 | date | Date Completed:
5a4d6fa6-eff8-4908-aeec-2541fc0bd6ee | signoff | AUTHORITY HOLDPOINT
142b296d-56a3-4576-9c5c-0b29f6f3bbfa | checkpoint | 3.4 - Asphalt Placement
0f3da3cd-bc5d-5689-aa59-8652039ec1dc | note | Frequency - During Paving
76ec15fc-338e-541d-b5a2-5821ed495eb9 | note | Acceptance Criteria - The following processes to be monitored with the Contract Administrator to confirm consistency with Construction Trial:
6e637df4-83cd-5d3e-ab89-19ece676732f | note | – Roller patterns
0a89e57f-8c51-580f-8e00-935758dde67d | note | – Surface texture within paving lanes
71c92926-13dd-5961-8478-373fe002cb12 | note | – Surface texture at the joints
134582bb-dff3-587c-94b9-7575c09e6eff | note | Reference Documents - AfPA Sec 11.4.1
cb4e5f95-4459-54f8-a91f-0ee027ab93c3 | note | Inspection/Test Method - Verify
82daf4a7-2650-5b15-8fd6-5a714933d924 | note | Record of conformity - This ITP signed
85015cef-7985-54f2-9768-8b468e2cc983 | note | WP
5094bbd6-ac4a-5586-8670-9b177d36c2b7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
870b5305-8aa7-5028-9197-2a9d4405b024 | date | Date Completed:
5a7a5f30-cd93-45ca-a0a3-4fd0ba23f096 | checkpoint | 3.5 - Longitudinal Joints
619d9178-dc5d-52cb-bf6b-859e782302fa | note | Frequency - During Paving
0925c409-735c-560d-a580-ebd41d244628 | note | Acceptance Criteria - All longitudinal joints shall be constructed as hot joints (exceeding 125°C upon placement of the adjacent paving run) unless restricted by staging constraints or in constrained working areas.
0e2ef384-b47f-517e-8f79-387d9bbd0b0a | note | ○ Gas fuelled infrared joint heaters may be used to reheat the joint and create a hot joint where the measured temperature has not fallen below 90°C.
c9d82ab5-3da3-5f24-82f0-df129a7af676 | note | Reference Documents - Beca Spec 002 10.5, AfPA Sec 10.4.4
39df120d-2163-5a39-a86c-214aedbd31ae | note | Inspection/Test Method - Verify, Infrared Thermometer
171bf6f6-35cb-557a-8111-8fab28ad0d77 | note | Record of conformity - This ITP signed
4adb2a41-7300-5dcf-ac31-251a81331fa4 | note | HP*
60547fd5-58c6-535d-a8a3-c9436bb0bd51 | note | Responsibility - Project / Site Engineer, Site Supervisor
934ed53a-3fa4-54ea-a96c-11ef015fef21 | date | Date Completed:
9d1b5089-fbca-4929-acef-8c10a2267407 | checkpoint | 3.6 - Surface Finish of Wearing Course
21fcb48b-1259-5831-ab67-4ea5876059c7 | note | Frequency - During paving and after final roll
5596fd42-29d0-5d18-bd3e-850dfbe73e60 | note | Acceptance Criteria - The finished surface of the asphalt must be a tightly bonded, closed textured, surface of uniform appearance, free of dragged areas, cracks, segregation and open textured patches. Joints must be tightly closed. Surface finish must be consistent with the asphalt construction trial.
c5ba9a73-63fd-5815-b26f-6871758a4b4f | note | Reference Documents - AfPA Sec 12.4.1 Cl 288-291
a35847a5-a752-5894-a474-1d74a5aeda7e | note | Inspection/Test Method - Visual Inspection
8845183d-ac15-504f-9673-cc51e4e2a444 | note | Record of conformity - This ITP signed
d8d46058-0cd3-562d-abc1-6baaf6ef4c00 | note | HP*
0824a6e9-4325-5c3b-a8fa-dd30a620d63f | note | Responsibility - Project / Site Engineer
fdd7b257-b107-5384-826e-f90f5e6565d0 | date | Date Completed:
8cb930ae-52c9-4e44-8e8d-2eba25935a42 | section | 4.0 - Compaction Testing
65918363-6123-4bbf-a500-09863b051283 | checkpoint | 4.1 - Compaction Testing (AfPA Mix)
5b5e0720-9ba9-5ca8-b6b1-e76d0a53d518 | note | Frequency - See Note 1.
990733fb-00d8-55f6-bd8e-d1af740d4de1 | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
07cb5bd2-2c4f-5f50-8bf4-1b8e14c1e604 | note | For test locations away from joints:
bf682df4-a28a-50ae-a8fc-dbe8587a2967 | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
c9a25a06-f594-55c1-93a2-cd84bb394fd7 | note | ○ Average Air Voids: Minimum 3% and Maximum 6.5%
65758bb4-6d1e-560e-b938-2478bee7b78c | note | For test locations on longitudinal joints:
16e1d95b-6321-5b92-a5e3-dce46f78dfdd | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
b077ab9a-869d-5b8a-9681-137185741295 | note | ○ Average Air Voids: Minimum 3% and Maximum 7.5%
5c99acb6-bb52-51bf-917c-2492ca5d594c | note | Reference Documents - AfPA Sec 12.4.2 Table 22
c075ad1d-7fa5-53b7-b9a3-b57a30a0c645 | note | Inspection/Test Method - Verify
f20839b2-94d2-5d01-a79b-734c6462b437 | note | Record of conformity - NATA accredited test certificate
c4571efc-9490-5578-a62b-cfe0cebe1985 | note | TP
bef2ed99-72f7-5036-835a-9f27ea19b464 | note | Responsibility - Project / Site Engineer, Laboratory Technician
fc5f5a58-40dc-5d7c-9c3a-8ca819ada0e0 | date | Date Completed:
099bf5a9-42e3-4058-8cfb-a636699af661 | checkpoint | 4.2 - Compaction Testing (Type H Shoulder Mix)
9b48356e-602d-559e-8a70-19606954c66f | note | Frequency - See Note 2.
a8551a37-bdba-521c-80f9-474ba6a6831d | note | Acceptance Criteria - The in-situ air voids content to be determined using calibration between the nuclear density gauge (NDG) and the asphalt cores developed during the Construction Trial.
0c7e4376-0e2c-5857-924b-0120a7ed0450 | note | For test locations away from joints:
107aea62-354c-53e3-9115-eb9771885bcb | note | ○ Individual Air Voids: Minimum 2% and Maximum 8%
473a830d-3b43-58bd-9e47-4a383d38304e | note | ○ Average Air Voids: Minimum 3% and Maximum 8%
2ba06b15-8b0b-5278-9835-4f90f88aa04c | note | For test locations on longitudinal joints:
5afbb6a7-a4a1-560e-b022-82e9bad1ac09 | note | ○ Individual Air Voids: Minimum 2% and Maximum 9%
6d90001c-c503-5e9b-8633-69a430cf8c68 | note | ○ Average Air Voids: Minimum 3% and Maximum 9%
cc46bb88-056d-53d7-82ce-d6c48ca4ae8f | note | Reference Documents - AfPA Sec 12.4.2 Table 22
b0191cb8-548b-5422-bde2-f41df3842d66 | note | Inspection/Test Method - Verify
d1b883be-5e5f-5ed4-b140-3befcf9b1ad2 | note | Record of conformity - NATA accredited test certificate
3fbdf891-67af-5c38-ab0c-79f738d20de3 | note | TP
6be359d7-c79a-5104-bb58-32105d588c66 | note | Responsibility - Project / Site Engineer, Laboratory Technician
285591af-2d8b-5f00-927a-b4fc49ea144c | date | Date Completed:
18252a39-32ab-442a-9d38-6c7bfe17dd9d | section | 5.0 - Completion
f135dadf-31b5-4ee1-8ff7-5a5dd8677e8c | checkpoint | 5.1 - Surface Smoothness Testing
c5b297c9-1eaa-5d22-b991-d7370db8f6b4 | note | Frequency - After completion of pneumatic tyred rolling
b8ef7f30-9a88-58b1-a959-233eb3238049 | note | Acceptance Criteria - The finished surface of the surface layer must not deviate from a 3.5 m straight edge by:
1c97bc8e-013f-5cc6-9051-95b3b7691b8f | note | – Full Strength Pavement (AfPa Mix)
a52d80a4-e60a-5e0c-a30a-08ce049272a0 | note | o Longitudinally: Max 4mm
2667ae6b-1201-57c3-910f-80419cb48b72 | note | o Transversely: Max 6mm
76e76f41-9bd0-57f9-a873-544c2cbc3215 | note | – Shoulder Pavement (14H Mix)
cd9cc2e5-680b-5aa0-94d7-a143aab8c022 | note | o Longitudinally: Max 6mm
b8766bfd-c89f-5557-8d40-dce12e9795bc | note | o Transversely: Max 7mm
b15d9a54-5ff8-57ac-973a-23ba0bcb77c5 | note | Reference Documents - AfPA Sec 12.4.3 Cl 293.
45da2edb-bcd3-5f1f-82f4-b03962d62b13 | note | Inspection/Test Method - Visual Inspection
cfe9e470-6d0b-5f2b-88ac-6e6d1c58af01 | note | Record of conformity - This ITP signed
61c443ad-591f-5ec9-a841-8ded3f0ddbe6 | note | HP*
624295ee-5c1c-5bf9-a4e3-eaf1381950f9 | note | Responsibility - Project / Site Engineer
a264105a-ffcc-579a-9d8b-8c89d1dae253 | date | Date Completed:
43fe13a2-0a84-4e51-82f6-ca67366a4941 | checkpoint | 5.2 - Finished Surface Levels
66876240-1348-5152-ac6d-41ce6367c2df | note | Frequency - Per Lot & Per Asphalt Layer
4cefae3a-08a3-5f96-80cf-af2c2804403e | note | Acceptance Criteria - Surface level must be as per following:
3c26b3ae-1fd7-5f3d-bee0-61edba6d1384 | note | – Full Strength Pavement (AfPa Mix)
c9ad5d4a-fd55-5803-8cfa-519b19ad020b | note | o ≥95% of the deviations between design surface level and finished surface level must be maximum 7mm.
2ad96614-1c2b-5c2c-b8cf-fdaa3b4d1095 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
914f0b94-6f35-5076-9c01-9f1643c1286e | note | – Shoulder Pavement (14H Mix) (14H Mix)
ffaa615c-26b4-5a2f-a2d0-a1ed3a8c9fee | note | o ≥90% of the deviations between design surface level and finished surface level must be maximum 7mm.
59bb3e47-78dc-596d-932a-d61366e367c5 | note | o ≥95% of the finished surface deviations between design surface cross fall and finished surface cross fall must be maximum 0.3%.
9c5be199-f41d-51ef-a6b0-5b574c0a900c | note | Reference Documents - AfPA Sec 11.5.1, Sec 12.4.5 Cl 298-299
22178bd7-0fcf-5c93-a8ab-c2723d84fd25 | note | Inspection/Test Method - Verify
7e22766e-22e3-56d7-9c4c-e9df49aa9a3d | note | Record of conformity - This ITP signed, Survey Reports
e7c89dad-45b0-551d-8de5-254576255443 | note | SCP
988132d4-0915-57d6-bde2-14bab73e2dcd | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d806959-75fa-5932-be18-d1cb9f89ec36 | date | Date Completed:
b253de93-fa93-48b5-a4e2-0c9980e58583 | checkpoint | 5.3 - Surveyed Average Layer Thicknesses
63e6e4f7-0a51-5e46-9448-c0f8df6a6857 | note | Frequency - Per Lot & Per Asphalt Layer
405b7330-f7cf-56e1-9351-f2a60f83585d | note | Acceptance Criteria - Average layer thickness must not vary by ± 4mm from nominal thickness.
f9a244f1-abe1-50a7-9fb4-8eb14124edde | note | Reference Documents - AfPA Sec 11.4.5 Cl 247-248, Sec 12.4.4 Cl 294-295
1d83e7a2-aaea-5045-9c0d-22d3430eec75 | note | Inspection/Test Method - Verify
578da9fa-c510-5aad-ac01-c3e36ce4ee63 | note | Record of conformity - This ITP signed, Survey Reports
d48ca06e-97df-596d-918b-21331cd7c500 | note | SCP
de4108f9-392a-53d2-9ef1-b3a49aa27687 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a770faed-91f7-5d62-b114-4a6ef6765ce8 | date | Date Completed:
a5eb0caa-ec90-4ffb-a402-1b1c3a0c235c | checkpoint | Final Inspection
a2ac3a83-86a1-5bf8-b2ff-78c908b1a89d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
594d0e9b-0456-5ab9-ae14-07100c0e9d21 | textbox | Print Name:
248be112-e257-515d-be95-4a4ca261c02a | textbox | Position:
42c4f1e7-3c8c-538f-acb9-b809dabca7df | date | Work Completed On:
ff9187ca-a632-5f3b-8c55-892c5854bac5 | date | Date:
f8615df5-4fd1-4e1a-957a-48b320d5cd93 | checklist | FH-ZU2-QU-ITP019 - Spray Seal Placement - Rev 1 | itp | ITP019 - Spray Seal Placement
e8bcd4ad-4c6e-425f-9433-981140c4ac85 | section | 1.0 - Preliminary Activities
57149455-e3a9-4ad5-b430-af51d0a24901 | checkpoint | 1.1 - Check for Correct Documentation
99d26f55-d53b-5be9-919d-f74e244ca72b | note | Frequency - Prior to commencing works
f44b925b-8ef3-5cbf-9564-c18048cf1da7 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
fd728d1f-dbca-598f-9a99-380ce33e6d02 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
385bde3c-18ea-5756-af9a-b177f4adb1f1 | note | Reference Documents - Current Revisions in Aconex or ACC
a1ce4557-03f4-56fb-b37d-e20fd3a97e9a | note | Inspection/Test Method - Verify
9ae40c17-71da-5e69-bf13-bed52a2dcc8a | note | Record of conformity - This ITP signed
ea1bf8a7-8bcf-5839-b274-32d5f5d551e0 | note | HP*
4970d0c4-183e-511b-91e6-99185641679a | note | Responsibility - Project / Site Engineer
cf668b44-5796-50eb-b82c-3a3544c86e42 | date | Date Completed:
e6fe80b7-4f90-4fdd-8026-1a074f6808cc | checkpoint | 1.2 - Implementation of all measures and controls
515120e3-76b8-51ab-b2b7-8575773312c4 | note | Frequency - Prior to commencing works
e4195976-f45f-5f6c-9bff-330c716b3ef3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
946ef10d-cc61-510c-810b-1c33215ca0e5 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
6407e481-51ff-5c31-bdeb-c4bd3b171a2e | note | Inspection/Test Method - Visual Inspection
68c2ba93-d343-5ef3-b7a2-03296d418963 | note | Record of conformity - This ITP signed
1f5e4321-6d40-55ba-b88f-4d8a837ad394 | note | HP*
e99d7166-ace9-52a2-b86a-1b8473160663 | note | Responsibility - Project / Site Engineer
19946092-3c09-5298-9e35-05f392ce81f1 | date | Date Completed:
d23305ae-bacf-43fa-b4b5-d08430aa855b | checkpoint | 1.3 - Plant & Equipment Check
9a2b3deb-4d64-50b5-85a9-039b86918458 | note | Frequency - Prior to commencing works
279b0fe8-bad9-5bab-8b28-1a4cef298b56 | note | Acceptance Criteria - All equipment shall comply with VicRoads Section 408 and VicRoads Bituminous Sprayed Surfacing Manual.
b0a61a36-6acb-55d1-aef5-93a93bf4ad11 | note | Reference Documents - Beca Spec 002 - 12.3
4e9e834e-f65f-50b1-80e9-176cc7e50741 | note | Inspection/Test Method - Verify
305535f9-f829-5f08-a2f4-f9b183621e3e | note | Record of conformity - This ITP signed
c4287885-cd53-5223-b23d-ebd5531c6f3f | note | HP*
401e6ef2-678d-5abb-9c2e-fe54abe0e62f | note | Responsibility - Project / Site Engineer
f76a6910-fd36-5143-b7cb-7c09734ff325 | date | Date Completed:
86e65bcb-0044-42c5-800f-41bbe5723b10 | section | 2.0 - Materials
51c9704a-2a0c-4520-9081-782837612c4a | checkpoint | 2.1 - Material Approval
0180bf66-82fe-5bdf-b75d-a5a3a494916a | note | Frequency - Prior to Works
b7f612c1-825d-5eca-82ac-c5078adca858 | note | Acceptance Criteria - The binder used shall be class 170 residual bitumen complying with AS 2008.
ad3c639b-e0c7-5c6c-9468-955e077988f7 | note | ○ All aggregates used shall comply with VicRoads section 801 and 831. Material and Test Reports to be submitted to the Principal’s Representative prior to commencement of works.
4b76e043-3a96-5d84-9078-cf3a5e38d0fb | note | Reference Documents - Beca Spec 002 - 12.6.1.1 to 12.6.1.3
1c829db9-cd91-555c-9bf6-2690806079dd | note | Inspection/Test Method - Verify
026372fd-6f92-5df9-85e1-172497381ef3 | note | Record of conformity - Test Reports, This ITP signed
306957d8-b06d-52b1-a97f-0cb06468180b | note | HP
5960453d-3adb-5f5c-aa48-22864a93455a | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a2f89ba-db0c-5606-92d1-5c6c6f1f3ea3 | date | Date Completed:
6b43d63c-ba7a-5475-83d2-8e8eb4441002 | note | Principal’s Representative - DCWC Mgt-GCOR-009596
a44762f8-fe22-4af4-9ad6-f40ced12d155 | signoff | AUTHORITY HOLDPOINT
8a2cad47-c623-4226-a99f-55e64477505a | section | 3.0 - Construction
0336702c-135e-4a8b-ad26-5e786bff34ef | checkpoint | 3.1 - Underlying Surface
b55c9220-1218-5b6b-9965-d5a620d7c5c5 | note | Frequency - Prior to works
8a6942f8-87cf-5f67-93a5-19f8b664c1bb | note | Acceptance Criteria - The pavement surface should be cleaned to remove all mud, carried on material, dirt and dust.
a1905cf2-aa5d-5c68-a05d-e3ea0e2adf5b | note | ○ After cleaning the surface should be swept with a suction sweeper, supplemented by hand brooms where required. Seal coat should only be applied to a sound clean dry surface.
c4b95760-ee66-5f4b-967e-ae1bd2dbbe9e | note | ○ Preparation of the underlying surface shall be approved by the Principal’s Representative.
da482898-a99b-564f-bf91-ea0730671827 | note | Reference Documents - Beca Spec 002 - 12.4.1 to 12.4.5
907dac99-ae2e-5ab5-ba6b-e820b1135a56 | note | Inspection/Test Method - Verify
6b71389b-b533-5318-bf2b-2369ac003a3a | note | Record of conformity - This ITP signed
e732b59b-9a25-55a6-a246-675f1888c65c | note | HP
dec31d14-7e78-5705-981d-5900356a0d60 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a94e1b2-3c5a-554b-83fa-72558f4fe7f0 | date | Date Completed:
389b6e60-5f91-4cee-8bac-b00d91a6eb23 | signoff | AUTHORITY HOLDPOINT
bc827790-c421-43a3-b33a-9c4c2631347f | checkpoint | 3.2 - Binder and Aggregate Application
460ff129-e91b-5d1c-8557-f539998c1c2a | note | Frequency - During works
e9108c97-6a3c-5c77-9af1-b4d273309262 | note | Acceptance Criteria - Application rates shall be:
e5dc51ac-c7a5-53f0-a742-63910cb561d0 | note | ○ Binder: 0.8 – 1.2 L/m2
55f29abb-e7ad-5805-bcf6-8c98d32ca74b | note | Refer Aconex: DCWC Mgt-RTRFI- 001272
10bcf56c-1534-59b1-a1b9-5cb997b62e67 | note | ○ Aggregate: 8 – 10 kg/m2
17fc8aaf-1094-56d0-9a29-213c3b45e032 | note | Reference Documents - Beca Spec 002 - 12.6.2
91bd4695-dbc1-5301-83a8-d81418984ff4 | note | Inspection/Test Method - Verify
afeecce6-979e-5a3f-b14e-964698b0d649 | note | Record of conformity - This ITP signed
22069dc3-6f08-5b8a-a768-17492cc4da03 | note | IP
f1650274-2108-54b7-9557-c47b13242630 | note | Responsibility - Project / Site Engineer
caa491e8-6357-53b2-9b3f-896606b18a58 | date | Date Completed:
3558efa7-7cce-4cc8-a9b7-c5c80dddb2a0 | checkpoint | 3.3 - Aggregate Spreading
5aaaeec4-daca-5031-82ff-6f3d20e0dace | note | Frequency - During works
90f2b260-756d-598a-b1d5-115f70a2538d | note | Acceptance Criteria - All aggregate spreading shall be undertaken using forward aggregate spreading and discharge plant.
e9df92de-0853-5fdd-9e67-e76b4b0e2b1d | note | Reference Documents - VicRoads Section 408 – 408.13(e) to 408.13(f)
91deb454-fb48-5ee9-9a00-d53385df6b64 | note | Inspection/Test Method - Verify
376bbbbc-c41f-5c66-b4b4-251f3de0f271 | note | Record of conformity - This ITP signed
3e762456-f42d-5369-96e4-1f2d7569ccfb | note | IP
3b210cfd-cb73-54cb-90ce-9757b15569b8 | note | Responsibility - Project / Site Engineer
b95944c8-e12b-577c-825d-a7fc3c9a1fff | date | Date Completed:
ecb510a8-5206-4b93-9181-49dc76567198 | checkpoint | 3.4 - Rolling of Aggregate
a7fce128-f8e8-5077-bf89-7a3c37aa1b55 | note | Frequency - During Works
d22150a9-200e-5a7f-8cdd-186dba96b56f | note | Acceptance Criteria - Rolling of aggregate shall be undertaken over the full width of the pavement being sealed. Works to be undertaken by static rubber tyred rollers or otherwise approved by the Principal’s Representative.
e464d500-9632-55b9-b873-6bd8740f7323 | note | Reference Documents - VicRoads Section 408 – 408.13(g)
7f6376ab-8124-5c2d-84c6-2bb3a7bd4e99 | note | Inspection/Test Method - Verify
2049228d-37a6-5e50-b5f9-90730444ff19 | note | Record of conformity - This ITP signed
123b39ab-4d8b-5fda-846f-2b4fa2145053 | note | IP
93355f4f-e6ed-5e20-b491-da8d2e372b00 | note | Responsibility - Project / Site Engineer
8672d42b-ebe7-550d-a954-d270e4c03e8a | date | Date Completed:
f94df72a-e1c3-4079-b178-e65baa3d3c27 | checkpoint | 3.5 - Removal of Loose Aggregate
086d6c37-30fc-500b-bd7b-dac102a3cd08 | note | Frequency - During Works
0f19303d-5fc5-5200-b707-0294471d0d79 | note | Acceptance Criteria - At completion of sprayed seal treatment, the Contractor shall remove and dispose of all loose aggregate.
18eef251-bc87-5480-ae5b-f73eab77b998 | note | Reference Documents - VicRoads Section 408 – 408.14
cc9ae318-b7a0-5772-bddf-62c993fee511 | note | Inspection/Test Method - Verify
8a30db57-cb6a-558c-b399-f5afba5e132f | note | Record of conformity - This ITP signed
0af44172-96bd-5bed-a873-9c16b72fdd11 | note | IP
e96c6382-4a04-500f-91bf-2d846f2d2fe3 | note | Responsibility - Project / Site Engineer
eb44069f-d261-5957-951c-6b9cb9c899f7 | date | Date Completed:
ee618c11-52bb-4dd3-9c47-0be815c7da71 | checkpoint | Final Inspection
093a37ab-ed53-55a4-8356-00f47ef65b7d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
7d02be77-d93e-5a61-8cb6-2a7e1eb9340a | textbox | Print Name:
b229b7f5-c9f1-5ed5-9d70-14a8e2cdcc0a | textbox | Position:
4e1a7de0-332c-5b3b-9cb1-37894f0e6a5b | date | Work Completed On:
e70f894e-7cbb-5c5b-8ee6-58631cf99e2c | date | Date:
b8376c32-7bdf-4fda-aac9-ba46ae4e16bc | checklist | FH-ZU2-QU-ITP020 - Prime Coat - Rev 1 | itp | ITP020 - Prime Coat
a1e0cb8c-28cc-424c-a78f-7fe526521fc2 | section | 1.0 - Preliminary Activities
1c0bdf25-0790-4f04-9077-28744eba5206 | checkpoint | 1.1 - Check for correct documentation
80e5f155-88d5-5bcd-ad99-df4b0aa779bf | note | Frequency - Prior to commencing works
fa088635-6c35-5834-bf44-3c991561f76b | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
cf1d362b-a3f0-57b5-b609-b432a06fce79 | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
64334896-b042-5621-9ccf-8c4ea78a093e | note | Reference Documents - Current Revisions in Aconex or ACC
60d86afc-e4e5-5400-910d-b781e2c1d2f8 | note | Inspection/Test Method - Verify
38f6b59d-c829-5bca-9a30-6991bd840622 | note | Record of conformity - This ITP signed
090a4366-69ed-5b45-b3fe-28db780f2220 | note | HP*
4b1083bc-f58e-5105-9dca-8cb800f274fb | note | Responsibility - Project / Site Engineer
ef660620-3032-56b3-9d60-7fd7b4e39609 | date | Date Completed:
6c32f2ec-3e86-4bbf-8f8c-f2f619a03918 | checkpoint | 1.2 - Implementation of all measures and controls
d195e0c3-5608-569b-8fb1-e9a47e8db907 | note | Frequency - Prior to commencing works
9781b6d1-2003-5001-a1b2-ef0efc3311f0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
ab7d6a29-018a-5822-9d9f-e2a713da4961 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
fcaee547-ed53-5cc0-8382-af25d76b5701 | note | Inspection/Test Method - Visual Inspection
083c25b2-2d46-500a-9a4f-c0ef5c2be2a9 | note | Record of conformity - This ITP signed
552fa7c7-a655-5b9c-bb10-711a3e743a9b | note | HP*
a58521ca-b4e7-5e86-b970-de24b28d6237 | note | Responsibility - Project / Site Engineer
1dbf899d-f489-5014-99f0-1b3c7b6d278b | date | Date Completed:
0a8af407-f3e0-4db0-a9a0-b4e782f6cd47 | checkpoint | 1.3 - Plant & Equipment Check
81e69d9a-5b44-5a8f-97f9-ce234fc7934f | note | Frequency - Prior to commencing works
de60ea39-2dc1-537a-8055-1bbcd19fdb31 | note | Acceptance Criteria - The Contractor shall provide equipment for heating and uniformly applying the bituminous material and blotter material.
1d90ffca-4aeb-5243-bd6e-4a3fc9a5f562 | note | ○ The bitumen distributor shall comply with the requirements of NAS 70: ‘Bitumen Sprayers’
e9e12f20-535b-54d5-83bb-156ac23d53b8 | note | Reference Documents - Beca Spec 002 - 7.3
42cd1320-3e39-55fc-a72a-00de41869e8a | note | Inspection/Test Method - Verify
680136a9-700a-5c42-96fe-f6a727c2a548 | note | Record of conformity - This ITP signed
72d6fd55-3c22-557a-b5e6-70b7c1db44a0 | note | HP*
3d9c33c4-db18-594b-a41c-b41ea185598b | note | Responsibility - Project / Site Engineer
88ffee46-8ff3-53f4-8227-30547653838b | date | Date Completed:
bbf324f0-fc6b-4983-8b48-4014871db62e | checkpoint | 1.4 - Weather Conditions
0f3982b2-bce5-5f5e-a2bb-71b976f8ecef | note | Frequency - Prior to commencing works
4805e412-0a30-55d6-af8b-97c13f793f9d | note | Acceptance Criteria - Prime coat shall not be applied on a wet surface, or when the surface temperature is below 10°C, or when the weather conditions would prevent the proper application or adhesion of the prime coat
d5f38335-254e-5f61-87c6-2ade1cc6f1dc | note | Reference Documents - Beca Spec 002 - 7.9
b67973ed-5400-544b-abcc-eb581fb36be3 | note | Inspection/Test Method - Verify
3c9d6a8f-19cb-58ca-a6df-7fe4ab9e183e | note | Record of conformity - This ITP signed
30700ce1-4ee6-5f7e-9317-366c06df8d7f | note | HP*
21402070-1d8e-57f4-b7fb-812c8ea5873a | note | Responsibility - Project / Site Engineer
68cbdc38-a1f4-5bdf-a13a-8e82d1885305 | date | Date Completed:
8a688cd1-e3a9-4ec0-adbc-05fc02ee376e | section | 2.0 - Materials
0d86362b-32ea-4f97-acbe-04e1e519108a | checkpoint | 2.1 - Cut-back Bitumen
edfce6ca-9860-547f-b246-713a7eef731d | note | Frequency - Prior to commencing works
be71cd22-df92-56a8-a2e5-572e4559b377 | note | Acceptance Criteria - Cut-back bitumen for prime coat shall comply with AS 2157 and shall be class AMC0, AMC00 or AMC1.
750cf271-f13e-5f7a-a9c3-d9bb75f66257 | note | Reference Documents - Beca Spec 002 – 7.4.1
9c39bdf3-7644-5b4c-b564-a2012325bb97 | note | Inspection/Test Method - Verify
0b57be03-5f65-5306-a59e-51d4ff1e5c2d | note | Record of conformity - This ITP signed
bdd0e7ae-f106-5d5b-9327-0bf3ba56a034 | note | HP*
fbc590d7-2ec0-58f4-93cf-1133ed77e60d | note | Responsibility - Project / Site Engineer
76913f32-d7b9-5876-859d-ce0afeaaea0b | date | Date Completed:
fdca09e4-1270-418f-9fab-dd36cbb42333 | checkpoint | 2.2 - Cutter
eefb8dcd-9b67-57f7-8363-a117e2ae0719 | note | Frequency - Prior to commencing works
0c87aad9-c9fb-5cb6-b412-a955c0a5f327 | note | Acceptance Criteria - The cutter for use in cutback bitumen shall be a suitable petroleum-based material complying with the requirement of AS 3569.
f9b606b3-73e7-5a30-8537-07106222a4de | note | Reference Documents - Beca Spec 002 – 7.4.4
19f8b060-d4d5-59a8-99b6-bcbcd0125ae2 | note | Inspection/Test Method - Verify
39148fc5-a21d-5962-bc1a-3eba6e10b7e7 | note | Record of conformity - This ITP signed
efbfb421-afa6-5e3f-9a8c-37445c679a72 | note | HP*
4e5fabdf-7445-5200-bf77-3fbfc79fb308 | note | Responsibility - Project / Site Engineer
458994b8-8aa5-5452-ba83-20c89d7b158f | date | Date Completed:
4fe7170e-50f9-4a44-90f1-4455616e3c1c | checkpoint | 2.3 - Bitumen Emulsion
aca34ed8-1ba0-515c-8116-163da6ad041d | note | Frequency - Prior to commencing works
b5f24114-5738-56ca-8e0d-242c3cdad483 | note | Acceptance Criteria - If directed by the Principal’s Representative, bitumen emulsion complying to AS 1160 shall be used as a prime coat.
e54f8d7b-5b04-5f97-8118-c33fa28654e1 | note | Reference Documents - Beca Spec 002 – 7.4.2
e9292f53-667e-5ec0-be49-cf0a66a59fb6 | note | Inspection/Test Method - Verify
c6f17cb2-f3e2-5c15-a49c-a878cbeef3b7 | note | Record of conformity - This ITP signed
68d8c2db-1067-5ad8-9eb2-23934fa25f48 | note | HP*
b2f87684-4113-5683-8389-21850ac419e4 | note | Responsibility - Project / Site Engineer
4e13904f-923c-5def-9741-ca93c6b29373 | date | Date Completed:
fc81c373-2332-5513-bf5c-ec962a3bbeb3 | note | Principal’s Representative - BecaCPL-GCOR-001036
361bc83d-b2d6-4456-8522-651de250b869 | checkpoint | 2.4 - Blinding Sand
011dff3c-cf11-513d-9e0b-a424ee1aaf96 | note | Frequency - Prior to commencing works
15385523-4d24-5e1a-a3ad-c811ca137a74 | note | Acceptance Criteria - If required, blinding sand to be used for absorbing excess primer shall comply with the following PSD.
2282c032-deb0-5f5f-be2e-a9476b4bac43 | note | – – – – – – – – –
4b68975f-d3bd-5155-b43f-58df01d6a150 | note | AS Sieve Size (mm) ¦¦ Percent Passing Sieve by Mass
0b774250-d152-5c76-bb81-e385511f2370 | note | – – – – – – – – –
8b212033-13e5-5f5b-b3c4-0a228318e308 | note | 6.7 ¦¦ 100
1e7a34d6-2f1a-56c0-95a9-b152ed54bdf0 | note | 4.75 ¦¦ 85-100
56e98935-3c6a-5607-839b-71da3f382d77 | note | 1.18 ¦¦ 40-100
978f3888-ceb9-57d4-98f4-bd102d4c6340 | note | 0.425 ¦¦ 10-50
acc5274b-bdb6-5588-858b-a1e12aef68a7 | note | 0.075 ¦¦ 0-5
03e9d942-3ff4-5260-9013-9efe247af5d7 | note | – – – – – – – – –
0c7ad2b4-7b69-5f37-ac63-73811b15fc0b | note | Reference Documents - Beca Spec 002 – 7.4.5
3339a759-c873-5713-8a9d-cde03860859c | note | Inspection/Test Method - Verify
a7f6daed-3c94-56df-b417-fe5fc0a37d68 | note | Record of conformity - Test Report
101888bf-2192-59ba-9475-afa6361e60c1 | note | TP
57de1639-c4d6-5695-94db-3a8287d54203 | note | Responsibility - Project / Site Engineer
a039e763-d319-59ef-95b2-b5c4f884abaf | date | Date Completed:
ca3eedf5-d89c-4186-9ffc-98f3e42542cc | checkpoint | 2.5 - Test Certificates
bd78bbfc-6b47-5001-8f1e-fb689f3a301e | note | Frequency - Prior to commencing works
4c5eedd5-396d-53fc-9749-55b6260bb7f2 | note | Acceptance Criteria - The Contractor shall submit a Test Certificate for each material proposed for use in the Works indicating compliance of those materials with the properties or requirements specified.
1e833167-31a8-56b8-a943-a3ddce13cc07 | note | Reference Documents - Beca Spec 002 – 7.11.2
967d1733-74ed-5952-9e01-b5a7366a283b | note | Inspection/Test Method - Verify
638b1d31-d5fb-5015-8bc6-07ff05209404 | note | Record of conformity - This ITP Signed
d16d41fc-ad72-5d5f-b5f4-75e6f8a908a1 | note | HP
1a8d1b10-7809-5069-81f0-f47131eb4e06 | note | Responsibility - Project / Site Engineer, Principal’s Representative
58b5c9bb-8669-519a-987c-6d73cb25fa82 | date | Date Completed:
55db0188-58d2-529b-8bd6-4460bdcd3764 | note | Principal’s Representative - BecaCPL-GCOR-000967
f8b41986-295f-4794-bf41-8dbda066fba5 | signoff | AUTHORITY HOLDPOINT
ecb49382-18fc-4eed-901a-408364f65541 | section | 3.0 - Construction
299089d7-10a2-4393-8a92-efe8d2b2848c | checkpoint | 3.1 - Trial Application
d144b3dc-64ed-5441-9b7f-c21dcb62a4b4 | note | Frequency - Prior to commencing works
bf4aa8bc-c909-54eb-a3b8-96e6fd37be54 | note | Acceptance Criteria - A trial application, to be conducted as part of permanent works, shall be conducted on an area of the Works agreed and witnessed by the Principal’s Representative
8fb97ab8-eaf8-5049-9422-386843d03e93 | note | Reference Documents - Beca Spec 002 – 7.5
cfe67c4c-15c1-59a5-9f39-9b382c8a83b3 | note | Inspection/Test Method - Visual inspection
1352953f-e4ac-59e1-ba7b-fcaf05f8dccb | note | Record of conformity - This ITP signed
3ff84b75-5407-539d-b851-f5cecf0b7b54 | note | WP
1c433402-1cda-5e93-a5b2-d0ef2fa1eb6d | note | Responsibility - Project / Site Engineer, Principal’s Representative
510ad5fe-5493-5a6d-9c53-b2d58b5f811f | date | Date Completed:
fd86f1c1-1d8c-4f6a-ba0d-e2961e358854 | checkpoint | 3.2 - Surface Preparation
5235856a-71f1-5bef-ad2d-647a8243a109 | note | Frequency - Prior to commencing works
b1d7c351-0622-5a32-a8ac-e793dc2fc850 | note | Acceptance Criteria - Immediately before applying the prime coat, the full width of the surface to be primed shall be swept to removal all loose dirt and material. The prepared surface is to be inspected by the Principal’s Representative.
5cc7f860-8c1a-5be2-8dc5-e550b89bfcb8 | note | Reference Documents - Beca Spec 002 – 7.6
901c69c8-d778-54e3-8215-5c43ff811247 | note | Inspection/Test Method - Visual inspection
2ef648d3-937e-538f-b17d-b13eaf318e1d | note | Record of conformity - This ITP signed
603fa105-9807-58ba-9a7e-1d644d6785f6 | note | HP
0450a84b-92ad-5df4-a3c5-4bb3999f537a | note | Responsibility - Project / Site Engineer, Principal’s Representative
5d17e978-e38c-5df7-ba97-6b2eee630565 | date | Date Completed:
812d3bc8-5983-4d8b-a284-7d3e9bfba958 | signoff | AUTHORITY HOLDPOINT
39ef0bc9-5453-4150-afd4-7ad1ceac2d05 | checkpoint | 3.3 - Application of Bituminous Material
07d3d7c5-b8ba-55f9-b5c0-58764fb49c6e | note | Frequency - During works
5baa220f-ed69-5830-989b-75b3b6736363 | note | Acceptance Criteria - The prime coat shall be applied at a uniform rate and shall be between 1.0 and 1.4 litres/m². The depth of penetration shall be a minimum of 6mm and maximum of 10mm
b03d062c-7d38-51c8-ba8c-45d9794ae3f9 | note | Reference Documents - Beca Spec 002 - 7.7.1
52be890b-5661-506d-b696-c3a1726b2fe7 | note | Inspection/Test Method - Visual inspection
492c42ab-98a7-5688-a2ac-94d8d5c7355b | note | Record of conformity - This ITP signed
3efbcb93-5f7b-512f-b49a-b1fd230fbd7e | note | WP
1ad3a74a-ad26-5172-9180-c0a4a9d90e17 | note | Responsibility - Project / Site Engineer, Principal’s Representative
68355d5c-0c4d-5e60-810f-135a9636b53c | date | Date Completed:
b5be9366-9f29-4c85-b275-a3adc09d7414 | checkpoint | 3.4 - Job Samples
3b9a3b34-f253-5b54-8edc-845f9c40e66a | note | Frequency - During works
f6bb36ca-d851-5d00-aa04-7377f9b443d9 | note | Acceptance Criteria - Samples of each bituminous material shall be obtained from the delivery vehicle at not less than one sample per 10,000 litres of bituminous material sprayed.
974acb5d-d74f-5838-9e5d-b517b0b9ba3e | note | Reference Documents - Beca Spec 002 – 7.11.3
c5aaf87e-97d8-545d-b640-bf8e0c18d9e2 | note | Inspection/Test Method - Verify
6eb4f2f3-2f56-55dd-afae-4ae1de94d265 | note | Record of conformity - This ITP signed
454a022a-e3a8-5dde-bc65-68d29eff10d9 | note | WP
3a0f3209-dd41-562f-9762-1de6531f5db1 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b242dd58-a2c4-5650-8498-a39b2073ee5b | date | Date Completed:
380b9c8c-4f81-4e01-a1b2-58fb404f6199 | checkpoint | 3.5 - Spray Rates
868ac34f-59cc-5b7d-a286-1adcc0c9e3a3 | note | Frequency - During works
bd2a5f0a-7689-5183-a3a1-8d43ffb60014 | note | Acceptance Criteria - The Contractor shall submit records of spray application rates at completion of each mobilisation
e6ba7726-410c-5af3-8b3f-143425285d6b | note | Reference Documents - Beca Spec 002 - 7.11.4
49ec4345-619c-509f-9ce5-ff4fdef9d760 | note | Inspection/Test Method - Verify
c8c8a3a4-4b14-536f-9c64-55c31f1a51ae | note | Record of conformity - This ITP Signed
aeef1bda-d3be-562a-8ea9-5a8985d0f1b4 | note | HP
6c0f3a68-b9da-5565-8b34-a91678c98257 | note | Responsibility - Project / Site Engineer, Principal’s Representative
8f57e5ff-a979-5812-aa1a-2c606dc62777 | date | Date Completed:
986974b7-9e9a-4beb-b57b-cda2b791ee73 | signoff | AUTHORITY HOLDPOINT
b406b5cd-d6ad-4c01-9333-64cebc0a3a17 | checkpoint | Final Inspection
c0962a4a-b69c-5e1b-88c9-9f018ec5c44f | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
92af86fd-5fe0-53a2-8875-03fde9ada4de | textbox | Print Name:
2be8e558-029f-5e73-af51-f5ff22bbd11c | textbox | Position:
852864a7-7c13-5d8b-864f-8b2460177ef6 | date | Work Completed On:
1cbb886e-5c23-579a-970a-252094c725e6 | date | Date:
4c88f19a-2e80-407b-9781-ef977af6d0c7 | checklist | FH-ZU2-QU-ITP022 - Hatelit Install - Rev 0 | itp | ITP022 - Hatelit Install
6bc8eb5b-477b-4042-babb-3146a6873793 | section | 1.0 - Preliminary Activities
0d347d33-2891-4382-9c28-6a6f35594b21 | checkpoint | 1.1 - Check for correct documentation
fe8ec0d2-1652-5981-a4f0-535d6de7b482 | note | Frequency - Prior to commencing works
fab6a839-e954-5ff7-80d9-ab5b3a1e48a1 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
a4f2392d-8f1e-57ff-8b7a-5aff62d805fd | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
9c710b9b-74a3-5ed7-8eef-5d2733d62035 | note | Reference Documents - Current Revisions in Aconex, ACC
4982040e-3988-5e94-8294-ff3faf0f4577 | note | Inspection/Test Method - Verify
8245a88e-f653-5775-a1d0-234e6fc4ba4c | note | Record of conformity - This ITP signed
459f7d5c-0ba6-5b9a-baa6-e5c810116ae5 | note | HP*
795dfdfa-7874-59e0-984f-287a48aaed7b | note | Responsibility - Project / Site Engineer
cf716e5f-76f7-5aee-9735-0288986f3092 | date | Date Completed:
bbaa98b3-bae0-4735-abdf-9e22130c368b | checkpoint | 1.2 - Implementation of all measures and controls
bc148166-d093-5c81-9388-1cfd64b2ba6f | note | Frequency - Prior to commencing works
8fa509c0-ee5d-5e65-b46b-553cb5cccd46 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
c32b3392-7d90-562a-99ec-c4bd3d9fb812 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
477aa62e-c5f1-5949-b9b9-6c284825a576 | note | Inspection/Test Method - Visual Inspection
e53b282d-6654-5abd-8855-9cd14fa4a1a9 | note | Record of conformity - This ITP signed
a4faf0ac-25ca-535a-a761-8200c18d958c | note | HP*
f3d028cd-6ee3-5a89-b3bf-4076c5e0c8a1 | note | Responsibility - Project / Site Engineer, Site Supervisor
09c16e9a-861c-5f6e-9246-db315f42905e | date | Date Completed:
4fa1d1e6-5777-4f0a-aa29-8e84bb3359ee | checkpoint | 1.3 - Equipment
272633c6-1fc7-5cf2-a8e2-dd4e72feef16 | note | Frequency - Prior to Commencing works
35d5d63a-5c2d-5c2b-a512-c722589e74f8 | note | Acceptance Criteria - All plant and equipment to be used in the constructed of the works must be deemed acceptable to use by the Principal’s Representative.
cda47b3e-1add-5037-921f-a664579c3a53 | note | Reference Documents - Huesker HaTelit C Specifications 1.4.1
139ac96f-d512-5273-988f-74d2c4a4c8f4 | note | Inspection/Test Method - Site Inspection
c93c7c50-505c-5973-b7d4-9b27958670c9 | note | Record of conformity - This ITP signed
9042bb6d-5a32-5c61-a3c9-dd1e44f8fbf7 | note | HP
b28982af-f8b7-57da-a97d-a5ec782fb95c | note | Responsibility - Project / Site Engineer, Site Supervisor, Principal’s Representative
83cb149f-6216-5f32-9be7-f86a2d9afe21 | date | Date Completed:
8b376bbb-a1e6-4f91-9655-461cf0f1876c | signoff | AUTHORITY HOLDPOINT
b4d9b665-6961-4e3d-85f1-bc904b77a984 | section | 2.0 - Materials
52866c82-e5fb-4b1a-a69a-901250eb4b8a | checkpoint | 2.1 - Tack Coat Material Acceptance
7e0d55c8-462f-54de-be33-477f787e7886 | note | Frequency - Prior to commencing works, not less than 10 days prior to commencement of delivery
3344c660-6a5e-52f7-8ca5-4031ae8fb73e | note | Acceptance Criteria - Proposed tack coat material and test certificates shall be submitted to the Principal’s Representative for review.
9226a2e1-7a0a-5e0f-a8ba-079522b5e11f | note | Reference Documents - Huesker HaTelit C Specifications 1.10.1
6a0c7f57-2012-54c1-be1e-7c99c7f46125 | note | Inspection/Test Method - Verify
b021f3a4-2a6f-5bf6-8b9d-504f7d874287 | note | Record of conformity - Aconex Corresponde nce
801e8926-5318-594f-ae97-185cb10f18f8 | note | HP
68a456bb-1658-54cc-8097-8178cfacc3fc | note | Responsibility - Project / Site Engineer, Principal’s Representative
0db0a516-4559-57e3-a199-2e162a1e745a | date | Date Completed:
f0a28a39-fd50-4fdb-9ab4-3224fa3e3a05 | signoff | AUTHORITY HOLDPOINT
ccb715f6-6da2-4866-82fa-b307ece78b6d | checkpoint | 2.2 - HaTelit C Material Acceptance
e2aaf721-7970-5676-b31e-2be913b2382e | note | Frequency - Prior to commencing works, not less than 20 days prior to scheduled commencement of application
1f487632-ff56-58df-ac6e-f75c7ba9fa40 | note | Acceptance Criteria - Information on proposed HaTelit C manufacturer and test certificates to be submitted to the Principal’s Representative.
4a8b75fd-8d24-55f3-b4a2-2cf21262a4fa | note | Reference Documents - Huesker HaTelit C Specifications 1.10.2
2b303032-c2a7-53a6-b52b-8d613a77d637 | note | Inspection/Test Method - Verify
45859df7-4fdb-535f-868a-c091c3c30506 | note | Record of conformity - Aconex Corresponde nce
d43c360a-5efd-5477-a08f-4056aa9246bd | note | HP
6b961f63-6a0d-5696-a738-2b00e9ace95b | note | Responsibility - Project / Site Engineer, Principal’s Representative
24b16133-02c4-5a16-80a7-814ba4c2f469 | date | Date Completed:
7cebd87c-8e30-46ce-800a-dd198f4e1775 | signoff | AUTHORITY HOLDPOINT
57cf3a97-43ba-4c6b-acbf-db85a9ad33ff | section | 3.0 - Surface Preparation & Tack Coat
6849b183-cbe8-4337-b9d3-edd40420caf5 | checkpoint | 3.1 - Surface Preparation
32a77ac6-f3c0-587c-b794-aa9341294367 | note | Frequency - Prior to Works
ae612268-10c6-5bc8-9f8b-0aa82321a613 | note | Acceptance Criteria - All loose and foreign materials must be removed from the surfaces to a distance not less than 150 mm beyond the edge of the area to be tack-coated
a53f0137-f67b-56d3-977f-37006ee75fbf | note | ○ All treatments within area to be tack coated to be inspected by the Principal’s Representative.
4831e874-8d2a-511f-9e48-28d24b622af6 | note | Reference Documents - Huesker HaTelit C Specifications 1.6.1
ff9f51df-3dc0-5304-ac07-6686e39fa7c7 | note | Inspection/Test Method - Site Inspection
c34a2050-f5c1-522f-9248-a37bb78ebdf2 | note | Record of conformity - This ITP signed
e410af66-4d28-58e1-a032-7aff3a168130 | note | HP
e49985fb-4326-5b7e-a025-9afa3d51dbc6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
b21de6dc-93f6-5e2a-979a-3182886244b7 | date | Date Completed:
7320c9a6-5add-4862-bbef-78dc8ad9426d | signoff | AUTHORITY HOLDPOINT
a7d10a46-ea30-4ecc-b03f-7dfeec3ac83c | checkpoint | 3.2 - Spraying of Tack Coat
afa2c015-45a6-5fd4-97da-71d113c3ff7c | note | Frequency - Each Shift
74f3f3d7-ad7b-566c-ac28-a8c6ba67475e | note | Acceptance Criteria - The tack coat shall be sprayed evenly at the required spray rate of 0.4 - 0.55 L/m2 to achieve target residual bitumen as per guide.
3a7a394f-a247-5187-bbdd-437168194be5 | note | ○ Rate may be adjusted based on site-specific conditions ensuring HaTelit C is bonded to underlying surface.
1a591022-abe6-55c6-81e6-f24ca0c07b0f | note | Reference Documents - Huesker HaTelit C Specifications 1.6.2
ccac4f47-2d35-540a-818b-a9a3ba729487 | note | Inspection/Test Method - Visual Inspection
c90db9dc-c712-5992-a7a4-67cf4369d2ae | note | Record of conformity - This ITP signed
d310d4fc-96b9-515f-bd07-c778e831d795 | note | IP
1790a5b6-13c6-5819-958f-365e4b0976e5 | note | Responsibility - Project / Site Engineer, Site Supervisor
8857be56-ddfc-51e4-b1f2-cff21571ab05 | date | Date Completed:
8ff253e8-234a-426e-945a-13cc3c8692ff | section | 4.0 - Placement
905319cb-332c-4583-aa0e-b3e286218653 | checkpoint | 4.1 - Prior to placing HaTelit
b4265550-c3bf-5b4f-8f06-d4a282b84b63 | note | Frequency - Each Shift
f5915ba1-db42-56ba-b8f2-08fc23571495 | note | Acceptance Criteria - A minimum of 48 hours’ notice shall be given to the Principal’s Representative prior to the commencement of placing the HaTelit.
c52d0313-603d-5036-aaa1-e61947832a1b | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
008db338-5c67-5bd1-adcb-e530b059d1f8 | note | Inspection/Test Method - Visual Inspection
23093d03-0a3f-5dbb-a0a4-795ef7fc7f83 | note | Record of conformity - This ITP signed
e6960f47-ef78-5994-96a3-f33762b2b033 | note | WP
15a869d1-d930-598a-9b3b-7c69a1fee506 | note | Responsibility - Project / Site Engineer, Principal’s Representative
859b2eaf-0a36-5df2-95d3-2dafb773b9e8 | date | Date Completed:
0c3531ae-3754-405a-9ea7-52ab36cd3aa7 | checkpoint | 4.2 - HaTelit installation
25491cdb-51a5-5b49-9c2e-22a961328a5f | note | Frequency - Each Shift
9245fff0-348b-560b-8436-3e7222976d59 | note | Acceptance Criteria - HaTelit to be installed to Manufacturers Specification. Where placing multiple rolls, an overlap of 250mm transversely and 150mm longitudinally is required. The overlaps shall be treated with tack coat and rolled to bond to one another. For small areas, manual installation is acceptable provided a fully flat and crease free installation is achieved.
4c324ba5-83cf-5cac-9d93-4f18a1ca7b02 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.2
08bd3837-8272-5c7d-af67-86ea640b873c | note | Inspection/Test Method - Visual Inspection
cc24844b-86a0-5eae-b19d-0423130cd4ff | note | Record of conformity - This ITP signed
4cc2a9ab-7593-5326-abc1-c63253b40466 | note | HP*
102bbd1b-e63a-5497-84d0-fbcc8becc5a4 | note | Responsibility - Project / Site Engineer, Principal’s Representative
978c385c-eab7-5749-bbc6-ad058bafeb03 | date | Date Completed:
5566f46b-1958-405e-bddb-579f6890be4a | checkpoint | 4.3 - HaTelit Rolling
979ae15e-de2a-56fe-b5cc-9b1b42d5ae1d | note | Frequency - Each Run
af49bb2b-99eb-5c95-a365-5b63d2135780 | note | Acceptance Criteria - Rolls applied to tack coated surface without wrinkles, creases and folds. HaTelit to be rolled with 2 passes using pneumatic tyred rollers following application.
e76b356f-6c2d-57c2-9584-63bf1dbe5581 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
5481f69d-3a75-55cc-9e32-bed7b3817204 | note | Inspection/Test Method - Verify
70def9b9-a338-54a0-964d-493f31264e65 | note | Record of conformity - This ITP signed
4599d628-a39f-5cd0-84c5-b9541a59f97f | note | HP*
1ec9fdee-3fba-5bbc-91df-8e5bf469b19a | note | Responsibility - Project / Site Engineer, Site Supervisor
66de617c-698f-54bc-94e9-5fbb6d89e4d9 | date | Date Completed:
b77fe150-eaee-432f-8f81-fa7b94680fdd | checkpoint | 4.4 - Surface Finish Inspection
1828e8a6-0e11-5554-ae7c-07625c4e931b | note | Frequency - Each Shift
6cc26bc3-694a-5014-88a7-c75c356a7534 | note | Acceptance Criteria - Installed HaTelit surface to be inspected and areas recorded where required for flatness and saturation.
62e91eb3-bb8c-5335-bf92-533c6c9b0787 | note | ○ Surface to be free from any loose or deleterious material.
094b8f7f-f4c0-5218-89d1-1c7a863ed108 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.3
186f480c-5404-527e-8c9c-f1c7141f1022 | note | Inspection/Test Method - Visual Inspection
7df486d6-2118-5d81-bdeb-1d15587811b3 | note | Record of conformity - This ITP signed
bcf895da-238c-5d8d-88e1-9c37f6ac5049 | note | WP
cb496516-171a-5bd1-9507-a50b59222499 | note | Responsibility - Project / Site Engineer, Principal’s Representative
f3049765-5ece-52ca-98fc-c84b9ee6d654 | date | Date Completed:
08348277-ec6f-4c95-9dfb-f225c5eb239d | checkpoint | 4.5 - Spring Balance Adhesion Testing
bf3a9662-78c4-5774-a483-e0b9d2e55bbd | note | Frequency - 1 every 50 to 150m2
e080bfca-23d5-5051-bc13-9a490953d3b3 | note | Acceptance Criteria - Test locations to show adequate bond between HaTelit and tack coated surface.
7dd62148-0c53-50d4-b3ff-fee5855fba59 | note | Reference Documents - Huesker HaTelit C Specifications 1.7.4
c0e76782-aacb-5d02-ba11-2648a44cef57 | note | Inspection/Test Method - Test Point
536a00b3-43ae-5ee8-b903-a03f8dd73190 | note | Record of conformity - This ITP signed
e1c8dbcf-db55-52a0-b938-3d6380baa1c9 | note | WP
50ee9d3a-2266-5752-b9db-2033d405a278 | note | Responsibility - Project / Site Engineer, Principal’s Representative
91898df6-2d34-5c79-9046-1c055b1f35cf | date | Date Completed:
a406d039-6ebe-4cba-b395-9e7ec98e7d10 | checkpoint | 4.6 - Asphalt paving over HaTelit
cea011ed-3dba-57d8-8670-e9b0fe1fd275 | note | Frequency - Each Shift
a3d59164-7e33-55cd-a69b-4a90064960e3 | note | Acceptance Criteria - Ensure that the surface of the installed HaTelit and the underlying asphalt layer is dry, clean, undamaged and free from loose material until the completion of paving over the installed HaTelit.
1f27c1e0-76e0-52c6-9edf-38387e05e15d | note | Reference Documents - Huesker HaTelit C Specifications 1.7.5
b5386e15-c8dd-5d4a-921e-6bdfb6bf111f | note | Inspection/Test Method - Visual Inspection
a0c8e412-a38c-5766-9472-25f18c4316d8 | note | Record of conformity - This ITP signed
f05e026a-276d-5e0e-90b4-f58f5ca70c97 | note | IP
d48bc467-ef2b-5a70-9d5e-02fec495a012 | note | Responsibility - Project / Site Engineer, Site Supervisor
7c4c1939-313d-5e55-b683-d22464184d3d | date | Date Completed:
b6db0038-bb2f-439e-9f37-af756f09e6e3 | section | 5.0 - Quality Assurance
8b6bdac1-8694-4698-9d49-3209be89fdcb | checkpoint | 5.1 - HaTelit Surface Conformance
20c67dec-9398-5456-8e61-a2ec224ed04f | note | Frequency - Each Lot
956a2fba-cc72-5356-bb16-b6d35517ee67 | note | Acceptance Criteria - The Contractor shall assess the conformance of the surface flatness and saturation of the installed HaTelit surface
4a200501-bd0e-50a1-8e3b-a7cc6316a7d1 | note | Reference Documents - Huesker HaTelit C Specifications 1.12.1
c14e827b-6ef4-51c2-bd6c-bbe5a77c4961 | note | Inspection/Test Method - Survey Report & Visual Inspection
43d53241-1fb7-5087-a6c3-fe4a887a5cc5 | note | Record of conformity - This ITP signed
68e22f3a-0ddb-58f1-ae0c-94b555197b70 | note | HP
9b84d4fd-5492-516d-832d-373d4dc519d5 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4fc0e46b-780c-548b-a2f7-d098d369a1dd | date | Date Completed:
2914a338-9bc7-4878-ac1d-44c51d437206 | signoff | AUTHORITY HOLDPOINT
c510222d-7d53-409f-babb-145b8f045d5e | checkpoint | 5.2 - Nonconforming HaTelit Lot areas
e90312d1-0277-5893-9eb9-7a73142177f2 | note | Frequency - Each Lot
ac5147ee-d2cf-5942-9748-337340752818 | note | Acceptance Criteria - If required, any sections deemed nonconforming shall be removed and replaced according to Manufacturer’s Specifications - FH NCR Procedure to be adopted when lot area is deemed nonconforming.
9e04a652-662a-5ee2-a8cd-6251d87df491 | note | Reference Documents - Huesker HaTelit C Specifications 1.13.1
3d6f2628-3913-57d9-8f68-2b5c1c37917a | note | Inspection/Test Method - Visual Inspection
c409c60e-a456-519f-b0fd-cde38fd8a1f8 | note | Record of conformity - Nonconform ance Report
58d9cb3b-1b7d-543a-9ef7-9a37c5c184ec | note | HP
e5c153ea-14cf-598d-aa8a-53e828231c3a | note | Responsibility - Project / Site Engineer, Principal’s Representative
115d9055-3e44-5308-a2a4-13496030db40 | date | Date Completed:
f02561f4-f59f-4692-96ed-a5877fc14740 | signoff | AUTHORITY HOLDPOINT
50e79eb9-6ce9-45ac-83f7-92e11a3f7043 | checkpoint | Final Inspection
173b0058-bb77-5e89-bd98-2e79ba84542b | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
934f17bb-c4dd-5150-b8d8-e299a363d351 | textbox | Print Name:
66cb06fd-c54e-51d3-88ad-6d43e3a33b94 | textbox | Position:
b1d141aa-a90f-5146-8be8-f61e957ac211 | date | Work Completed On:
602f60e6-bc64-5dfa-98f3-3fcd848960c7 | date | Date:
3a5a8c4d-f5de-43d5-8221-26c5eda8b31a | checklist | FH-ZU2-QU-ITP023 - RBB Install - Rev 1 | itp | ITP023 - RBB Install
dcdaef01-6bd5-4a06-ac1a-58e2c5b6d29f | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
4fcd1e68-80e5-4bb7-8e19-d3bc4cf48d97 | checkpoint | 1.1 - Check for correct documentation
076989a2-7070-5129-8757-c1049d765e54 | note | Frequency - Prior to commencing works
8ab324a6-d792-50c9-9522-bf1d24063433 | note | Acceptance Criteria - Current revision drawing is being used including the Subcontractor’s copy.
2cc89f1a-6980-5a3d-bd29-76588fb9e1f7 | note | ○ Current revision to be obtained via Aconex.
096b2722-38a4-535f-8eb8-cd5cc091787c | note | Reference Documents - Current Revisions in Aconex or ACC
e120386b-0744-5b4e-b0ca-e871cd1caa9a | note | Inspection/Test Method - Visual inspection
671d1b0d-4961-534e-b4d7-950c894a8383 | note | Record of conformity - This ITP signed
68c78ca3-feab-53e1-9e4d-96f99bb3f966 | note | HP*
fe5140a3-526f-5dac-a580-d55946e8ee60 | note | Responsibility - Project / Site Engineer
2dbdf7a6-7f02-5f6b-a503-5106c718f14c | date | Date Completed:
8b85f332-4477-4c84-9f4a-ae9595c78b88 | checkpoint | 1.2 - Implementation of all measures and controls
d021a529-7fe6-5df3-a58c-23cb69fb83ca | note | Frequency - Prior to commencing works
83549a14-23a5-5f24-8c24-7d95e54f9c48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
a74f2587-6a16-566c-8605-a831de28358e | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
99ed3f38-ac8d-5a3e-a4fd-43207a8ec220 | note | Inspection/Test Method - Visual Inspection
d7084fb2-a245-5971-95b0-d1dc5e55922a | note | Record of conformity - This ITP signed
ed1458d1-45b6-561c-9e4b-3506c8524308 | note | HP*
fc337892-9734-581b-8dac-79a5aff5f45f | note | Responsibility - Project / Site Engineer
e6b73a27-a34e-5b03-a259-8c5bce6c73e9 | date | Date Completed:
94262c83-1e3f-4cbe-a5a4-c4a1eb3f0901 | checkpoint | 1.3 - Definition of the work area
1a5e2cc3-a3fd-5a1e-ab3d-4bd57f1374b8 | note | Frequency - Prior to commencing works
c1f23998-33aa-52ea-9436-28846c4be2b8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of work clearly defined.
ac3357d8-f66a-577d-bcdf-cc5fa629b795 | note | Reference Documents - Drawings
6dc96475-832e-526b-89de-c4d1d3c65e6b | note | Inspection/Test Method - Visual Inspection
7bd6fbca-c7a4-53ed-bc19-ec0fac2aadd9 | note | Record of conformity - This ITP signed
b28ac2c2-baa6-56ee-88cd-8894704fdf97 | note | HP*
9e86b5cf-f894-5bbd-9b70-0ef43b2e7bd2 | note | Responsibility - Project / Site Engineer
fbfab279-813c-5a6c-b752-f8a105943905 | date | Date Completed:
fed9bf3e-e7d7-4c36-bf3d-e9beb1ab0dd7 | section | 2.0 - Materials
d336e5a0-3f30-4c5c-944e-7199ca2e0a06 | checkpoint | 2.1 - Rubberised Bituminous Sealant
46c20e35-100d-5502-bd8e-5393ddc96e42 | note | Frequency - Prior to commencing any activity
b71ea934-32f1-5210-b963-72e8919cbd94 | note | Acceptance Criteria - RBB must be a proprietary polymer modified bitumen (PMB) crack and joint bandage product and have the following properties:
931300e2-bc2b-5eea-8773-a3866c81c6db | note | – Minimum softening point to be 95°C
68e41a9d-6658-57cc-96d6-b9cca9083f2a | note | – Penetration at 25°C between 20 and 50
f5c0e729-388e-57a6-a283-d1c9cd6566aa | note | – Flow at 60°C at 5 hours to be maximum 5mm
c5dfb34f-e2f3-57ed-b2db-511b538a26d4 | note | – Viscosity at 180°C to be maximum 3Pa.s
061fb492-70d9-5864-9a6a-df7276616a1b | note | Reference Documents - Beca Spec 002 – 10.7
09d4a1c6-e2ae-5cf3-9065-6707c3a6b62a | note | Inspection/Test Method - Verify
2742e306-541f-586e-9807-e4c0a6981811 | note | Record of conformity - Manufacturer’s Datasheet
71220d4d-abc3-53ca-a04d-63f612aa2817 | note | HP*
3f673356-3a53-588c-b1a5-c807cb95ed90 | note | Responsibility - Project / Site Engineer
a5499590-02f5-594e-bde8-60eb9d06ec3e | date | Date Completed:
01d7c12d-26c6-5652-9d64-72480eb0bb01 | note | Principal’s Representative - BecaCPL-GCOR-001062
56fc0e9a-9b61-4a0d-917a-8ed0fa3a3cb9 | checkpoint | 2.2 - Material Sources – Conformance Test Certificates/Reports
787aba00-eee8-599f-9626-ebfc860c4e09 | note | Frequency - Prior to commencing works
8d2628a7-7a9d-5065-b1c4-e9bada109c94 | note | Acceptance Criteria - Test certificates and matching production batch numbers are to be provided for each product used
b5da5be3-4bfa-5164-84b7-63e3f2f33e06 | note | Reference Documents - Beca Spec 002 – 10.7
e148dd43-abe8-5f65-a485-4db1ea878bc9 | note | Inspection/Test Method - Test Certificates
5b40d57f-5c0a-5c55-a20d-7016a6410114 | note | Record of conformity - Aconex Reference
0a98c9a0-b359-5379-ba41-d76fe29d580c | note | HP*
999e91f5-4f36-5ac9-990b-3c7fc6f3bacd | note | Responsibility - Project / Site Engineer
d68b3006-3f52-56ae-855d-2424ee86b33d | date | Date Completed:
d365a1f9-54af-4dce-8c2d-8d60f70cd91f | section | 3.0 - Sealing
482c8dde-014d-4e9d-aaf5-7aa772f825d3 | checkpoint | 3.1 - Applying Sealant
9a756b36-40eb-5ada-9195-c5104d5ba09a | note | Frequency - During joint sealing works
0893c822-f2d4-51a7-9f7d-f0f065e672b0 | note | Acceptance Criteria - Sealant bandage is to be between 50mm and 75mm wide or as per drawings.
146426d9-4d8c-5f10-9952-2fbaf0e58cac | note | Reference Documents - Beca Spec 002 – 10.7
aa6fd26e-650b-5f09-b33e-e6cb2367c1fd | note | Inspection/Test Method - Visual Inspection
ecf7c0e0-50c9-5c76-8e93-2dc32c98dfe6 | note | Record of conformity - This ITP signed
392d5474-73d9-5241-9f11-47852ba9d032 | note | IP
eda2d52e-1965-573b-b5d3-858102d764b1 | note | Responsibility - Project / Site Engineer
2e27a488-3a39-50db-bd91-6adc8dadd495 | date | Date Completed:
413e0bb0-b3d5-443d-aa69-3d467ceec380 | checkpoint | 3.2 - Protection of Applied Sealant
f1bf55ba-e32a-54be-b92b-6cf9a53b2035 | note | Frequency - During joint sealing works
86bc56ab-d80d-5518-a3f1-a3832a896dd7 | note | Acceptance Criteria - Installed sealant must be protected from damage by traffic (and possible pick up on construction vehicles and aircraft tyres) until it has cooled to ambient temperature.
28e6b8be-ef23-5c14-9757-264ce692aa0f | note | Reference Documents - Beca Spec 002 – 10.7
21247d4d-52b7-5de3-b28e-491a0dbd1bd0 | note | Inspection/Test Method - Visual Inspection
fbce94d7-4564-5fe6-9232-5f0c9e52eacc | note | Record of conformity - This ITP signed
67197ec3-d4e2-55db-8401-6d2a3017c736 | note | IP
686a0439-61b6-57ff-a2af-46e13d05cd0d | note | Responsibility - Project / Site Engineer
01725427-4a4e-5d92-9954-6b43381320f6 | date | Date Completed:
8b87b40c-e1f0-4db7-8933-2393d3bcfa9f | checkpoint | 3.3 - Cleaning up
2e7b0d4f-6245-586d-bb38-cc655cc828d1 | note | Frequency - After sealing works
289efcc6-085b-5160-993c-8d3aa14f68af | note | Acceptance Criteria - Any sealant split on surface of pavements must be cleaned off immediately.
11fde04e-72b0-5aef-8cae-99a6b2ef0e3e | note | Reference Documents - Beca Spec 002 – 10.7
8fc5b485-d548-5b58-8d77-4001e75598f4 | note | Inspection/Test Method - Visual Inspection
8d9245d8-afa5-5d65-b818-788d066cb935 | note | Record of conformity - This ITP signed
2e0246b9-3808-5855-90ed-36022d27595d | note | IP
3763f5e2-7141-5813-a984-71c768f5d0dc | note | Responsibility - Project / Site Engineer
dbc7c48c-8731-5ca4-bed5-493b207f3e2b | date | Date Completed:
279b1e7d-3230-4c14-affb-ef5dac9bef03 | checkpoint | Final Inspection
aba71fc6-9e1b-5918-889f-808b781c76fa | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
13f73ea6-e61a-50b4-bd59-d5feef7e77d2 | textbox | Print Name:
ad82700b-e91c-5752-8002-6277c2b5121a | textbox | Position:
9a55fab0-5494-5ac2-8676-5f7538c7ee96 | date | Work Completed On:
ef1ec8a0-88f4-5097-b918-f4eb4872b7d9 | date | Date:
0167ee88-4c50-4b65-8a52-3446ac6d1a17 | checklist | FH-ZU2-QU-ITP024 - Line Marking - Rev 1 | itp | ITP024 - Line Marking
a299e125-7c64-4afd-a2e2-d4471a03b878 | section | 1.0 - Preliminary Activities
f0317af8-8c31-415c-8892-cdceda1b2037 | checkpoint | 1.1 - Check for correct documentation
1c95aad2-4d03-5f6a-9184-2163d9fd3936 | note | Frequency - Prior to commencing works
d0a8f690-1a31-5e04-85be-55feedda7db2 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
a34ab5a9-d383-521f-b12f-ea63c1852b56 | note | ○ Current revisions of these documents to be obtained via Aconex.
6a5efa0e-2e4c-5200-8112-ba29953976f5 | note | Reference Documents - Current revisions in Aconex
cc825b48-d061-5643-a41c-9df4bb176038 | note | Inspection/Test Method - Visual inspection
d4c00f5f-8db5-55ba-9f3b-f2269bdb26aa | note | Record of conformity - This ITP Signed
831ca973-204b-5441-b6c9-f7bca1db966a | note | IP
e274bf2d-29d7-5392-89bf-82cba6c946f5 | note | Responsibility - Project / Site Engineer
607ab3b5-faca-5e7b-aaba-0196390c8611 | date | Date Completed:
7354dc44-71cf-471b-abfd-980d23843a87 | checkpoint | 1.2 - Linemarking Plan Approval
37f17cd7-b5a0-5e46-a18a-e66ca4a5960a | note | Frequency - Prior to commencing works
ec63fb9b-7fde-5502-a4fe-9834104b2b06 | note | Acceptance Criteria - A linemarking plan showing which lines are to be removed and which lines are to be applied needs to be approved by the Contract Administrator prior to commencement.
6c7fbfcf-1f53-515b-8442-50d21b0d5767 | note | Reference Documents - FH Internal
b592e6c7-972e-5a74-87e9-944ea4a9e884 | note | Inspection/Test Method - Aconex Correspondence
f6b2ac78-5899-59d3-b86d-98e25f7e44c2 | note | Record of conformity - This ITP Signed
fe376690-52ba-51db-b942-732a5ff9c76a | note | HP
167646d4-47fa-5192-804d-4572606fea56 | note | Responsibility - Project Engineer, Principal’s Representative
35cc15ee-56dd-5cbb-a4f5-15a4e018d3f3 | date | Date Completed:
cb2a21f6-fb4c-4544-b255-69d3f20df216 | signoff | AUTHORITY HOLDPOINT
ff5bdf16-6926-4b6e-a4b6-b993ccbe9f46 | checkpoint | 1.3 - Implementation of all measures and controls
8f3f67a2-b768-5bbf-a5dc-976aaf2d4913 | note | Frequency - Prior to commencing works
d92786a5-edfc-5401-bbee-d0b187d71770 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
9030c3d9-e64b-5b45-8190-fee14814841c | note | Reference Documents - PSP, EMP, TMP, WMS, SWMS
203d6f66-289e-55f8-a2c6-edf495358df2 | note | Inspection/Test Method - Visual Inspection
4ce9e843-66f8-5480-a9c9-3d8ce4d46202 | note | Record of conformity - This ITP Signed
ddef3d95-5462-5444-ac10-e1b7bf678e44 | note | IP
1ba9a100-05a0-5da0-ae3e-c9feded8f14a | note | Responsibility - Project / Site Engineer
2564380b-255b-5b79-a891-29176703d3e9 | date | Date Completed:
b105acad-d456-4c83-87de-0cec95778938 | checkpoint | 1.3 - Plant and Equipment
b0975770-804c-5145-bd18-e380afec0178 | note | Frequency - Prior to commencing works
2ee3312b-928c-5762-97d5-d1e1dbb34aa6 | note | Acceptance Criteria - Plant and equipment used in the works are appropriate to achieve specification requirements.
02023e64-f85f-55ea-b6f3-577de5e9b79c | note | Reference Documents - Beca Spec 002 15.3
54f9fefa-6bd7-58ee-ac6b-55c3d18cd4a3 | note | Inspection/Test Method - Verify
a027c058-e51d-55d2-a7b4-9afbdacfdd04 | note | Record of conformity - This ITP Signed
4a601782-6b71-50c4-8cf3-6ac74ba3bb1c | note | IP
670cb1e9-174f-5cd6-aadf-0fba227ba420 | note | Responsibility - Project / Site Engineer
0b713300-d79a-5720-af08-80567420d30a | date | Date Completed:
2760ee2e-8cc6-4a9c-bbc4-73a92d7bb4bf | checkpoint | 1.4 - Materials
cf0db8c5-4235-5b49-8379-e0c6a63d77bc | note | Frequency - Prior to commencing works
8445c45a-206a-5068-8bac-e82e32f02b94 | note | Acceptance Criteria - The paint to be used shall be a premixed synthetic latex-based paint (such as WATTYL AIRPAVE or approved equivalent).
fd5aa652-fc05-5132-b3fc-55a67cf8ecef | note | Reference Documents - Beca Spec 002 15.4.1
2d68c304-ecbb-5a28-a723-c0cb0809ff08 | note | Inspection/Test Method - Aconex Correspondence
07bb3d86-0c29-5fdd-8abd-36257538cef6 | note | Aconex ref: FHPL-TRANSMIT-001678
a4a67aa3-dbc1-5d6b-885e-a4896aabb98c | note | Record of conformity - This ITP signed
36200506-3e84-57a9-b113-8c5ef71c3417 | note | HP
24576453-a408-5e01-8d8c-9e5e7e054fda | note | Responsibility - Project Engineer, Principal’s Representative
8ef096ed-e8ec-51b4-afeb-ae2f3ad275d6 | date | Date Completed:
913d4602-695f-5337-8706-fed16c659486 | note | Principal’s Representative - FHPL-TRANSMIT-001678
d5b4157b-e53a-4848-ac04-442f47508617 | signoff | AUTHORITY HOLDPOINT
adfb61f7-c09b-4e39-89ab-d77d74981ca6 | checkpoint | 1.5 - Material Handling
1112afe0-cc4d-5df4-9411-2bd33eca6780 | note | Frequency - Prior / During works
9052b74d-63f3-5f90-9c22-4d154eef1746 | note | Acceptance Criteria - The paint Is to be packaged in 20 litre containers that are of durable construction without sharp edges. Paint containers are to be clearly labelled “Airport Pavement Marking Paint” as well as being labelled with the following: Manufacturer’s name, Colour, Batch number and Date.
5d3c3329-5657-5cb9-9efd-e1346664a23a | note | Reference Documents - Beca Spec 002 15.4.2
1ff988d2-c6f4-5281-a330-6ca62588a509 | note | Inspection/Test Method - Visual Inspection
03229cbf-536a-5571-becc-40707289d0f2 | note | Record of conformity - This ITP signed
97df309b-9d4b-593c-a0f0-808e1d7dc9ca | note | IP
1c44103e-32fc-5db0-9965-35c9b0f60ad5 | note | Responsibility - Project / Site Engineer
46e585b5-3519-546c-9bee-296fe203fddb | date | Date Completed:
bc71a1b5-eb4e-44dc-a17c-45095bbea9e3 | checkpoint | 1.6 - Survey and setting out
359fe79d-356a-54e8-9f56-35f73c1ddb11 | note | Frequency - Prior to commencing works
62050159-c89f-51dd-ab80-8b0cf01c3671 | note | Acceptance Criteria - The Contractor shall carry out the setting out of the pavement Markings as shown on the drawings. This shall be approved by the Principal’s Representative.
9355a37f-b923-561b-bd56-55b8ab6a06d4 | note | Reference Documents - Beca Spec 002 15.7
0e2fa374-70f7-5468-8f8a-24e27672b3db | note | Inspection/Test Method - Verify
83f9096e-647c-58f5-8aad-ef7b49339da0 | note | Record of conformity - This ITP Signed
0b27f0fd-f8e0-54c7-81d1-ff17491437ae | note | HP
b94edfcb-2744-5677-b3bb-10193da5d706 | note | Responsibility - Project Engineer, Principal’s Representative
6ff6d711-c088-587c-9075-46b39836b935 | date | Date Completed:
83c92210-7c93-443c-9583-637380fc5bde | signoff | AUTHORITY HOLDPOINT
5f7c8c18-50d4-4fd6-9258-c165f78903c7 | section | 2.0 - Construction
6f813773-e496-4db1-bf52-3f85374433a3 | checkpoint | 2.1 - Removal of Existing Line Marking
f93552ff-2dc0-5ef4-8a03-60614968b111 | note | Frequency - Each Lot
d7d59580-70a4-5e65-aa24-2fe9d10d1d9a | note | Acceptance Criteria - Existing pavement markings, at the locations shown on the Drawings, shall be removed by water blasting or other approved means that is non-destructive to the existing pavement surface.
824f8fcc-dba6-5e2e-877d-311790c59662 | note | Reference Documents - Beca Spec 002 15.5
1949ecf6-b6cb-5b1f-8243-b714444f192d | note | Inspection/Test Method - Verify
cda23d5c-51e3-5dd6-8ba2-7b8e4d8f55f4 | note | Record of conformity - This ITP Signed
9fd8c0ab-7e78-59d5-bbb5-e781bcadd297 | note | HP
45f07539-bab1-58bb-a242-2863705837c6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
60b4b4d7-2c2e-5794-87c5-408a629ea992 | date | Date Completed:
ef1902be-f39f-48bd-95a3-dc072b9b7252 | signoff | AUTHORITY HOLDPOINT
1972b639-66e8-4c44-9f71-a9589c08b9b8 | checkpoint | 2.2 - Surface preparation
a7cd42a2-4467-5d0c-9123-fd5fd5517a17 | note | Frequency - Each Lot
0047f222-e84c-50c7-bca1-92b122b6e308 | note | Acceptance Criteria - The surface of the asphalt or concrete pavement in the areas to be painted shall be thoroughly cleaned prior to the application of the pavement marking paint. This shall be approved by the Principal’s Representative.
dc708d1c-009c-558c-9fc0-ea136e878581 | note | Reference Documents - Beca Spec 002 15.6
c510abd7-c15d-5386-b960-797f54ddaa70 | note | Inspection/Test Method - Visual Inspection
ba692d16-82b4-5117-8538-bdda2d74a71d | note | Record of conformity - This ITP Signed
040b17db-4273-57dc-854d-f5c26dedf176 | note | HP
2a635c34-e75c-5367-9fe9-7aa6fb5009d6 | note | Responsibility - Project / Site Engineer, Principal’s Representative
eda5414d-0f9a-5cdf-b388-427d18290fb6 | date | Date Completed:
bfa4638d-d74f-410b-8e38-6c2041ef95a5 | signoff | AUTHORITY HOLDPOINT
c58ae312-07cc-448e-b608-0d03c1a712a5 | checkpoint | 2.3 - Weather Conditions
5f5d2f60-115f-5941-9ad4-9bfa1444d790 | note | Frequency - Each Lot
2389c5e2-5911-5def-8db4-147198dd3d01 | note | Acceptance Criteria - Pavement marking shall not proceed during wet weather or when the pavement surface is wet or when rain is likely or during high winds.
ba28dc58-594a-5cd5-88a5-905c735c0ee5 | note | Reference Documents - Beca Spec 002 15.10
7e221c9e-7fdd-5fc9-82a2-6afe5041f16b | note | Inspection/Test Method - Verify & Visual Inspection
bb8215e6-a5e3-53d6-8580-a4bbc9277bad | note | Record of conformity - This ITP Signed
d8ef71e6-4abc-5786-abef-1aedafc23270 | note | IP
0290e50d-b501-529e-a8e8-1175415fa108 | note | Responsibility - Project / Site Engineer
83244b9d-88ec-5d66-be11-ee7e40b9440f | date | Date Completed:
e99a8e2e-5747-4615-9f71-8bf4f6a7ba2d | checkpoint | 2.4 - Application
cfc6a77b-a432-5242-b898-367538f2f851 | note | Frequency - Each Lot
6a5972e3-5300-5d24-b237-7a908e61f527 | note | Acceptance Criteria - The paint must be applied in two even coats to provide the required minimum total dry film thickness for the two different paints are:
170c31ca-aa67-5b7d-bac1-5a6783623d2e | note | – Dulux Roadmaster dry film thickness (210µm)
512af01e-eff5-57ae-bbfa-11ad07c3a1f7 | note | – WATTYL Airpave dry film thickness (60µm).
14cdb87d-2623-5f58-933c-68db27764cc8 | note | ○ The second coat is to be applied no less than three days following the initial coat.
b7ea9683-aa0e-5bf3-bda6-4bddae569b41 | note | Reference Documents - Beca Spec 002 15.8 / Manufacture rs Specs
2c30166a-3203-5547-ba76-a8f32407e78a | note | Inspection/Test Method - Visual Inspection
6b1634ca-913d-5754-b1af-a287d16e0706 | note | Record of conformity - This ITP Signed
460f4178-c9b1-5fb4-b4c6-3ae52b2505e6 | note | IP
91bfbfd2-b001-57d0-b256-374661ed3ce4 | note | Responsibility - Project / Site Engineer
0b933190-6814-5f5d-a6c6-575eb6ee43b8 | date | Date Completed:
8fc6fb5c-3f14-4012-9598-7da5b74c387b | checkpoint | 2.5 - Application Rate and Conformity of Application
2d92bcc1-6de7-5e3c-bdd1-be5b141c705e | note | Frequency - Each Lot
a97115b8-8eeb-5c19-b6fc-1f3b91012ac9 | note | Acceptance Criteria - Daily records of paint usage and the area covered shall be maintained by the Contractor.
e38371ea-78c5-52a5-8e44-85c7d55d1dee | note | Reference Documents - Beca Spec 002 15.12
3e39d713-f152-59df-b0ab-baa370a5c716 | note | Inspection/Test Method - Verify
82678e9e-a5c7-55e6-beac-4a0883bca80b | note | Record of conformity - This ITP Signed / Daily Records
34646071-82ff-55ba-9b97-277227e24c1f | note | IP
605058c2-584f-5f7e-b3ce-a2c570d849d6 | note | Responsibility - Project / Site Engineer
474613d1-4204-56ce-b1d0-64d4ce23d864 | date | Date Completed:
3e5f7e68-ecb1-4aee-8a2c-0cf4539844ce | section | 3.0 - Post Construction
4d8cb768-212d-400c-8ed8-80492a32d25f | checkpoint | 3.1 - Records
d5c7358e-1f33-5705-b408-736e05383966 | note | Frequency - Each Lot
f0e2c474-7bbc-50d4-a553-e33a9c9177f0 | note | Acceptance Criteria - Finished pavement markings shall conform to the following tolerances:
3ad955ea-ebde-57c9-b83c-9f928b34b751 | note | – Location of pavement markings ±10mm
ad1896b1-7d54-5a4b-9b5b-1d3f23cbee34 | note | – Width of any line or line forming an alpha/numeric symbol ±5mm
ea691ebc-baf6-5caa-86fe-55cd05d00ee0 | note | – Length of any line and the spacing of broken lines ±50mm
c7270f38-4826-50db-acfb-341b7db8a2b4 | note | – Dimensions of any alpha/numeric symbol ±10mm
72ef3a4c-66d1-513e-9f04-87c08fac1111 | note | Reference Documents - Beca Spec 002 15.9
116fcd21-9260-51f7-b9fd-f964684f4433 | note | Inspection/Test Method - Verify
df62826e-24db-52d0-9f4f-6a277fb28ad2 | note | Record of conformity - Survey
95e9d011-caa7-5ff1-bfaf-4142677fbd19 | note | SCP
83102d1e-685a-567c-b93c-4e15bd4b8642 | note | Responsibility - Project / Site Engineer
005a68c9-7e8e-5686-a098-fc13c86c10cb | date | Date Completed:
484101ca-0126-4182-84a6-58c3c059b05e | checkpoint | Final Inspection
fc3dbe4d-1b31-544b-b7ca-9ac225ab4b25 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in a ccordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
50301623-e6bf-51a3-adb5-4d912e8f3190 | textbox | Print Name:
7becb5e9-8fd1-53c6-add9-4aca6843ab22 | textbox | Position:
2f040c82-6f78-5cb0-b295-195fd2363c42 | date | Work Completed On:
4b6a41e3-e571-5d4e-a0f0-1ed4cd73d2bf | date | Date:
9c50517b-d80f-55e3-90fa-62076d1f1ebb | checklist | FH-ZU2-QU-ITP025 - AGL Conduit and Boring Installation - Rev 0 | itp | ITP025 - AGL Conduit and Boring Installation
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
b8a32079-1aa5-57e6-8a66-15d046efe9a4 | note | Frequency - Prior to commencing activity
dca089ff-fabe-5dfd-9155-fd95e5e738e2 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
dba1a5c0-d0de-5d6d-b571-cae043ee78fd | note | – using the correct and complete set of drawings.
99e63a8b-aa25-5791-87ed-2128adff683e | note | – all drawings are the latest revision.
0d37360b-f68e-5e84-8b12-8e39c9daf073 | note | Reference Documents - Drawings / Aconex Register
e1eaf8d7-ca21-5f67-8a56-b4657842d17c | note | Inspection/Test Method - Verify
8d9414de-68d1-5128-86de-09bf100caffa | note | Record of conformity - Drawings and drawing registers
cac2c81a-95d7-527f-ba64-e416799584f2 | note | HP*
7f726786-8251-5e46-83af-455cd1302016 | note | Responsibility - Project Engineer
10a06d2c-0727-5f35-9bdc-3e4672b3a79c | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
9e830bc9-6113-5cb4-9a34-eba9ba021b42 | note | Frequency - Prior to commencing activity
9418b1c8-716b-5ea0-a719-ba1ccd42d304 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
81fa21ec-76e9-5833-816a-8d4f88d14f18 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
5b75c70f-9e38-5946-9d65-a6a3204df160 | note | Inspection/Test Method - Visual inspection
1deda285-60ca-5351-b3d3-e42caadce55e | note | Record of conformity - This ITP signed
3767b002-064d-5f2b-a08e-c974d9b21578 | note | HP*
4cbb564b-8fa9-59a0-893a-1706d763fe3f | note | Responsibility - Project Engineer
343fa595-a04c-5db6-b296-f79f8b91a9a9 | date | Date Completed:
a3708d55-ad49-5ddc-9f9e-a05b95777606 | checkpoint | 1.3 - Definition of the work area (survey)
2a01ebfc-039d-5ba5-a171-e3056faf5778 | note | Frequency - Prior to commencing activity
ff5b4170-c852-50d2-86d7-a1bfe1389ea8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
2360f750-b416-5fe2-bb88-558bdaeec326 | note | Reference Documents - Drawings
d84c98fa-fcb1-575a-a417-1f8ecf6ca0a3 | note | Inspection/Test Method - Visual inspection
79ded8b4-2e16-52fe-b9f2-cb72048a09e9 | note | Record of conformity - This ITP signed
3de3e26d-10d8-5785-bd23-f9c04341127d | note | HP*
bf9859db-19aa-5d27-9a66-8544815d825c | note | Responsibility - Project Engineer / Surveyor
b31fbb3b-c423-5d91-a5ab-4207c71c863d | date | Date Completed:
69a20f57-e9c4-5c06-8e72-d3bebb914fa4 | checkpoint | 1.4 - Check conduit compliance
ca75f7e2-9fe0-5872-8553-2e25ec68ebeb | note | Frequency - Prior to commencing activity
bda3bffd-140a-5c53-a9d5-ed07bf6460c2 | note | Acceptance Criteria - Ensure that uPVC conduits comply with AS 1477 or equivalent AS 2053. Shall be heavy duty, orange for electrical services and white for communication services.
0a9b4a58-a26a-5475-97ba-dfaf945b9ef1 | note | ○ Ensure that pipe diameter is correct as per the drawings.
2228e221-89bc-5623-96c3-d7daf7b13c94 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.4 AS 1477, AS 2053
cf302bda-01b5-536e-9688-e3b16a7a9c35 | note | Inspection/Test Method - Verify
86110fe3-7368-5cab-a456-dd3623a8f731 | note | Record of conformity - Aconex reference This ITP signed
5af08d7a-b984-5b02-9978-fc0db3cb6214 | note | IP
593f0f5e-a639-5aa7-b8c4-36cdafa92cab | note | Responsibility - Project Engineer
cec57df8-208a-5528-9608-2e86de3bf819 | date | Date Completed:
82950bf0-d615-5ff3-a99f-7bf277f6815e | checkpoint | 1.5 - Check bedding material compliance
5f2c1b92-3599-5a8a-834a-427ad7a18190 | note | Frequency - Prior to commencing activity
6fb6c1f2-9d81-5b59-b99f-e5f49ee6ddb5 | note | Acceptance Criteria - HOLD POINT
020b801f-5412-5d77-9d2a-2145dfd4cc60 | note | ○ Ensure that conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification.
8727225b-c976-525a-8b39-a8a70dd7c5b2 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.3
7636d754-0604-5df7-9841-02fb51f9bc27 | note | Inspection/Test Method - Verify
c4bc2b8d-464c-5b8b-a1ce-34e10567a9a9 | note | Record of conformity - Aconex reference
c202e6eb-af88-5ad4-b192-43b7eadbf787 | note | TP / HP
c7e23314-96b2-5d4f-95ae-b805ad0bb910 | note | Responsibility - Project Engineer / Principal’s Representative
f52f6ef1-99d5-583b-9def-0012f8fe7415 | date | Date Completed:
172b0902-de79-58d1-95cc-4735738969af | signoff | AUTHORITY HOLDPOINT
684111da-41f7-5ea1-aa5a-130ec2c9ca08 | checkpoint | 1.6 - Locate and prove existing services
b481a873-1b9b-587c-bb85-6db6664f6e12 | note | Frequency - Prior to commencing activity
079fe04c-e0fd-5abd-89d5-2beade7873ef | note | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
cab71392-4f1d-5730-b896-8dc966adc310 | note | ○ Contractor to obtain excavation permit from APAM prior to any demolition works.
c12281a4-c363-5678-af29-17485de6279a | note | ○ Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
e3f2e297-de92-5390-a29a-e6ecffaa0e1b | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.15
f37db078-ea05-5781-947a-5141c960d86d | note | Inspection/Test Method - Verify
47c50d96-5b10-547a-b164-c366eded8ae3 | note | Record of conformity - Melbourne Airport Excavation Permit
6ae7ada3-828e-5efa-b02d-1f97814f83c4 | note | HP*
21f800ce-67b2-55b4-b05d-59bd92905a1b | note | Responsibility - Project Engineer / Surveyor
22b782f4-e33b-586a-9f54-a5ccbadb9f8b | date | Date Completed:
648931ca-ea92-5007-b762-3e625bbef167 | section | 2.0 - Construction
2b66cee4-ab86-506c-82c0-b3598e5d3273 | checkpoint | 2.1 - Excavate trenches for conduits
5bd4a899-f778-5d8c-b992-335b43cabe80 | note | Frequency - Each lot
47fee060-3be0-5cd5-92ff-7cc2ecafb650 | note | Acceptance Criteria - - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
08811dd7-8796-5bb3-8ac0-cdca7c1dae5f | note | ○ The level at the bottom of the trench shall not be above the required level at any point.
6b0450c6-a3f2-5f66-89e7-7f3673de58ad | note | ○ Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
80e258da-eebe-5947-af44-4382d2235a85 | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.6
6ef7be7b-a588-5265-ac5d-3cdc2601cbf3 | note | Inspection/Test Method - Visual inspection
8be7f315-2c5e-5326-8ad1-19ab81608184 | note | Record of conformity - This ITP signed
4c8ef0f8-c97d-5915-a9db-4f39a711b06a | note | IP
01d592f3-fdb5-502b-82ac-c60be15407cf | note | Responsibility - Project Engineer / Foreman
21de2358-3437-5033-a795-74e2bc6a791b | date | Date Completed:
35a2a621-7af0-57be-b8a1-332a08eb0e12 | checkpoint | 2.2 - Existing services crossing new conduits
ad540ad0-90dd-5cfe-b7b4-cd38d1129a8b | note | Frequency - Each lot
8610695a-f5b6-5cde-aede-10dd232465a0 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
15c7adb2-452b-5f6f-903e-0b6b2d59e030 | note | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
8c691458-22ee-56c5-8d0c-e75f284652b2 | note | Reference Documents - WMS002 – Working Near Existing Services
c4d3d455-51a3-5cf5-bc75-56a0a78aa1bc | note | Inspection/Test Method - Visual inspection
62d0f4e4-b8ea-51a3-badf-52674410f43c | note | Record of conformity - As-built survey report
cb8ad14c-84af-5a07-9bcf-1568b1c7441e | note | SCP
8a014a96-019e-5793-8c6b-9d9a6c7f2a18 | note | Responsibility - Project Engineer / Surveyor
b9cd8c33-d715-597c-b3a2-9debd806dc21 | date | Date Completed:
1d54f976-f7c0-5a5c-8aaf-b6c27df0189f | checkpoint | 2.3 - Laying and jointing of conduits
a6d44dc9-0037-5d39-8d4a-0172eede369a | note | Frequency - Each lot
f32cb045-a292-5246-87d4-d27f7f190010 | note | Acceptance Criteria - - All conduits shall be rigidly supported and positioned by concrete or plastic spacer blocks so that no displacement occurs during backfill.
a339ad4c-3e9f-59ea-b9f1-185bbda9515c | note | ○ Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
cff3ddce-2f19-59ad-b7ba-f60ad7f88809 | note | ○ Number of conduits and duct route to be confirmed for conformity with design.
a0edff87-a828-5c1e-8c99-46f0d6a2a643 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.7
9101403f-eeba-575d-82b0-a0702d54a132 | note | Inspection/Test Method - Visual inspection
df67a876-f59e-5da8-97cb-148c5ebf4c95 | note | Record of conformity - This ITP signed
2aeb0379-0633-5c03-af97-8446cd0ed6ba | note | IP
8e72718a-8e55-528f-8731-d5c59ffe18f2 | note | Responsibility - Project Engineer / Foreman
e4395f7c-9b90-5450-bc92-c1e031fe526d | date | Date Completed:
52ec0b35-2d23-569c-af3c-96adb7e7aae9 | checkpoint | 2.4 - Survey as-built
8ae894e3-637b-5fdf-a08c-96583d56b234 | note | Frequency - Prior to backfilling each lot
7d523446-7f0c-5c9e-839a-bcbb7c6c5b79 | note | Acceptance Criteria - Surveyor to pick up completed conduit runs before backfill
b3ba4b9a-ccd1-531e-96fd-fd243d60682e | note | Reference Documents - FH QMP
4d18d776-ce5e-598f-81ad-04054ca2922a | note | Inspection/Test Method - Verify / Inspection
3f74a3af-7a35-51d7-bdae-fd3f196f6863 | note | Record of conformity - Survey report
83f3fdd7-21a2-5f4a-b12e-2487dac36cee | note | SCP / IP
99848c36-7396-5e20-b1bc-49bfd1f61ff2 | note | Responsibility - Project Engineer / Surveyor
69571608-498b-5acb-b8a7-5ef9bf8be068 | date | Date Completed:
4ac71dda-3d00-5e58-b229-b9125906adbe | checkpoint | 2.5 - Pre-backfill inspection
63e1ddfb-324e-5352-9960-19ac059be51f | note | Frequency - Prior to backfilling each lot
6ca47f8f-1783-5edc-9745-8a5e7115652f | note | Acceptance Criteria - WITNESS POINT
30198f96-49f8-5a96-8f9d-8b6683ec08e9 | note | ○ The Contractor must provide the Contract Administrator with five (5) working days' notice of intention to backfill trenches within a Lot. This must include details of the date and location of the proposed work.
e44ee0b4-2433-5de2-ac27-d8b2b4fde155 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.1
8562ecdb-2c4f-5f07-b889-1f23e5f9f6ed | note | Inspection/Test Method - Inspection
652e0800-e063-5a07-ba7f-3bc1de37badc | note | Record of conformity - This ITP signed
43d6d4a8-04db-576a-b546-2c9247a84fc5 | note | WP
cdb2e9f2-10a0-504c-af39-93028bb6a316 | note | Responsibility - Project Engineer / Principal’s Representative
573ab9dc-8565-5dac-ad8b-861c41d100c2 | date | Date Completed:
e682c742-f93b-5e2c-89bd-4ca838794a9a | checkpoint | 2.6 - Backfilling conduits
9b79ab7a-473c-565a-a81c-bb41bd53e5af | note | Frequency - Each lot
84a78bd4-7be1-5deb-bfa2-179e60c267dd | note | Acceptance Criteria -
abc9cbbe-1707-5518-b988-c316816c6500 | note | – Concrete encasement of conduits: –
566010c6-75cd-57c1-8111-ec78c8b7c60f | note | ○ Conduits to be encased in 5MPa lean mix concrete as per drawings.
fa092b72-e40e-55ac-98ab-6d7b0007dfee | note | – Trenches in existing pavement: –
de46ec6a-dabe-58d8-8332-7a8328fca9ab | note | ○ Surface shall be reinstated to match surrounding pavement.
1e85192b-473e-51fa-b43d-fedae8eb6680 | note | ○ Unless noted otherwise, reinstate asphalt pavement surfaces to a minimum of 70mm (or to match existing depth (whichever is greater)).
59f28043-12cd-563f-a677-368f1909068b | note | – Trenches in new pavement: –
9fe060f9-0b13-5bae-a2af-be5f946c1a9c | note | ○ Pavement shall be constructed as per the drawings and specification.
26f5dcc8-5e5e-530f-9875-62c54f019961 | note | – In grassed areas –
565604c9-ed7f-5020-8def-0499a9cb91e2 | note | ○ Conduits to be encased in compacted sand bedding. The material shall be non-plastic and comply with properties specified in Table 3-1 & 3-2 of the specification.
12860750-fde5-5604-8134-1a02f743e65e | note | – Backfill layers: –
a744eb01-f590-5431-8686-57e6fd14281b | note | ○ Not exceeding 300mm compacted thickness.
db2c2dad-8f21-55da-88e2-08aee972a7b5 | note | ○ Not less than 90% maximum dry density (test no. 5.1.1).
4cf81bc4-7e92-5a64-a0bf-ff13456f981a | note | ○ Not less than 70% of density index (test E6.1).
dbbd9d0e-81bf-518b-aa0c-e8531768a32f | note | – Compaction testing carried out at a rate of not less than: –
1bb80dc0-28a3-57ad-9a07-c358bd21d958 | note | ○ Bedding: 1 soil test report from the supplier per 300m3 of dust supplied.
dedee7fb-9db4-5c23-90a0-35190daff671 | note | ○ Backfill: 1 test per 400m of conduit laid per 0.5m of backfill depth.
7550c732-f38c-537f-9200-c01e9ff9a7d8 | note | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.8.3.1, cl. 3.8.3.2, cl. 3.8.3.3 AS 1289 Test no. 5.1.1, Test no. E6.1
3a66f37e-934e-56f1-886a-3e68eae11bff | note | Inspection/Test Method - Verify
c5efc8e5-daf7-5e6f-ab90-b25e211022dc | note | Record of conformity - Test report Aconex reference, This ITP signed
5f74d6c4-d856-5fc1-8b57-bf837c2a8afc | note | TP / IP
1c9176f5-613e-565a-a8f8-7dec5cc6ab00 | note | Responsibility - Project Engineer / Foreman
e5b430f5-d150-5815-94e9-18ca37d37822 | date | Date Completed:
6db2beff-d160-5ad0-b44e-6a0604821a02 | checkpoint | 2.7 - Conduit markers & warning tape
45368ed3-77e7-5171-ae93-bcbf8cd8ee0b | note | Frequency - Each lot
29da3ecb-bb95-5c21-b2a4-32111784782f | note | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
59d30ef8-d784-5d37-8c08-6a0a18f2bed1 | note | ○ Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
28cf0053-f801-58d7-b6cb-b6e4e75f8fc3 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.11, cl. 3.12 AS 2648.1
433db3cd-880b-58a5-96bb-b64607ef2cca | note | Inspection/Test Method - Visual inspection
4c8cc8c4-fe17-5dec-9fdf-60b2222e0f42 | note | Record of conformity - This ITP signed
edc91752-a980-5b96-8dc6-f1574072c350 | note | IP
baaf9703-c6e3-5675-8495-e3496825ad94 | note | Responsibility - Project Engineer / Foreman
d5d45f2f-1e5f-5b35-b476-6a00e3449a19 | date | Date Completed:
94428992-2156-5864-9d44-a4e563d52ab6 | checkpoint | 2.8 - Checking of conduit lines
6ea7d1b1-ffa1-5921-83a5-3151011919a2 | note | Frequency - Each lot
de28fb13-ba74-59ad-8e7a-eeeab8d601aa | note | Acceptance Criteria - HOLD POINT
bcbeb64e-f56a-569b-8128-3ed37af656e4 | note | ○ Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
38f811d4-24d1-5c07-9dac-4c36110837a8 | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.9
6634aa92-d07c-546d-a377-973a89791ee2 | note | Inspection/Test Method - Visual inspection
66351acf-25c2-572e-ab3d-e8deb113b632 | note | Record of conformity - This ITP signed, Avionics Primary Trenching Checklist
b4c3b1d6-8dc3-5b46-9a4c-652f4e4c3e1e | note | HP
4bae3308-85c1-5999-a239-9a56912eb3a0 | note | Responsibility - Project Engineer / Principal’s Representative
c6c08a2b-8e73-5271-b9f4-e2d11ff92c70 | date | Date Completed:
11c0ea96-4007-5115-b506-238100aaa986 | signoff | AUTHORITY HOLDPOINT
dfb3fc63-1dd7-5f16-8bb7-58300a6a0328 | checkpoint | 2.9 - Conduit draw cord
8df5d2ce-8815-57bc-921e-dc99ad009ab5 | note | Frequency - Each lot
16282afc-900c-56dc-8833-be8ad010029a | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
68f2e7f4-e2ad-5085-8702-3990e8c8fc8a | note | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.10
5b24093c-85b7-51d8-84d5-238e6ef03f3e | note | Inspection/Test Method - Visual
89ce2275-1a9c-5b93-a389-9b14dc59ca27 | note | Record of conformity - This ITP signed, Avionics Primary/Secondary Trenching Checklist
883bc1e9-e8ae-54f0-a3c5-3319d36a752e | note | IP
33cd7518-82c4-584a-a692-fd104f0153a6 | note | Responsibility - Project Engineer / Foreman
d83875da-a9e6-515e-856e-19e14be8752f | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
39a43258-897d-53f9-8eb9-2a6c7ad42338 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
53ed455d-bef3-5f8d-9f79-194429c69199 | textbox | Print Name:
665cc1aa-388f-535b-8ea2-10b9cf3d21f6 | textbox | Position:
4f86ab93-9bc3-5ff3-b5ad-bb0b015601ba | date | Work Completed On:
24a47102-b649-5f4b-8d21-4dc7e7aff131 | date | Date:
d0319b60-9681-5d64-8f93-33fe55208828 | checklist | FH-ZU2-QU-ITP027 - AGL Cabling - Rev 0 | itp | ITP027 - AGL Cabling
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
084ecec0-08c1-5480-8d74-efa85d9a76ee | note | Frequency - Prior to commencing any activity
9cf17b9a-0296-5121-bb59-c09361c4f722 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
c79d28c3-2ad0-5255-8028-702fc73647b9 | note | Reference Documents - IFC Drawings
fc5214f9-eb77-50a2-b18d-2cb2846dce3b | note | Inspection/Test Method - Verify
f53bce20-91ed-5f05-8562-ea715bec3633 | note | Record of conformity - Drawings
3956a579-86ec-5eff-9e4a-7cb57c2eb271 | note | IP
15d1bba0-187d-5a60-9f6a-74c25f25b456 | note | Responsibility - Project Engineer
1d8ecb9a-5b52-5485-b3b7-52afe398bc4d | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
c6e968b0-29d1-5fc3-a00b-f3487f707c88 | note | Frequency - Prior to commencing any activities
e14bf65a-9dc4-5e81-ac7a-17abebc913e8 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
b0147824-8e3a-580c-9a41-7035645ed709 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
e9e53ba2-3666-573d-8745-b4f4b768c75b | note | Inspection/Test Method - Verify
5ee7f0d3-73d9-5ebd-995e-3226eb9d0f9a | note | Record of conformity - Site and office inspection
4ccf422a-beef-54e9-9e0f-58c36f451a5d | note | HP*
a0b07714-756d-5a16-80f7-dd77e5338b67 | note | Responsibility - Project Engineer / Site Supervisor
5b08f91e-7c1b-542d-9d0d-13ac51c58d6f | date | Date Completed:
520fc374-5377-50ba-b879-f98bb15b317d | checkpoint | 1.3 - Existing service location
f7e0a76f-bb66-599b-8dc6-5c96fecf6108 | note | Frequency - Prior to Start
8b5366c1-2c24-522f-b19b-28fd5bc1b429 | note | Acceptance Criteria - Prior to installing any fittings, location of all existing services to be identified and marked onsite.
73376e7b-6ec6-580d-b9d0-34afd28e1bc4 | note | ○ Services located in the works area to be proven.
9c79d5f1-9689-52f1-9398-fb9f9771e9c0 | note | Reference Documents - SWMS
eea18c1d-6def-5b6b-b17e-24506aa8f41c | note | Inspection/Test Method - Verify
dff13372-6be7-5222-b692-73cfc179bbb3 | note | Record of conformity - APAM Excavation Permit
b56d90d2-979b-5488-a1bf-01570a99015c | note | HP*
d5c96297-fe67-5e2c-85c2-7f12b293f64c | note | Responsibility - Project Engineer/ Site Supervisor
23a9c78d-9f3e-5f6b-8fdb-ebd1dc1753f4 | date | Date Completed:
b4360bab-78b3-5063-ae73-2589e72b2f02 | checkpoint | 1.4 - Cable route
03bcb88c-dbb4-5a7c-8025-39e72b794caf | note | Frequency - Each Lot
a0bcbaf1-c3f4-5bab-a543-7fa6c5d4066e | note | Acceptance Criteria - HOLD POINT
9a5ce38e-3353-5874-b422-019c9ab8302b | note | ○ Primary cabling route installed as per path shown in construction drawings (and/or approved markup).
90d91336-1d81-5d57-801c-c3a066eaf8ee | note | ○ See relevant lot from ITP 025 – AGL Conduit Installation for cable route.
44c77117-fef3-567e-87e8-19d52c85c1ef | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1, ITP025 – AGL Conduit Installation
2e613ce2-b0af-5d92-a459-99d17ae91845 | note | Inspection/Test Method - Verify
3d98ff75-4225-596b-9e58-e1a3c8c2539d | note | Record of conformity - This ITP signed, Aconex reference
b625d644-30b5-51e1-9af1-cccc76587060 | note | HP
01e00bb4-877a-5213-b35e-a1ebdf6557b0 | note | Responsibility - Project Engineer / Beca
29c73fdf-273b-5d49-b87c-712ec8e4165c | date | Date Completed:
5245df6c-7530-5e73-8dbf-68583d02af62 | signoff | AUTHORITY HOLDPOINT
43b5292c-d817-5d31-a654-aa9a9fb6996b | section | 2.0 - Material / Equipment Approvals
122f376e-e033-556a-af86-1b7db76a3bb9 | checkpoint | 2.1 - Primary cable
a4cfcd29-f001-5898-99d5-aea2ed7dae11 | note | Frequency - Prior to Start
20690dcf-c0f0-5f39-8aa8-2fde40a065b5 | note | Acceptance Criteria - Primary cables shall be:
9670b5af-42c5-5b09-bf68-75b15edff80f | note | ○ 6mm2 cable with black polyethylene jacket and copper tape screen
e637605e-20ef-58b9-90e2-6be82f3e36a7 | note | ○ Rated for 5000V
d326591b-4763-538d-83da-89729d6a441f | note | ○ 7 Strands
ee079a69-7ee0-5d57-849b-4011e89e0ce7 | note | – or approved alternative.
c0c1ca0c-b955-5091-923f-7ed9c45285c9 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.1
c563a629-6af2-5db4-910c-9e5cb7e36225 | note | Inspection/Test Method - Aconex
d377bcc3-b1b0-52ec-b726-e8eaf8ee04f9 | note | Record of conformity - Datasheet
4f6e1f99-b816-5649-902a-f1371e263942 | note | HP*
50157a5e-7a28-57ed-b565-fc6723f7cfd2 | note | Responsibility - Project Engineer
2ff1bf0e-8e3b-51f3-b9f1-8f1a2390a308 | date | Date Completed:
3432dcfd-91fe-5c00-854b-7b55f23a5161 | checkpoint | 2.2 - Secondary cable
02c825d0-9463-5d10-908a-5776a6ee38c1 | note | Frequency - Prior to Start
52f4d154-8af1-5719-8224-0f418e45606c | note | Acceptance Criteria - Secondary cables shall be:
44d71d7e-47f4-53ca-8fe0-dcdbf79ac714 | note | ○ Min 4mm2 cable with black nylon jacket.
7a40335d-5509-539c-924c-6fcda49c0716 | note | ○ Rated for 600V
3872fc69-1b47-510d-907f-98720bfaf136 | note | ○ 56 strands
e8ab4674-6ef6-53e9-a70b-7f0d461d0da5 | note | – or approved alternative.
8aff2a2b-fe11-52f6-b2e3-23abc4326c74 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.2
4ae35278-4742-5729-8cfd-68865b2188b6 | note | Inspection/Test Method - Aconex
3e6ca5c6-27ef-542a-97b7-94c52dd40f63 | note | Record of conformity - Datasheet
0301d6eb-5530-5d94-9a47-18403d44c79c | note | HP*
3f600ea7-c96b-5ede-aeb1-e1890b3f777e | note | Responsibility - Project Engineer
29144972-5c24-503e-ba07-de15f3241fda | date | Date Completed:
262538c1-c2d6-51b8-95ee-efd3a2cfd00b | checkpoint | 2.3 - Cable connectors
91357c0b-6615-5f70-a6d6-3e23d4560efe | note | Frequency - Prior to Start
c92cf1f7-00a2-526f-8576-138d0d9873c3 | note | Acceptance Criteria - Plug and sockets shall be further sealed by the application of double lapped layer of self-amalgamating tape protected with a double layer of PVC insulation tape.
b99c8fd4-8940-5c39-8668-8f6a4f175a5b | note | ○ Field attached plug and socket connections shall be constructed in accordance with the manufacturer’s instructions.
4417737e-8692-58bf-8c97-f3b6cdff95d2 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3.3
f3e252d4-b3cb-52d1-8e5a-23b63082c72f | note | Inspection/Test Method - Aconex
bb294352-9e84-5ee6-8863-ac6ad920bfa5 | note | Record of conformity - Datasheet
d4a2e8f6-4eff-535e-9cd8-cf7e67cd3e05 | note | HP*
1331058a-48b5-5da6-a7f9-208bfa631de0 | note | Responsibility - Project Engineer
3f816d24-9eef-5296-a933-b1e06087f758 | date | Date Completed:
0f506738-ab3b-55ca-85b8-126890ec5d15 | checkpoint | 2.4 - Series isolation transformers
6d768cdd-92c9-5df0-b66f-03310679378c | note | Frequency - Prior to Start
58cc99f6-1105-50d9-9640-c9b017da833e | note | Acceptance Criteria - New SITS shall be:
36cdee4a-1209-55b0-9a64-12ebbb5cffd0 | note | ○ Fully encapsulated synthetic rubber watertight (IP68)
0f66dc6f-e6c1-5947-ab6b-b7f626d5f9a7 | note | ○ 6.6 Amps rating
9e43bca9-5498-5d13-b69e-72fbf134f526 | note | ○ Minimum 600 mm long primary tail/1200mm long secondary tail
aa3245e2-c20b-5312-94f0-c807b7047f1e | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.3
d8e756e7-9177-5d62-bf54-1db70c39f9bc | note | Inspection/Test Method - Aconex
ad67297c-22b9-5468-9afe-e2de309eebb7 | note | Record of conformity - Datasheet
58c85867-a8e0-5bae-8e91-893355021d6e | note | HP*
c19a30da-ceda-51d4-9c29-64d1c6f68cf4 | note | Responsibility - Project Engineer
aa5c7237-766a-5f7f-ba7c-231f10cec1ab | date | Date Completed:
577a7835-cc47-549f-b10f-2fe7edb3af10 | section | 3.0 - Cable Installation
5592fe8f-ccb0-5b75-99f5-348b238dc66c | checkpoint | 3.1 - Primary cabling connections
ea9d079c-2a66-55c9-bb18-242e37729a70 | note | Frequency - Each Lot
2243b91b-3809-53de-b099-828910c65b19 | note | Acceptance Criteria - Underground primary cable joints are only to be made where the cable length exceeds the maximum cable drum length or jointed to existing cabling. These joints shall only be made in pits. The joint shall be waterproof and shall allow the jointed cable to be installed within the pits without causing damage or undue strain on the joint.
043c37d0-da9d-5747-bd65-773ae0272a95 | note | ○ Use only approved plug and sockets for joints in primary cables. Primary cable must be jointed to the primary cable tails of SITs using approved cable jointing kits.
6c40c918-3883-5df6-aad4-88a5c5ed27aa | note | ○ Plug and socket connections shall be constructed in accordance with the manufacturer’s instructions paying particular attention to the screen continuity joint and ensuring the rubber housing and insulating silicone remains free from moisture, dirt and debris.
6c65db7a-3b38-512a-be73-ae5e9b1146ca | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.1
e13925a7-705a-5c56-b184-22641a23caf9 | note | Inspection/Test Method - Verify
846b7873-773c-51e1-9e00-f184596e2726 | note | Record of conformity - This ITP signed
5f3c0794-3a9e-52c7-8071-6008d5ab6eaa | note | IP
508909fd-f8cc-5530-ba2b-0e5bc3884e17 | note | Responsibility - Project Engineer / Site Supervisor
b019303d-e7e5-5e18-a362-fbdeb9436f53 | date | Date Completed:
2cdc1460-dc79-5817-9790-ff12ef77b52f | checkpoint | 3.2 - Secondary cabling connections
15614fa1-b345-5403-9db2-3c9f0d2ffb08 | note | Frequency - Each Lot
bffd1973-f393-5401-8d63-a0570a17a67d | note | Acceptance Criteria - Individual secondary cables shall be provided for each lamp contained within individual lights. The secondary cable shall be installed in a single, unjointed length from the SIT to the AGL light.
4b01cb52-b615-5ade-bc21-bcf411c5277e | note | ○ A secondary cable that shares a common slot shall not be installed under any light base. Any joints within the slot shall be made utilising crimped links “staggered” and be installed external to the light base.
afdd9390-f698-535e-b1c6-527752df2859 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
8ca84581-aadb-5430-8c67-78e90d21cd14 | note | Inspection/Test Method - Verify
9304141f-7b41-57c3-98d7-5392d95ffc0d | note | Record of conformity - This ITP signed
13e87572-3f6c-53aa-a953-1be7bb496315 | note | IP
c4862c2c-2c95-5f55-9d2b-c389b45c68db | note | Responsibility - Project Engineer/ Site Supervisor
47ae2efa-08a3-51a3-a7b6-964e99817080 | date | Date Completed:
903fd3d2-62dc-5f1a-a81e-4e63048c1527 | checkpoint | 3.3 - Secondary slotting
9e096c81-d57e-52de-aca2-c387d8e3d981 | note | Frequency - Each Lot
48ee0b44-923a-5497-ad9f-8d80f41f7cb5 | note | Acceptance Criteria - Pavement shall be saw-cut to specified depth and thickness and slots cleaned/free from debris.
d9f87c01-cdd0-503a-b474-f622021a407b | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
0165c77b-68c1-57d5-99ba-46d16a829b60 | note | Inspection/Test Method - Verify
48f4a900-5a6f-59b6-8d1d-400ca5d8111b | note | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
549d7b64-d47a-550f-ab5e-1402dff8847f | note | IP
2b2115c3-a236-5ea3-a202-5f0e0fa7d70a | note | Responsibility - Project Engineer / Site Supervisor
6c2a9dff-ac7d-53b5-be06-592d0d48ddd8 | date | Date Completed:
d66caef2-751e-5767-b48b-3bfa0b4bb7bb | checkpoint | 3.4 - Max conduit capacity
b6b31181-2c85-5d37-8d46-a75bbb4e7e8d | note | Frequency - Each Lot
1b87870c-f6d7-5e0e-b697-a38d3829ca60 | note | Acceptance Criteria - If APAM approve three or more cables enclosed in conduits and/or ducts, the total cross sectional area of the conductors must not exceed 40% of the internal area of the respective conduit and/or wiring duct as recommended in AS/NZS 3000 for short distances without bends.
333a725b-5074-5b9a-ae2e-c774ef15a1cd | note | ○ No more than 10 primary cables shall be installed in a conduit
0bd5e56b-56cc-5808-8b49-a3cdf5ed0f66 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.2.3
f1737631-1a73-5351-9176-dc1ede50b9ce | note | Inspection/Test Method - Verify
4d8d6ccb-8ba4-52f7-a489-6cd2068f8376 | note | Record of conformity - This ITP signed
c7ded4d5-231f-5382-bde9-aa38ed255345 | note | IP
6d7361e5-1b4c-52bf-9fa4-0c30d11ac193 | note | Responsibility - Project Engineer / Site Supervisor
e226c20e-d9ce-5287-86b9-610eee1e2e48 | date | Date Completed:
e507161a-d055-5c27-8551-5f26faa6d11c | checkpoint | 3.5 - Secondary sealing
f062f36f-3fa7-5e14-b5de-d61d9ea3b475 | note | Frequency - Each Lot
1adcea5f-6e85-5300-9bcd-c69c1f01545a | note | Acceptance Criteria - Backing rod shall be installed on top of the secondary cable, followed by flexible sealant:
aa8d978a-c98e-549a-9289-0b3b5c4655d8 | note | ○ Dowsil 888 to be used in concrete expansion joints.
5ef02737-3cc2-55cf-abfb-49a9350af82c | note | ○ Dowsil 890SL to be used in asphalt slots.
14f281c1-a5d0-5029-8cd4-1f58a35b8d27 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 4.5
2ae4e0a1-e1a0-5ce2-8843-962ababbc36f | note | Inspection/Test Method - Verify
b37e2ee4-593d-58af-8372-8386987aef16 | note | Record of conformity - This ITP signed, Avionics Secondary Slotting and Sealing checklist
fff47d18-3cb4-5870-b270-f3edbd0d0f6f | note | IP
64903664-af96-53a8-81e5-5638822bd6b4 | note | Responsibility - Project Engineer / Site Supervisor
ec73ec40-fd32-5e9a-a5fb-1503f94d5f0f | date | Date Completed:
b20adada-f2f8-51de-bde6-091148b0e106 | section | 4.0 - General Works
5442b8e1-6da8-5222-b6f0-f588fc9cc3ae | checkpoint | 4.1 - Protection of existing cabling
3bf93f01-555b-54d4-a582-037f3bbb5d03 | note | Frequency - Each Lot
248d71c1-0b97-55f6-8e5f-7236a7339eb2 | note | Acceptance Criteria - Where the crossing of existing secondary cables cannot be avoided, the existing secondary cables shall be reinstated and made good.
614967ac-49be-5eb3-b4a4-5e2a416fe8dc | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5.3
197c8456-1b37-576d-b956-4c9dfb1ecfc6 | note | Inspection/Test Method - Verify
f140fba5-11b8-5a1a-8466-c67126c7eb90 | note | Record of conformity - This ITP signed
251241da-1c79-5865-ad28-350adca01eab | note | IP
7fb33dc8-893f-5f67-bda9-36b54ed65019 | note | Responsibility - Project Engineer / Site Supervisor
80dbe2aa-e49d-5f8f-91da-5a384a46d295 | date | Date Completed:
7aaaccdc-6334-521c-8b32-81e7323ac175 | checkpoint | 4.2 - Slack
5bca6755-97ff-5b88-b7ca-e3148358c514 | note | Frequency - Each Lot
cdedd2a9-f061-5069-9b6a-059946986c83 | note | Acceptance Criteria - Primary Cabling – a single minimum 500mm diameter loop shall be made in each primary cable where they pass through a pit other than a SIT pit.
d5ba2815-1717-57c3-aae8-1159abdf46e2 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 5.5
e94e0a39-5c2a-5943-9aa6-a1c3d52fafcd | note | Inspection/Test Method - Verify
6621fec5-b16e-52a2-b4a9-9e931b50831e | note | Record of conformity - This ITP signed, ADBSG Installation of Primary Cable checklist
52ae351d-e471-5fe6-918e-14decf9c1691 | note | IP
b267a4d4-a105-5628-83f3-576bf3477c0a | note | Responsibility - Project Engineer / Site Supervisor
dbcf3142-60f1-5794-960a-1cc3d3e52aa5 | date | Date Completed:
08e5f340-f964-53f9-9d5e-d37deed19b8c | checkpoint | 4.3 - SIT pit earthing rod
a14c2c6f-127a-5a25-a0f4-5c1bdeb75cf0 | note | Frequency - Each Lot
7b891f9c-47f9-57ca-a3b9-2c4ddb46a812 | note | Acceptance Criteria - Earthing inspection pits shall be provided with earth electrodes of sufficient length to achieve the required resistivity of less than 6 ohms. Earthing electrodes shall be copped clad stainless-steel rods of minimum size 13mm diameter.
762d0357-b40a-554d-8701-108c165fcc01 | note | ○ The earth wire size shall be 16 mm2 PVC insulated copper, other than where equipment is wired in PVC/PVC cable in which case the earth continuity conductor may be enclosed within the PVC/PVC sheath.
521a7e30-fe6b-5679-8531-dafd848094db | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 6
2c89753b-8848-5daf-9cb0-974bfbce040c | note | Inspection/Test Method - Verify
e89b7054-9b6d-546e-a45e-54c3166779d3 | note | Record of conformity - This ITP signed
e24392e3-32ab-5e0f-b556-44280a507148 | note | IP
c3b3db98-4d1e-533c-82e4-315160b85025 | note | Responsibility - Project Engineer / Site Supervisor
7f0d89f1-0c1d-5e4c-b946-b26987e2976b | date | Date Completed:
b6ec13a1-58c8-59f1-8549-f219e0c553bf | checkpoint | 4.5 - Identification of configuration
8d761c6c-2d7d-5fb8-a94a-0edb816aa6ff | note | Frequency - Each Lot
76f55867-4af1-5970-addb-837d87187468 | note | Acceptance Criteria - Label all cables for new and existing circuits remaining in service at every access location such as pits, duct crossings, and ALER. Position the labels such that they can be read without displacement of the cables.
82e52b35-f14d-51bd-a162-8bfe8c2d6a02 | note | ○ In transformer pits serving multiple taxiway lights, the Contractor shall label each secondary cable at the transformer connection to indicate the designation of the associated light connected.
d8f2b1aa-e672-58e9-9d9d-a554cb0f8c11 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl. 7.2
2326d521-a431-5428-aab0-e20472db1be7 | note | Inspection/Test Method - Visual
410ba2ff-f505-5e22-b7e3-dcacb0bad6d6 | note | Record of conformity - This ITP signed
6218bb73-084a-5d77-b9f0-be4ffb63a444 | note | IP
99074f27-35e3-5c20-8bef-1e9b8369b278 | note | Responsibility - Project Engineer
e7cd0188-1683-5cac-854b-edca2a3e23a4 | date | Date Completed:
3e68cc9c-da03-5c12-a911-0dcb053881a0 | section | 5.0 - Post Construction
a033fb3e-023c-53fe-b5e0-911e943a0480 | checkpoint | 5.1 - As-built Documentation
11dd7507-b970-571b-ac32-4491371ee8ff | note | Frequency - Prior to practical Completion
5d2dc373-07b2-5763-ae3f-1a29a8fb553a | note | Acceptance Criteria - Submission of as built report showing cabling route submitted to the Principal’s Representative prior to practical completion.
36472891-ad44-5c25-b118-0d207308de4c | note | Reference Documents - FH QMP
0e8769aa-d815-501c-96e3-f869244cd8fa | note | Inspection/Test Method - Verify
9c3385b9-97e5-5e23-9ea1-df36f907e5c1 | note | Record of conformity - As-built survey report
ac3a000e-49d2-54d6-89d3-bf30c8214e2d | note | SCP
d1d4caef-8eb9-5a1f-a947-1be67b7498a4 | note | Responsibility - Project Engineer
0901d4b2-d248-5567-9637-773d8239ebee | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c3c0d97b-0908-5237-a1f1-72513f227cb3 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
05edde7a-f08f-5c70-b88f-1accb1d8d8e4 | textbox | Print Name:
5bdcbcc6-9a38-590f-8004-c7bbf198ca9e | textbox | Position:
31a47a32-f239-5abd-b74e-9127e755a3b1 | date | Work Completed On:
cdce0b6e-8f82-5da0-9dbc-cd8e91518eac | date | Date:
24b923b5-1a36-5875-8feb-802ee8863ecb | checklist | FH-ZU2-QU-ITP028 - AGL MAG Signs - Rev 0 | itp | ITP028 - AGL MAG Signs
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
8ddc60c2-52d6-5ba3-bb5f-c822692ca78e | note | Frequency - Prior to commencing any activity
6df18c19-7c6f-50f9-b677-3f2b959531f8 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
f9da8ea9-89b7-5f0e-b989-84b6a8b80b8e | note | Reference Documents - IFC Drawings
4683521a-f900-5473-98f3-a67b4f6ea1e5 | note | Inspection/Test Method - Verify
674379bd-c284-5e3d-873f-ce09bf739c70 | note | Record of conformity - Drawings
d8eb3e01-fda0-5c31-856a-83c759b25a3e | note | IP
175b6b71-cc52-516e-8e9f-846a379cfcc0 | note | Responsibility - Project Engineer
dfc620fd-985a-53d1-b486-992f4c1d8362 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
260a7c4b-a99c-5a02-adad-d000ceabfd8b | note | Frequency - Prior to commencing any activities
813e3056-3b3e-51c9-8d23-d749416004b0 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
c9605aa4-86a1-52a6-83ce-2ee4605031fa | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
b313f28e-2438-582e-ab7c-e25ba2da9340 | note | Inspection/Test Method - Verify
2224f6d5-342a-592e-9d5c-41029967a1a7 | note | Record of conformity - Site and office Inspection
d87775a1-ef24-51a6-a318-1ccc0adeec75 | note | HP*
cf72e15b-9c45-5942-92d3-14461509a1d6 | note | Responsibility - Project Engineer / Site Supervisor
0b8b7bbc-9c92-59c0-8160-fb26bad4aa5b | date | Date Completed:
6950b5cb-7d87-5252-8927-66c6362f45bc | checkpoint | 1.3 - Material/Equipment Approvals
48893bdb-4389-5907-9976-dd6ddf0f8c56 | note | Frequency - Prior to start
34c061f0-7aee-5109-a88b-625ab5d38f62 | note | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
5fe73daf-9af6-5110-a145-b770a0022e1e | note | ○ MAGS shall be from ATG Airfield guidance signs range.
a6532fa3-d5e3-5a41-b2ab-395352d6acc5 | note | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
13379fa6-158f-5a66-95b5-84d65aff3b24 | note | Reference Documents - ZULU- BECA-001- SPC-00003 cl 2.3
cb7f38e8-7634-5cc9-9ed5-70723d66218a | note | Inspection/Test Method - Verify
e44fdd8a-7997-5917-bd17-07bd45a39200 | note | Record of conformity - Aconex reference(s)
919a5e4d-2e49-546d-8fa5-373dcb126d7d | note | HP*
d445324b-b5cb-5add-a93b-5fb130ce1c55 | note | Responsibility - Project Engineer
bd170232-4df1-5bea-aee7-01b489ce921c | date | Date Completed:
9eb64960-a579-5c04-a038-8713272d9ee7 | section | 2.0 - Installation of MAG Sign Footing
7242a731-b698-5c5a-a5d7-fa8ee5d5f578 | checkpoint | 2.1 - MAG Sign Base
b5e75d4b-ba5e-512f-b305-af4a72153d70 | note | Frequency - Each lot
54b5f099-4b4e-5e08-8742-199530135d52 | note | Acceptance Criteria - Position of rectangular base to be as per set out coordinated listed in MAG schedule.
68a3f16a-00de-5635-ac38-c10fc7eb2b48 | note | ○ 150mm thick class 2 crushed rock base layer compacted to 98% STD on prepared subgrade.
efcf5c26-7fbd-57b8-b37e-3b3bbed3a269 | note | ○ Subgrade Bearing strength of 130kPA confirmed by a qualified geotechnical engineer on behalf of the contractor before placing membrane, reinforcement or concrete.
26c34011-20fb-5b2b-9342-d03d93dab5ec | note | ○ 50mm blinding concrete between subgrade and foundation.
1361518f-7030-5a8b-a82c-5bf3e706f9a8 | note | ○ Slab thickness to be 300mm for all H<900mm signs, min. 32 MPa concrete.
28cefa2c-b332-5be7-8348-f7c0639fcf1a | note | ○ Footing to be placed flush with FSL when placed in pavement surfaced areas.
d3bc008f-5ac3-5001-965d-721918b27030 | note | ○ N12-200 top and bottom reinforcing bars with minimum 50mm cover from edge of concrete.
0e9e1085-36c9-552e-a6f2-0803bba1b4aa | note | ○ Sign mounting brackets and frangible coupling as per manufacturers guidelines
99b4b9d2-8f6f-5b2c-bbe0-ca5e4ef81b1a | note | Reference Documents - ZULU-BECA-023-DWG-07502
2c46142e-8c92-580a-b15c-8143787bd00b | note | Inspection/Test Method - Visual Inspection
fa5695c3-bc1c-5393-a2dd-5c2d327be5c6 | note | Record of conformity - This ITP signed, DCP test result, Concrete test certificate, Avionics Installation of New MAG Slab and Sign checklist
fbd2220d-bd86-5e38-a782-43c2d0712fe1 | note | IP
17c8bcb1-6358-5a68-826b-72b35e9e546e | note | Responsibility - Project Engineer
1661ae28-e9c6-53cb-88e0-dcd5b3024934 | date | Date Completed:
bc20e016-f324-5514-b18a-ef482ef032e2 | section | 3.0 - Installation of MAG Sign
daf0a513-a1d3-5af9-aea4-370e647fd5d5 | checkpoint | 3.1 - Luminaire Circuit
649045eb-7b83-5714-8fcd-5679b6a48f55 | note | Frequency - Each lot
35f7888b-a995-585d-ba71-3d5588cae03a | note | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
c4f8306d-842a-546b-83a0-de6e924ee263 | note | Reference Documents - ZULU-BECA-024-DWG-09001-16
4736f50d-ba8b-5e52-8973-cfffbf02d65d | note | Inspection/Test Method - Verify
b74f2399-6413-5405-8088-8793ec0d8281 | note | Record of conformity - This ITP signed, As-Built Documentation
f7953965-0b65-517b-aa70-b79462b51b48 | note | IP
3b31a614-8e8a-556a-b653-a0225400d8e5 | note | Responsibility - Project Engineer
0b78267f-d355-55de-877f-46da63527d4b | date | Date Completed:
c7451fec-d8cc-5895-b0d6-abb96dbfa9ff | checkpoint | 3.2 - MAG Sign Face
e271b798-8392-52fa-bbc9-fcc5c50d9445 | note | Frequency - Each lot
65e89ebe-45e9-5dfe-9fb5-16068bb9c2a4 | note | Acceptance Criteria - All MAGS that are to be mounted on frangible couplings. The provision of internal illumination of the MAGS shall be as detailed on the Drawings.
2418b2c0-d908-590e-a501-656146b5875f | note | ○ Bird spikes provided with MAGS Chain tether installed on side further from taxiway and installed as per manufacturer’s recommendations
aae51f8e-af26-5831-b4e5-ee1b4d57ac58 | note | ○ Where multiple panels are required, the inscription shall appear continuous over any joint and shall only include a bar if the bar is part of the inscription.
9d39b429-0499-5f89-8c13-88ff7fa8ee14 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 4.7.1
ddb0b542-b302-5082-8da0-213b3846b37f | note | Inspection/Test Method - Verify
bc671c39-5ef8-5b06-bc94-7c327ca06502 | note | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
807e5a06-a1dc-5e4c-8900-cab92739b26f | note | IP
f1ab977d-08e0-5a56-bc90-8394e3858bd3 | note | Responsibility - Project Engineer
41095d3a-5d75-5593-927e-01d84d3868f8 | date | Date Completed:
d0dd6e34-86d2-5297-913f-37b8b638172d | section | 4.0 - Post Construction
fc9c9030-8e63-5899-b7a4-3ce432cd125e | checkpoint | 4.1 - As-Built
d2db8983-8962-5251-8907-3a1af8d4868b | note | Frequency - Each lot
d40e1033-e6a3-5a67-ba70-c917adff63e0 | note | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
13b6ec89-5610-5d0c-bab6-59a273075fdd | note | Reference Documents - WP-001-09
887bebae-c0ad-58b6-85b9-cd2ff8c8f678 | note | Inspection/Test Method - Verify
61623fca-ce75-5d91-8d5d-d6ab18564d4d | note | Record of conformity - SCP
a5c81aff-54c0-5186-b766-f50c3760b787 | note | IP
f9903796-9cf8-5ea2-b162-9e3f120f9827 | note | Responsibility - Project Engineer
bb1d6c76-c8ea-5a38-b46f-92638b522829 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c44b9953-a27c-53c7-86a8-3482ecbc51a0 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
dadff64c-aa37-5bda-834d-acbbc2fccf63 | textbox | Print Name:
b3256f93-fe30-5261-ba15-c2ca5080105d | textbox | Position:
22333328-1ec8-5b1f-b442-2c4df6d45cbc | date | Work Completed On:
915032fe-efc9-5633-8c63-2d8aa5994c45 | date | Date:
6006b4cb-b0a6-5fca-873e-b21b8b4167c0 | checklist | FH-ZU2-QU-ITP029 - Topsoil and Grassing - Rev 0 | itp | ITP029 - Topsoil and Grassing
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3b455b0c-df8a-5f1c-a79d-c52ea7a6a8ab | note | Frequency - Prior to commencing any activity
29a5a0fb-8c5f-5829-97c4-410a0803f5db | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
5eda98ec-8fb0-5741-a8e1-c7c40ccd2dad | note | Reference Documents - Drawings and Aconex
195bdef3-62b1-5bf1-beda-08a907688282 | note | Inspection/Test Method - Verify
4b5a655d-77ec-5c91-bd29-6a80e9931a2d | note | Record of conformity - This ITP signed
3ccce2ad-1d19-5b28-b3b3-7dee77eb89fc | note | HP*
25e4db16-7785-59d5-87e6-cc0420ae4731 | note | Responsibility - Project Engineer, Site Engineer
a93086e7-5190-5256-8d5d-1717712b6210 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
e6b2b67c-e0e8-5f5f-a2f9-e1a3c81010e5 | note | Frequency - Prior to commencing any activity
dc31e77f-30f1-5b15-aff1-6c4d965a4c8b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
4c3546f3-020b-55b8-a279-10f8c0c10cc9 | note | Reference Documents - PSP, EMP, TMP, SWMS, WP
6724336f-d1f3-53d4-aeed-2b90dd156027 | note | Inspection/Test Method - Inspect
84f6f406-6ed0-5476-a871-03a19d856734 | note | Record of conformity - This ITP signed
b3972c52-fb7e-5b81-a56f-df6f0f80d788 | note | HP*
dbfa3b13-0391-5e7d-8b30-4ee248da766c | note | Responsibility - Project Engineer, Site Engineer
73e35de8-dacb-575e-91ee-4937df969a01 | date | Date Completed:
7eb2974f-59a3-5b8d-a6e0-aa0c675c7b2b | checkpoint | 1.3 - Material Approval
e69a4fd6-eb2b-5c83-946d-b8c141f28e0c | note | Frequency - Prior to hydro seeding
76f70115-2ab2-5dff-970d-59a9e457cb7e | note | Acceptance Criteria - Hydro mulch supplier are either to be Flexterra HP-FGM, Vital Bon, or Hydro Mulch 1000 unless agreed otherwise by Melbourne Airport.
47ba3291-edb8-59a2-9c2c-c0f1fe8ce22a | note | Reference Documents - Grassing Spec cl. 7.2
ddb7657a-4539-5c8f-92f7-f61cd4c30d23 | note | Inspection/Test Method - Verify
f319968e-522a-583f-ad61-408af2693a4f | note | Record of conformity - ACONEX, This ITP signed
774542f1-492c-5de9-a65b-e4b5e53c1d23 | note | HP
6fe8fdbf-d96f-54de-ae62-65012f523451 | note | Responsibility - Project Engineer, Site Engineer
895a271b-e90f-59de-89e8-ef64c690a0b0 | date | Date Completed:
19d86115-8851-5070-b2a5-57661884286d | signoff | AUTHORITY HOLDPOINT
b50dde49-0719-5a28-aac3-589ad521f851 | section | 2.0 - Herbicide
10ee340d-ecf7-5aad-bf29-b25b09c9c16a | checkpoint | 2.1 - Topsoil Material
121fea79-5a6f-5520-9736-6f5ecc0f1b3a | note | Frequency - Prior to topsoil placement
68d37ac7-884c-5db6-ba8f-2254cd6f50d3 | note | Acceptance Criteria - Topsoil material is to be virgin topsoil free from clay lumps larger than 50mm in diameter, contaminants, pest, weeds, stones, subsoil, tree, and shrub roots.
c2738e77-b8fb-53e9-b554-5b1c71779944 | note | Reference Documents - Grassing Spec cl. 7.4
4ed17697-54e6-5fe8-a4a4-44103ffea086 | note | Inspection/Test Method - Visual Inspecti on
afd1e987-a2a8-5c61-8c03-378ed2ada6fd | note | Record of conformity - This ITP signed
4735cb8a-826f-5729-91d1-f9a4f753861c | note | HP*
3f8a9cbc-78f6-5230-a3bd-1458d3bd77c6 | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Advisor
97fcac60-3ba7-5750-87ae-af29d5c984f5 | date | Date Completed:
1dfea3b9-d16a-5f2e-a8be-72e3a8adb60a | section | 3.0 - Placement of top soil
fdd73569-43c3-5ac6-9387-4ec01cfd9142 | checkpoint | 3.1 - Topsoil placement
332dff45-1f69-58a7-bc82-5d383410af29 | note | Frequency - Each Lot
0182e849-7f3c-5fde-9854-a88538c8193b | note | Acceptance Criteria - APAM engineering standard (MAS- CVL-001-V1-1-Grassing-Standard – Dec 2022) calls for a uniform thickness of not less than 100mm of topsoil prior to seeding and subject to the Contractor making necessary allowance for compaction of the topsoil prior to Hydro mulching.
4f2616c8-7420-56b4-8c1f-ccb232e64981 | note | Reference Documents - Grassing Spec cl. 5.2
c87334f3-efe4-5932-8782-061264e8c10a | note | Inspection/Test Method - Verify
102ee9d9-bb4f-57ff-b3b3-dcb3e3b24887 | note | Record of conformity - Survey data
be0ec143-e6cb-5e9a-b00f-9ff7baafa4d8 | note | HP*
18308c07-7d0a-51e5-9d23-2b94196ce4a7 | note | Responsibility - Project Engineer, Site Engineer, Foreman
b30a613c-9fa5-56b3-a547-31bfd246ee0f | date | Date Completed:
8401add0-f8c6-5126-85ad-957bd9c9d47e | section | 4.0 - Hydro seeding
522eab20-d28d-56ce-a99f-6f8fe47a5d5a | checkpoint | 4.1 - Grass Seeds
a62c0590-1756-53d9-ae85-4fd1f451ba31 | note | Frequency - Each Lot
ab8fbaa1-3def-5c8a-9785-23cc7789537b | note | Acceptance Criteria - Grass seed to be used during hydroseeding is to be the following:
b9157f92-2f32-5304-861e-c35d5cf27906 | note | ○ 50% Common Couch & 50% Colosseum Ryegrass during the warmer seasons (October to March)
8156911c-89b2-56af-ab66-c62045259e17 | note | ○ 100% Ryegrass during cooler seasons (April to September)
8194b431-f749-51c3-ad13-95ae4720fc93 | note | – Use of other grass seeds to be approved by Environment and Sustainability Manager.
2fe5a693-3a69-54ec-a9e9-bd8ed78cc0d7 | note | Reference Documents - Grassing Spec cl. 7.1
ab2487d0-5ba7-5eab-88b0-3d3f44a07e3d | note | Inspection/Test Method - Verify
7de79e55-493a-5453-beed-82c3888744eb | note | Record of conformity - Aconex material submission
5e722056-6c3d-5120-b734-29e4054fda1d | note | HP
e28aed0d-e6a2-59d0-b171-68a6ce0ed6ab | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Advisor
ffb78f2c-484c-55cd-8e72-82650909293e | date | Date Completed:
7059c742-95e2-5e4e-9420-0139ba15f2e4 | signoff | AUTHORITY HOLDPOINT
1bd80803-d9e9-5db0-a5cd-014ba6cfa644 | checkpoint | 4.2 - Coverage / Tolerances
d50c7e95-efad-5cc6-910a-e17952611883 | note | Frequency - Each Lot
11ed75f1-485a-507c-b69f-973d461d6a27 | note | Acceptance Criteria - A minimum of 95% healthy cover it to be achieved. 95% grass coverage will not take into account any growing weeds as part of the cover.
713141ba-d806-5c54-b6e1-6c607774aca7 | note | Reference Documents - Grassing Spec cl. 5.6
e0b141db-bab3-5044-bb3c-2d2b7977aaeb | note | Inspection/Test Method - Visual Inspecti on
24855dfb-da22-5ee7-bca7-934d64c0d7a0 | note | Record of conformity - This signed ITP
612abc13-5422-58a3-aa38-2b87270048ba | note | HP*
850f33a0-9d7f-57aa-b254-5a41e55ef2d3 | note | Responsibility - Project Engineer, Site Engineer
4c2eca47-c97f-522c-907e-2369fffa30c5 | date | Date Completed:
65a8a184-fa65-5663-8723-e9738e5bb431 | checkpoint | 4.3 - Stabilisation Treatment
5d2b062d-d5cd-5f57-bce5-82f643e4acf2 | note | Frequency - Prior to opening area to airport traffic
d438457d-ea2c-5c11-97ea-f263705e337b | note | Acceptance Criteria - Use of Vital Bon-Matt Stonewall, or equivalent, is to be prioritised instead of the use of bitumen emulsion in areas prone to jet blast following topsoil and seeding. FH will use bitumen emulsion if directed by APAM Operations.
b3f56920-bc7c-595f-b9f3-cdbb81213829 | note | ○ Use of alternative stabiliser to be used for the works is subject to approval by Environment and Sustainability Manager.
1ff87080-2032-5cb1-a5c2-08b1a814197f | note | Reference Documents - Grassing Spec cl. 4.9
6726ede9-0d8f-5224-8833-51abc2a3663e | note | Inspection/Test Method - Verify
e38b7577-8613-555b-8e6b-623d7b0fed74 | note | Record of conformity - This signed ITP
add1b41e-bf73-5cea-8b88-e85a5a088f19 | note | HP*
e8125edf-99fe-58a8-ac07-4bced42ad9f4 | note | Responsibility - Project Engineer, Site Engineer, Enviro & Sustainability Manager
1f7ab866-31ba-5af1-bddc-cbbaec7d8825 | date | Date Completed:
d4b3c58c-425e-5d48-8e64-d4a361d36b8e | checkpoint | 4.4 - Hydro seeding
e63160d6-a6ab-5e9f-83c5-e8fc11c7e451 | note | Frequency - Each lot
ef2f4f6d-29be-5685-9cbc-502309f650cc | note | Acceptance Criteria - Application rates shall be more than six tonnes/ha flexterra or alternative (vital bon / hydro mulch 1000) unless agreed otherwise.
8d7990e9-0478-505a-a5e4-8e2bcbceac4e | note | Reference Documents - Grassing Spec cl. 5.5
0dc89bc2-906d-5b9a-8697-4a2ef9ee1c74 | note | Inspection/Test Method - Visual inspecti on
1ee2b8d2-a991-5301-b613-1e2cd9287d74 | note | Record of conformity - This signed ITP
1ea3ef8f-bbf3-54b8-aaae-853c50c9ac3a | note | HP*
c148f76b-5bd7-5aba-84cb-a3a2755c676b | note | Responsibility - Project Engineer, Site Engineer, Foreman
4cff54af-709f-51da-8da6-10a9d99aa1d3 | date | Date Completed:
9e7d1168-4b28-5f78-bd22-f2a3ef41bd04 | checkpoint | Reinstatement of Disturbed Surfaces
44776fcc-d25e-5d37-a936-9c9634567373 | note | Frequency - As Required
85f4fbd6-d095-5d42-995f-7a751b5ff116 | note | Acceptance Criteria - Hydro mulched areas are not to be trafficked for 3 months or until grass has been established.
3898c38d-53f4-5ea1-9b61-98e2a492c9ba | note | Reference Documents - Grassing Spec cl. 5.5
29f39ab4-605c-5081-9e0d-88ee910f6fe3 | note | Inspection/Test Method - Visual inspection
4c19778d-19d1-50fe-8735-ce062c0811ea | note | Record of conformity - This signed ITP
def3e65b-0887-51cb-a2b1-73b176057165 | note | HP*
560c63db-1426-52d4-82c7-6f350cb5a7d6 | note | Responsibility - Site Engineer, Foreman
4631bfec-a164-59e4-aa7e-e4147cc7a84d | date | Date Completed:
3e68cc9c-da03-5c12-a911-0dcb053881a0 | section | 5.0 - Post Construction
c6cdc8e3-eecd-54bb-b50d-c535e7bdab5b | checkpoint | 5.1 - Reinstatement of Disturbed Surfaces
02f8159d-348b-5556-809b-b39c7131cd7c | note | Frequency - As Required
a62a8e47-63c1-538d-bff8-756ef9d0d9e3 | note | Acceptance Criteria - Disturbed surfaces are to be reinstated to their original condition. In areas prone to jet blast, the topsoil surface should be sprayed with bitumen emulsion, Vital Bon-Matt Stonewall, or equivalent, following seeding if grass strike has not been achieved prior to opening the area to aircraft traffic.
1703378e-f25f-552c-bca3-85e58d5b900e | note | Reference Documents - Grassing Spec cl. 4.13
30eb13d0-5cd3-58bc-82c1-05d4a8f892f2 | note | Inspection/Test Method - Inspection Point
e063f192-ac41-5209-9b71-6da2e67c3dd6 | note | Record of conformity - This signed ITP
191b7b79-b18d-5ab6-b43a-84d36a3b8f99 | note | IP
dc9c7e00-6ea9-5017-a9f8-956e1642bc72 | note | Responsibility - Project Engineer, Site Engineer
1ec2c84b-c1b6-56d7-917e-7615d8ee093c | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
2420c0c4-f05f-565b-9c33-0f000dc15e8d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
765bf4a2-cae1-5a9e-874b-770434bb0e32 | textbox | Print Name:
51ad3199-cbb8-55c8-90f6-ada6168f2c26 | textbox | Position:
1c53a362-da89-5590-8a58-2c8453cb7311 | date | Work Completed On:
c62ac221-9d9a-52d2-93b2-3ac632e66716 | date | Date:
d8fe27e8-cb1d-4b8d-bc8b-16f64532cfd8 | checklist | FH-ZU2-QU-ITP030 - ALER 3 Groundworks - Rev 0 | itp | ITP030 - ALER 3 Groundworks
b6468ec3-8d28-4866-a8b9-1846dabd52f2 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
66c85a2f-f057-4eda-9b4a-0eb363d6ba82 | checkpoint | 1.1 - Check for correct documentation
4fd13d14-090b-5076-ac1f-ecc61124a60c | note | Frequency - Prior to commencing activity
66ee8ce2-d804-583e-84be-8dd6493254f0 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
33969afe-b5cf-52a8-a8ee-c7305ceb1024 | note | – using the correct and complete set of drawings.
4ad42863-9d5f-558c-8cae-922d6c8dce5d | note | – all drawings are the latest revision.
e06cdbc1-70db-5fff-bd97-3eac98c3fea7 | note | Reference Documents - Drawings / Aconex Register
32b2e300-4a2a-5a41-88c4-c83393942f68 | note | Inspection/Test Method - Verify
9f34f180-b0c1-59e6-b72b-bcbc3addfcbf | note | Record of conformity - Drawings and drawing registers
605bea02-42f2-51f5-bc5a-abc010f8b98f | note | HP*
5931ba92-403e-598f-95ed-74351fb48958 | note | Responsibility - Project Engineer
83b8fee5-2ecf-56a0-9e37-1c4a08fb5fdb | date | Date Completed:
6d968585-c3bb-4939-9757-7e877650b3c5 | checkpoint | 1.2 - Implementation of all measures and controls
bc21d9bf-a06e-5d0b-80d8-09383f0b14c3 | note | Frequency - Prior to commencing activity
66e6b91e-5004-5583-8d6e-4bd4b6ed912f | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
73a67ea2-d588-5579-802a-a126654f83ee | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
beb68b6a-7030-5486-ab53-1ad3d4863dde | note | Inspection/Test Method - Visual inspection
e92999bb-8a27-5b7f-906c-be877169e219 | note | Record of conformity - This ITP signed
ee57f482-9fc5-5460-b260-c1029f2723b6 | note | HP*
4b6d6c39-7a60-5db2-bf6e-f44477c81d88 | note | Responsibility - Project Engineer
7565f229-73f0-5739-88af-b61738bf7aa4 | date | Date Completed:
d2f7d06a-c661-4d8a-8167-ece6323dbfc7 | checkpoint | 1.3 - Definition of the work area (survey)
ca4fd58a-4d48-5325-9f6f-fb32632d747e | note | Frequency - Prior to commencing activity
3f2ebf23-beae-5655-9f48-87e05b8921bd | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
534cadbf-0d90-5378-9662-c73301a8c5d7 | note | ○ Pits & trenches all marked out prior to excavation commencing
be75a025-544d-549a-b98f-c36e554c854f | note | Reference Documents - Drawings
bbe7f2ef-81de-5c14-b811-0acb91b61238 | note | Inspection/Test Method - Visual inspection
c5a3c469-7c65-5bfb-ae5d-03f6817cbf18 | note | Record of conformity - This ITP signed
d24585e5-489f-5ade-ae17-37a251d4abbb | note | HP*
01848afa-0402-5502-ac45-d78d1275fd6d | note | Responsibility - Project Engineer / Surveyor
3a62ee66-cf07-5408-84f8-a018dd89cf80 | date | Date Completed:
1e131eaa-7821-4f44-b73d-ceac8fa3c7c8 | checkpoint | 1.4 - Material submissions and pipe compliance
e529b769-9685-5c50-8c29-6405989279a0 | note | Frequency - Prior to commencing activity
8b4b40d9-8edb-5396-8656-62adcadc7912 | note | Acceptance Criteria - Material submission of:
92a93712-2d9a-5ed4-9941-c60fb9650c44 | note | ○ Electrical
ef6323ae-3e8e-579d-8f5d-065889712ef7 | note | – Ensure uPVC conduits comply with AS 1477 or equivalent AS 2053
f15b70b8-e314-5c4e-9e18-cb1872fa617e | note | – Shall be heavy duty, orange for electrical services and white for communication services
6c996737-cf7e-5127-8d68-3b4ca2a136ca | note | – Ensure pipe diameter is correct AS per drawings
22ad7d40-ef26-584c-9bc7-aab1cb4149e8 | note | ○ Stormwater/Sanitary Drainage – Below Ground
ab4d9dbb-7d98-572a-97b0-958e5191b1d8 | note | – uPVC Non Pressure Pipes shall be DWV MIN SN8 Solvent Welded to AS 1462 with an environmental product
c9c95f8e-d928-51fd-bbcc-14471f906789 | note | – uPVC pipe Shall be SN10 SWJ AS per DCWC Mgt-RTRFI-1317
c76a3bbf-224c-5cbb-92e7-75836ca79517 | note | ○ Cold Water – Below Ground
8f32d90e-0051-5f46-9a76-48e1eb34dd22 | note | – Polyethylene pipe shall be used conforming to AS 4130 & 4131
8551ae16-112a-55e7-b304-85939201e469 | note | Reference Documents - Drawings
c38a792d-9147-5e17-ac5d-0740859d1644 | note | ○ ZULU-BECA-001-SPC-00004 Cl. 3.4
23c569e8-f561-573f-9368-032ac9d6a1ac | note | ○ ZULU-BECA-001-SPC-00005
153a5404-1c21-54d5-9fa1-0a15003e1d50 | note | ○ Table C1710-A, AS1477, AS 2053, AS 1462, AS 4401, AS 3500.3, AS 4130, AS 4131
2dedd07d-f11e-525c-b5f5-22c5b7826aaf | note | Inspection/Test Method - Verify
02e62425-76fd-512c-9cfa-0c871530b9ac | note | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
10250a77-29f9-50d0-8322-7acb541d92df | note | HP
a02efb04-7c6a-5b89-9981-80b5658cffc1 | note | Responsibility - Project Engineer / Principal’s Representative
945b580f-83a9-5739-b42d-09c405369bba | date | Date Completed:
41e9f41d-fe99-477f-80c6-d0a927e00b72 | signoff | AUTHORITY HOLDPOINT
77ae5afc-71c3-4b95-840b-0e97bf4b69d4 | checkpoint | 1.5 - Check bedding material compliance
2c571580-0f5d-5a8f-b4e8-49866a0b9bb3 | note | Frequency - Prior to commencing activity
f2262bcb-e41e-5008-b7d8-91e3658d9bda | note | Acceptance Criteria - HOLD POINT
6a39db73-051a-53bc-abf4-f6c274bb9f1b | note | ○ Electrical
34ad3722-4931-58ba-9480-fc3876ec1abe | note | – Ensure that the conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification
259fad47-231b-57df-9caa-46eb71e9827d | note | ○ Stormwater/Sanitary Drainage/Water
296ba5dc-3d60-59ce-b7d2-3c3bea4e5de5 | note | – Ensure Bedding Material is Well Graded
849716ba-8e45-54ad-8e91-e6cd6abaf3f4 | note | – Manufactured Sand to VicRoads Specification 407 Clause 407.03(f).
433a39d8-b085-5306-9e51-bdb2a1d3821f | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.3.3
c0117bee-0129-592b-bd1d-90f917b2e783 | note | ○ ZULU-BECA-030-DWG-00201 Note D03
b7bc1ac2-7338-5914-a0cc-fee7b0f26726 | note | Inspection/Test Method - Verify
d2f4e54d-854b-5ed4-a373-74e87b28e66a | note | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
eb768e6a-d13d-5fe6-9fc9-d4d6e9d2ab5f | note | HP
a1e47a2b-45ff-5d53-9bfe-e83a2cb544da | note | Responsibility - Project Engineer / Principal’s Representative
d2eb2153-bf94-5670-ab74-55f405b308be | date | Date Completed:
3ed30c02-9996-4b05-aef0-30472fa95cbb | signoff | AUTHORITY HOLDPOINT
b17c037c-22de-44f9-9f8b-1aa2be406fb5 | checkpoint | 1.6 - Material Submissions and Shop Drawings
6ca2d775-fb67-57c2-bcb7-f169e726aaa8 | note | Frequency - Prior to commencing activity
bb11dd27-cb59-57db-8985-3505ca7fd6f7 | note | Acceptance Criteria - Submission of:
bda42b8b-f270-5fb6-870e-2209767d7653 | note | – Spel Puraceptor for approval prior to commencing works.
dc6f1b00-7d1a-50d5-93c9-cb0ee83cb16d | note | – Septic Tank & Sewer Disposal Unit Design
368ce014-ff40-5866-9474-f27b325bd217 | note | – Pre-cast Pits for approval prior to commencing works
6c26b4e5-074a-5dd7-aaaa-a7d6ff28fadd | note | – Precast headwalls
06d207ee-435f-5bda-bed3-41c35734acab | note | Reference Documents - ZULU-BECA-001-SPC-00005
f37e4e7b-5cf8-5f88-b3df-a2e1dcce8efb | note | ○ Drawings C1700 cl. 3a AS 1546.1-2008.2
e1aac23b-37b0-5101-bf9b-b4918f5ef176 | note | Inspection/Test Method - Verify
be4b2ca1-0aa6-5531-ba66-f2e92ad429b1 | note | Record of conformity - Aconex Reference, Building Engineering ITC
8e7206b0-e55c-5177-bfd5-53b1f170d305 | note | HP
d46655db-4d3e-5cc9-b699-6fb5d487464f | note | Responsibility - Project Engineer / Principal’s Representative
e0259936-f34a-5afd-b1af-75e3c44dd954 | date | Date Completed:
a930f738-bf4e-4e0a-bf81-4d91a24ea9f4 | signoff | AUTHORITY HOLDPOINT
9db186c0-1e25-48d1-8fb8-8434e932368b | checkpoint | 1.7 - Permits & relevant approvals obtained
385c4c59-a517-5a27-9a60-718de9816a2e | note | Frequency - Prior to commencing activity
6606e056-2df4-5056-971d-e35c19b3d09a | note | Acceptance Criteria - Excavation Permit
b30fc166-7862-5d4a-8c74-443951a866f9 | note | – Location of services to be found and marked on the ground within the works;
ee709bc7-42da-5680-9978-e24c553b5be6 | note | – Contractor to obtain excavation permit from APAM prior to any demolition works.
00cafb75-1109-52aa-9d25-8b5e31c179fd | note | – Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
50ba3d0f-dfd0-56d5-a9f7-9d88e6065bcf | note | ○ Service conduits shall be protected from damage due to subsequent construction operations as required using whatever measures are necessary. Any damaged conduits shall be removed and replaced at no cost to the Principal.
bb5e8056-c0d8-54de-81df-155dfdd2d480 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.15
eea5bde8-2ac7-5f81-b624-f68a093dc1b2 | note | ○ WMS-002
07024245-5c42-568d-9ec8-31b0dc64cb51 | note | Inspection/Test Method - Verify
ce2806fb-d9c5-5bca-b0ab-a21f6afa8c73 | note | Record of conformity - Melbourne Airport Excavation Permit, PIC
0011384e-cd88-50ab-95f9-5bcd6b3eb54b | note | HP*
5c25b1c1-d7b2-5b77-8725-fba76adcdb6b | note | Responsibility - Project Engineer / Surveyor
768dd82a-4187-59a4-8f64-a4c8a7e1e8ee | date | Date Completed:
e34e05f3-7263-493d-9287-26943a6513d4 | checkpoint | 1.8 - Native Grass Protection
6d9ea899-ed7d-5cd4-bdd1-864c2e77ee73 | note | Frequency - Prior to commencing activity
04d0e116-764c-5b6c-8452-a09259c4c8bd | note | Acceptance Criteria - Native grass protection installed. As per native grass model
acc04b65-cd9c-5d84-b51c-fe2f73953b09 | note | Reference Documents - Relevant Native Grass Permit
a592f9e2-dfd2-5d8c-9ffa-b4f17f734b63 | note | Inspection/Test Method - Visual Inspection
c1328a0a-e5bd-5710-9fb6-5b5f010fc21a | note | Record of conformity - FH-ZU2-QU-ITP038, This ITP Signed
709d56e4-413c-5228-8c5a-b937bbfb83d6 | note | IP
4a688fb7-6a49-5746-af79-91da6cc34551 | note | Responsibility - Project Engineer
9adecd8f-fe56-5561-8d00-8b3788fb5564 | date | Date Completed:
28bcf6d2-69df-4511-a469-d9c1a5b98b10 | section | 2.0 - Construction - Stormwater
a5c7ba1b-e6a0-4407-b5dc-7428727f9261 | checkpoint | 2.1 - Excavate trenches for pipes
a297126c-6462-516c-8d87-7287b313d33c | note | Frequency - Each lot
7db50315-8217-555e-8791-602e869eccce | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
24995865-d116-546e-a2aa-be5d0ce60668 | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
fcdb807a-9818-5b8d-8180-fc77e1670a7f | note | Reference Documents - Drawings AS 1289
5b177ddc-f874-5248-817e-acd5abdac2c2 | note | Inspection/Test Method - Visual inspection
c77a8d0e-01cf-59dc-bb85-afa2845fee8c | note | Record of conformity - This ITP signed, Building Engineering ITC
1a361107-a5dd-53a6-8c40-43841bcf9d1c | note | IP
e21baca4-f35b-579e-87be-4e71782116de | note | Responsibility - Project Engineer
4091c989-2a94-5de9-b5a1-89dcf36100c1 | date | Date Completed:
ba24ed20-ea59-4f10-bb43-57c72c6a82ae | checkpoint | 2.2 - Existing services crossing new pipes
d92c0b18-c8a9-51f4-9cc9-104ce5aec41f | note | Frequency - Each lot
5010d2ea-2941-5f73-8936-0c9144b300c6 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
31ef19cf-489e-5457-ac19-91d625ee7559 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
b1860150-edd0-5019-b4a6-ea9c3e10de18 | note | Reference Documents - WMS002 – Working Near Existing Services
07149115-db0e-5dde-a8af-8ac1f4fa8611 | note | Inspection/Test Method - Visual inspection
a4b79c8a-70dc-52a9-9d00-198343fc87c0 | note | Record of conformity - As-built survey report
2f65b858-b802-5acf-a039-1c30be8e8abf | note | SCP
b1c281b9-3c27-5f6c-acab-ae3fc138c776 | note | Responsibility - Project Engineer / Surveyor
540963c4-0151-5478-a1c1-1a640ff3e46e | date | Date Completed:
2f2fa42e-8012-4b84-80f9-fc2a588b17d9 | checkpoint | 2.3 - Laying and jointing of pipes
3b0353e6-89ad-5bf0-b4b1-1cec099ce7e3 | note | Frequency - Each lot
f0255c12-7a5a-5e67-8d56-a3645a707622 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
ad4fe8e0-f82d-5216-89d5-d496c1d4acce | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
89e13217-42bd-5237-8be4-3a16a6cc516b | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
e5184946-c419-5c79-b0b7-62a7ab146937 | note | – Lay at MIN grade 1:100 UNO.
f42c536d-ef8d-5b10-829a-1db2e7ad839b | note | Reference Documents - Drawings
35977add-9a8f-5b43-9ad9-2dd7d75cfc94 | note | Inspection/Test Method - Visual inspection
d729777c-7f25-5e60-ae61-df9d25306255 | note | Record of conformity - This ITP signed, Building Engineering ITC
edbb05b8-8f4f-5580-b736-8ec15e831b31 | note | IP
7a8a5c57-c27a-5e5e-8399-956edfea2f97 | note | Responsibility - Project Engineer / Foreman
b28533cb-a986-5b6d-8faa-a94b736f8ffe | date | Date Completed:
54d6deab-1aae-420f-a0b3-2bb039f7f191 | checkpoint | 2.4 - Pre-backfill inspection & testing
ad1b93f8-7ea8-501d-a5b0-42815fdcde5c | note | Frequency - Prior to backfilling each lot
1903e199-f368-57da-8f31-8db52d06993c | note | Acceptance Criteria - HOLD POINT
9b76851f-2c9a-55fb-8014-57d4ca17b863 | note | ○ Backfilling of the trenches shall not proceed until the pipeline has been tested and inspected.
89294627-ab01-5f5c-874b-79572ceca63f | note | ○ Check for leaks to the requirement of clause 15.2 of AS3500.2
6c63ecce-3b32-5e88-a30d-41899cdd1080 | note | – Inspect for proper laying and jointing
d19b5c23-9882-5e22-9c88-da8f70ed4f76 | note | – Pipeline has continuity in fall
14e783ec-8e44-5f96-a6e8-cf2c755a317d | note | – Expansion/swivel joints provided for all pipework
c5a05143-f7e7-51fc-98df-c8861ca721a1 | note | – Testing as per AS 3500.3 to be carried out
d5f7a963-39f7-59c6-8106-814a35e720f7 | note | • Water Test
69c2e0de-4baa-5f33-824c-907f16fd0a4a | note | • Air Test
8c84844e-a097-5fdd-bdef-991963b4c684 | note | – Building Engineering to run camera through Stormwater pipeas and upload link
78f6ae3b-bc4f-540d-bb9a-1ff53c99e4e3 | note | Reference Documents - Drawings
2fe3129e-3876-5549-a904-e683046269e9 | note | ○ ZULU-BECA-001-SPC-00005 C1700.8 2c, C1700.2 .2a, AS 3500.2
ce1e34ef-a18a-58d6-8558-132cbed74279 | note | ○ Building Engineering ITC
f8892474-3e96-5e03-afe0-3170054665db | note | Inspection/Test Method - Visual Inspection, Test Result
2cbbe4f6-e42f-5895-b531-345782795ee5 | note | Record of conformity - This ITP signed, Building Engineering ITC
b2e1a587-00d7-5534-8e67-cf88d8f6990d | note | HP/TP
3a9104e5-e23f-58ff-9700-48323346cfab | note | Responsibility - Project Engineer / Principal’s Representative
4ba30ac0-ef6a-52ae-874f-49ce1ca8494f | date | Date Completed:
446d6d2f-6184-4352-b1d7-a072096bb9b3 | signoff | AUTHORITY HOLDPOINT
45bea17c-342b-4836-acc0-0cc82a6026e1 | section | 3.0 - Construction – Sanitary Drainage
cf6b6159-2553-4bf4-bd61-1241af222729 | checkpoint | 3.1 - Excavate trenches for pipes
8c7806ff-fcf1-5d77-9651-875b47e91825 | note | Frequency - Each lot
97fa39f0-7a07-5f44-b035-511f15d296fb | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
e9b8f515-43d5-5246-bc25-aec171ba758f | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
db972636-738d-52b8-b1a6-bf8641a54edd | note | Reference Documents - Drawings AS 1289
847355f3-bcfa-5e6f-a113-c73eec5f2aa3 | note | Inspection/Test Method - Visual inspection
6a017eeb-82e2-5aae-9bd9-7d38cfda2bd6 | note | Record of conformity - This ITP signed, Building Engineering ITC
19564aa9-d5b1-5136-972d-42ff0ccf2a0f | note | IP
7c3e7145-ef72-5f1b-a854-72b746008998 | note | Responsibility - Project Engineer
9b87dc8a-9175-5136-8adf-1459fe00fefc | date | Date Completed:
313915e0-3116-4c3e-b2bc-0b4204e3e243 | checkpoint | 3.2 - Existing services crossing new pipes
7d4f33b2-53b8-58b3-97a8-9eb83f209ae7 | note | Frequency - Each lot
3ea30ad9-4d5f-5af0-9d0d-0fd38cfe6639 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
85d0e942-0de6-5e25-8817-9539547a34d9 | note | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
e57e27cb-9734-5ebb-b921-25e5b835fbd0 | note | Reference Documents - WMS002 – Working Near Existing Services
4ab38647-b782-52b2-add4-19b6b7453ee9 | note | Inspection/Test Method - Visual inspection
46a5157e-e298-5bad-81a7-b234ac6f0f00 | note | Record of conformity - As-built survey report, Building Engineering ITC
664e5aff-79f3-5396-aeeb-2e2789b1a0e0 | note | SCP
6c7035c0-0af2-5e7a-abd7-644de0da6c49 | note | Responsibility - Project Engineer / Surveyor
0f307240-1886-5595-9770-30e0b5073b9b | date | Date Completed:
457d19e5-721c-46a2-8416-df9b81c3638e | checkpoint | 3.3 - Laying and jointing of pipes
fdfa6d0f-69c3-5e81-b8c0-2b9a826a1402 | note | Frequency - Each lot
c056fa19-12d9-5bd6-a898-1cb5280b5e98 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
c6b9e4ba-6f7c-5162-a26c-4148f8f7d97d | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
c885d1e8-af72-5704-bff4-effcddba9d85 | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
8d3aa237-1eff-56a0-afa5-d8dbdc11a5f9 | note | – Lay at MIN grade 1:100 UNO.
272f9eda-98a7-51a0-984b-516ac8aae7e6 | note | Reference Documents - Drawings
374bda96-7306-5842-8369-b3aa3947323c | note | Inspection/Test Method - Visual inspection
ebb9770d-e041-55ed-9b97-a182f1d19175 | note | Record of conformity - This ITP signed, Building Engineering ITC
63d35e62-8c40-540a-8965-916d5f7753bd | note | IP
5b1934f1-1960-5aa1-8a50-2693c8aa6852 | note | Responsibility - Project Engineer / Foreman
65e06c3f-5a90-5b4f-bbc0-49eb02567a32 | date | Date Completed:
82509668-c645-4694-bc10-6d7ff2b86c23 | checkpoint | 3.4 - Pre-backfill inspection and Testing
010361f1-9638-5f07-9d43-713dcdeac719 | note | Frequency - Prior to backfilling each lot
a2d1ab62-9c0f-5658-857b-6c32e1719d40 | note | Acceptance Criteria - HOLD POINT
c03b6a47-bba7-5833-a378-6cce1e2c78ee | note | – Pipeline will need to be tested and inspected prior to any backfilling
d4b6f60f-9d91-5174-81dc-fece7fa9d8fa | note | – Inspect for proper laying and jointing
923ce56b-236f-5985-8aa1-78b32583a867 | note | – Pipeline has continuity in fall
4cc55a83-2ec5-54dd-92d1-9b875ffa300a | note | – Expansion/swivel joints provided for all pipework
bbc18ff3-05ac-5d31-a3bd-56b480b90e39 | note | – Use temporary capping to isolate piping to be tested; fill piping with clean water and check for leaks to the requirement of clause 15.2 of AS 3500.2
e1759dc0-771b-5d21-a922-203313d2430a | note | – After testing, drain and reconnect the piping, flush the drains clean with water and check for fall to discharge
f7792468-6687-5f89-a33d-5886aa5dd77b | note | – Building Engineering to run camera through Sanitary pipes and upload link
eb56aebd-8a9a-52c9-84ee-cb01a872c8ed | note | Reference Documents - Building Engineering ITC, ZULU-BECA-001-SPC-00005 C1700.8 .2 C AS 3500.2
44535d90-c902-5a89-8b00-801064c63011 | note | Inspection/Test Method - Visual Inspection, Test Result
5528d656-826d-58bc-9341-51a3a0d0ce69 | note | Record of conformity - This ITP signed Camera Footage, Building Engineering ITC
4b6cfe42-cf01-5160-9d38-6607291d2165 | note | HP/TP
edf4398d-9c58-5167-974e-17d25204f0f6 | note | Responsibility - Project Engineer / Principal’s Representative
07cd460d-a6e7-59f2-9166-98f39b1d92f1 | date | Date Completed:
68c7d6b5-9ccc-492b-8589-b0b880af2c66 | signoff | AUTHORITY HOLDPOINT
3eec507e-58f8-4ddf-95e4-cc94027267d4 | section | 4.0 - Construction – Cold Water Pipes
b4fab121-db22-46d6-8ef8-de9ccaa2c7d8 | checkpoint | 4.1 - Excavate trenches for pipes
a9c67a52-74de-5457-b4ad-d9be3d5f0374 | note | Frequency - Each lot
b34b0b63-7c0f-5ddc-a625-bae9bb8c5d87 | note | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
a529069b-7344-5925-8506-8e95f7dc822f | note | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
2b633649-3547-5002-9792-ee3cc6e09a08 | note | Reference Documents - Drawings AS 1289
9aaf3c8b-9d5d-5615-93e6-f551885e9455 | note | Inspection/Test Method - Visual inspection
2d0925ea-e711-5521-9fa3-1d20b609cffb | note | Record of conformity - This ITP signed, Building Engineering ITC
4b56bee5-4977-5d20-bbed-4db5a5d81f38 | note | IP
6bf0f3ff-1472-5548-8181-a5f664e73ad7 | note | Responsibility - Project Engineer
6c4f094f-cbe9-57d8-9f5a-2605f5f17d4d | date | Date Completed:
f381e59a-5d2d-4824-bb46-ca2a925075d5 | checkpoint | 4.2 - Existing services crossing new pipes
e96cc255-8921-55f3-962c-0c6e6c746f79 | note | Frequency - Each lot
8101c81d-1a1e-5837-8653-5cb80ae036a7 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
408741dc-d324-5476-9603-e1e240c27958 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
8680bcc5-58c3-5d9d-8548-99b15c8b0c60 | note | Reference Documents - WMS002 – Working Near Existing Services
ab3c8806-b6ae-5754-9ab7-d78b4399b4c3 | note | Inspection/Test Method - Visual inspection
e15a76b5-b809-5acd-bed5-db69f2ee4f96 | note | Record of conformity - As-built survey report, Building Engineering ITC
5e710dd0-d88f-5167-8df0-9ca38c6ae3b8 | note | SCP
241ab6e3-b2d7-5601-89de-873898e5b728 | note | Responsibility - Project Engineer / Surveyor
04e2ba2e-696a-5eb2-b60e-8e176421c2a5 | date | Date Completed:
f2224ebf-ef15-497d-8ea8-952316e2b618 | checkpoint | 4.3 - Laying and jointing of pipes
1443e3e3-606e-5d4c-bfe4-e9e27c2a6713 | note | Frequency - Each lot
d7c6b4b0-6619-51cf-b374-40c3308627e0 | note | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
6c7a9112-f5d2-5cf5-a1e1-509559f7eaf2 | note | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
794ee1b3-05ff-5069-94a8-28bdcf0f023a | note | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
7b1ddd85-54f0-568f-aeb1-99ac422f45f3 | note | Reference Documents - Drawings
4a7702c1-69fd-5e41-b2b9-135a589de5f2 | note | Inspection/Test Method - Visual inspection
0b528149-7ce8-504c-b95b-9120c2ce531b | note | Record of conformity - This ITP signed, Building Engineering ITC
fc01a11f-6de9-5e89-bbfe-8dff256561ae | note | IP
09515fc1-3968-5c77-912f-0349666cb3f6 | note | Responsibility - Project Engineer / Foreman
6984ec20-2520-5287-8b75-3b3ffe366be0 | date | Date Completed:
191d9742-27c9-49ad-a940-9b07e7a2704c | checkpoint | 4.4 - Pre-backfill inspection and Testing
038c5a50-849b-57b7-8247-ff9532e56f0b | note | Frequency - Prior to backfilling each lot
aa796a9c-748c-5829-829b-5636ecc4e979 | note | Acceptance Criteria - HOLD POINT
a0e36d3d-9bd3-5c79-bec7-cd04d9e0d2b3 | note | ○ Pipeline will need to be tested and inspected prior to any backfilling
43ebdf66-a270-5f48-a717-e8c97988d904 | note | ○ Inspect for proper laying and jointing
9663fa0e-9052-5d5f-a679-63422163c57a | note | ○ Conduct Pressure Test and Flushing of the Pipeline
c85dc92d-791b-5b62-809c-a92e4739d813 | note | – Prior to testing, flush all pipework and equipment with clean potable water until the flushed water runs out completely clear
df1c667d-a770-5273-b5c6-fe317984fafc | note | – Pressurise with clean potable water (free of oil and other impurities) and maintain the test pressure for 2 hrs
2719480c-d263-5ba8-b54d-214d8767c0a7 | note | – Immediately after successful testing, final flush all pipework and equipment with clean potable water at “full flow” for at least 10 minutes
f51140fa-4aaa-589c-a2b6-014a35ec4879 | note | ○ In addition to general flushing and cleaning requirement above, disinfect and passivate pipework systems in accordance with AS 3500.1 and any relevant manufacturer written instructions
92b0e9c4-46b4-5d2d-b098-5f3608c0e05e | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00005 C1700.8 .2 a AS 3500.1
616e2453-617a-5bb1-989e-9de29875cf1a | note | Inspection/Test Method - Visual Inspection
d540ab4d-500b-5d4c-8b61-f5d10953a948 | note | Record of conformity - This ITP signed, Building Engineering ITC
826406e1-0eac-5b47-b8cf-98b27206b514 | note | HP/TP
604553a3-a815-526c-b84d-072f523c7336 | note | Responsibility - Project Engineer / Principal’s Representative
ef0aaa0c-ba2c-5bc5-b326-5098c7bfabbd | date | Date Completed:
af20ff8c-4f8a-490a-af70-397667aaa1e4 | signoff | AUTHORITY HOLDPOINT
ab3bb048-b91b-47ee-bf23-378288646064 | section | 5.0 - Construction – Electrical & Comms
12f75b6e-fa0e-475f-9b7c-fd6dfcc25333 | checkpoint | 5.1 - Excavate trenches for conduits
ea48a8a0-a34c-5b2a-8ea9-5fa59533d22a | note | Frequency - Each lot
a99dc15c-51b5-5731-b84e-4f22fff719aa | note | Acceptance Criteria - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
0f8bb527-9406-5506-aa76-f1037f41c65a | note | – The level at the bottom of the trench shall not be above the required level at any point.
8c381322-01dd-5d43-8e4e-c9c08354bd3e | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00004 cl. 3.6
97f3c284-e9b7-5f31-b3e5-7a2b26bcecc5 | note | Inspection/Test Method - Visual inspection
4eceafbb-071d-59f6-a8b1-9bad0780826b | note | Record of conformity - This ITP signed, Building Engineering ITC
0ff200b0-8d09-5d5e-9989-546de0b09b95 | note | IP / TP
416072d5-ec89-5983-af65-5337d4e34eb8 | note | Responsibility - Project Engineer
5d7caf50-514c-5d6c-b2ce-4034c1955745 | date | Date Completed:
ba2c1b87-56f1-4a83-97b5-5a4efa084fa8 | checkpoint | 5.2 - Existing services crossing new conduits
6f790e3b-b6c3-5a66-8d47-24bd0fcb7705 | note | Frequency - Each lot
a22872f2-6f64-59df-8109-e03e88fde06d | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
fa61938c-1e7f-5c27-95cf-d6a0986196be | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
4a5741f1-e307-5256-9dbc-08e56f8b0586 | note | Reference Documents - WMS002 – Working Near Existing Services
623d9add-e448-5ca9-a20e-c07a468ddc3f | note | Inspection/Test Method - Visual inspection
a81e8d2d-3c5b-51c8-b837-14cf235b5282 | note | Record of conformity - As-built survey report, Building Engineering ITC
77ee8d0b-44c9-59cc-93a5-1cfc28011f7a | note | SCP
066fd1fe-213a-567e-9126-e7c286956531 | note | Responsibility - Project Engineer / Surveyor
dc5b7dcb-8f3e-5779-a8ce-bd6940678159 | date | Date Completed:
9aae277d-3059-4106-94be-ce9c7378f29e | checkpoint | 5.3 - Laying and jointing of conduits
d2ddef4f-853b-5036-9173-f09d5b205f72 | note | Frequency - Each lot
aa44c76c-2b31-54a0-96c7-a96ec8717ab3 | note | Acceptance Criteria - All conduits shall be rigidly supported and positioned by concrete former or plastic spacer blocks so that no displacement occurs during backfill.
00784a6b-90f6-5efe-9fee-79c6912d4969 | note | – Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
2836e5b5-ed9f-56ab-86f0-a2aa3d236b15 | note | – Number of conduits and duct route to be confirmed for conformity with design.
7982d891-b717-51e0-bf12-8a49312bf42e | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.7
19965150-2551-5f1b-9a92-7da6a778108d | note | Inspection/Test Method - Visual inspection
6425c996-03ee-544c-81f7-6f4d278ca9d9 | note | Record of conformity - This ITP signed, Building Engineering ITC
8a5fb23e-2cdd-50d5-a120-714c483664b5 | note | IP
c6b7a6e6-c2ee-58b1-85b1-f84e9ee04a3c | note | Responsibility - Project Engineer / Foreman
7aaaef6e-ccc6-51a8-a741-e17d1e9b95b6 | date | Date Completed:
db4eaadb-801f-4c93-95ed-5f94f5ec27f7 | checkpoint | 5.4 - Pre-backfill inspection
92f399bf-89fb-5731-959e-2337afdacc25 | note | Frequency - Prior to backfilling each lot
4d9c51d2-d47b-5209-bc97-2cb4faf54593 | note | Acceptance Criteria - HOLD POINT
715bed06-a062-5962-8787-4f720cd609a1 | note | ○ All trenches shall be inspected by the Contract Administrator before backfilling takes place.
d856aac9-e53f-5eaa-8c81-e5625aef521d | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.1
f477b7fe-e890-5197-8761-034bdfa692fb | note | Inspection/Test Method - Inspection
3cffa7d2-4747-5f80-932a-15a36bbf223f | note | Record of conformity - This ITP signed, Building Engineering ITC
058655c7-1868-5b04-ae59-d8d7bec82512 | note | HP
9563c4a6-61bf-546d-987e-a81d09aff01f | note | Responsibility - Project Engineer / Principal’s Representative
41546e4a-fd84-52cb-a7c7-354a1704b002 | date | Date Completed:
4fb50c44-6943-4843-9475-b235f57a004f | signoff | AUTHORITY HOLDPOINT
a44902a2-81d5-4e2b-a482-9ee7ce19c18c | checkpoint | 5.5 - Conduit markers & warning tape
a839ac4b-3b2e-52c2-8cdd-9357fc2b0951 | note | Frequency - Each lot
3568bef5-f477-5059-9e8d-c803cb4b839d | note | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
b0e8397d-bfbd-5a2a-bba3-cbb9e8a8e5e2 | note | – Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
2f25a123-0f35-5f6d-a993-44258c2e69b2 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.11, cl. 3.12 AS 2648.1
8789eff7-4966-5a9c-9f70-0ea61420b2d6 | note | Inspection/Test Method - Visual inspection
d4814b27-351a-5fc7-8e75-6f757c71e018 | note | Record of conformity - This ITP signed, Building Engineering ITC
0c2aa1a8-d499-5c31-812d-325a4fee3764 | note | IP
95caea90-6fdf-5476-8e9e-f0ff29538591 | note | Responsibility - Project Engineer / Foreman
cc41c03f-97fd-5e88-a7bb-655d53943695 | date | Date Completed:
f9e480ca-b4d7-4f4a-8794-784db2eed334 | checkpoint | 5.6 - Checking of conduit lines
a25d8438-4008-539d-a81a-2e0a272ad43b | note | Frequency - Each lot
37ab6ccb-721c-52b9-a439-f6b45d0bcfea | note | Acceptance Criteria - - Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
43559418-18ff-5e2c-bcf4-c2cb615be3c1 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.9
cd73e86d-5feb-53d4-b047-bae5de9c43a5 | note | Inspection/Test Method - Visual inspection
dd054580-aece-57ca-971e-78d663ad9f4b | note | Record of conformity - This ITP signed, Building Engineering ITC
ff58b552-0d40-51bf-8e06-07af90ae3ada | note | HP*
ce2479e4-fac7-5daa-a65e-69f522ba9e2f | note | Responsibility - Project Engineer
3292ccfd-114a-506f-bc82-f085caaa7bd5 | date | Date Completed:
2d4b5f44-5098-4a1f-8433-fb1456e5f95c | checkpoint | 5.7 - Conduit draw cord
80ca212e-99a0-53eb-8634-4825927f2180 | note | Frequency - Each lot
b3b006a2-caa7-5a9b-bd9f-94ec2e14c491 | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
81657ff7-6287-5c5c-bf7c-2ef57f73ab7a | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.10
5ddb686e-14e7-53dc-a90c-29f22ec41b13 | note | Inspection/Test Method - Visual inspection
595ed43f-f051-5055-a40f-e71c177de1c1 | note | Record of conformity - This ITP signed, Building Engineering ITC
99934019-7ff6-54d3-b085-a86806ed335b | note | IP
a4a6f2b6-aed9-5587-845c-4edda9221723 | note | Responsibility - Project Engineer / Foreman
8167ccdc-a59f-51a9-a4f6-3ff2b01a150a | date | Date Completed:
ec8762e3-bfbe-49dc-ae3d-eb8418ebffd3 | section | 6.0 - Backfilling
7bd2c996-de43-48c2-bc13-e07297400737 | checkpoint | 6.1 - Survey AS BUILT
3666eead-6c3d-5f27-a128-6af2d3511781 | note | Frequency - Each lot
b7d8dba4-b8ad-5e6f-a263-632872289ef5 | note | Acceptance Criteria - Surveyor to pick up completed pipe/conduit runs & underground tanks before backfill
69812a03-2647-54c9-a892-cc190a73ae47 | note | Reference Documents - FH QMP
b5e66ec3-d332-5ddc-8719-d916eb4f1d8e | note | Inspection/Test Method - Verify / Inspection
f1856722-ea30-5fc7-9aeb-abb45990bed2 | note | Record of conformity - Survey Report
b3e1d7a5-cdc9-533e-be89-153ef6d8f18c | note | SCP / IP
91e49d0c-4baf-5372-b1c4-bf54ed69c6bb | note | Responsibility - Project Engineer / Surveyor
15b51c45-79fa-5d1b-9d20-d18643b9d9cb | date | Date Completed:
1e7b5f5f-5ca2-406e-adbd-7f6f46574828 | checkpoint | 6.2 - Backfilling Conduits/Pipes
74c4b981-4976-5da4-92b5-e9e4ee8c98cf | note | Frequency - Each lot
cdb4ec65-1ad1-5326-aaf4-b90047db4ef5 | note | Acceptance Criteria - Bedding
040cd87b-ae88-5112-92c3-4657c99f8661 | note | – Bedding material shall encase the pipe to 100mm compacted thickness above the pipe and be compacted simultaneously around both sides of the pipe
efcd0867-f5dc-5529-a398-de036df479c0 | note | ○ Backfill
6f14e4a1-fa51-5918-b08a-a81ea550fc5f | note | – Backfill remaining area with site won material from excavations and compact in minimum 200mm thick layers
73504798-d733-553b-ad69-dd79fcf7f5e8 | note | Reference Documents - Drawings
5e68a8c9-94a7-5ee1-8a92-685668f704bf | note | Inspection/Test Method - Verify
8d6316b7-d157-5fe0-ac59-4d035d0894f1 | note | Record of conformity - This ITP Signed, Building Engineering ITC
745e37ee-6739-5941-9a84-35861f57682e | note | IP
9aae55b7-a8a5-5f79-bb4f-07d87f25f853 | note | Responsibility - Project Engineer / Foreman
43787b90-4fe2-5d30-878a-2a1ae3e7df38 | date | Date Completed:
f4590df8-cedd-429a-9df5-ef6ac2c718ca | checkpoint | 6.3 - Testing of Trench Backfill
6b599328-9a1a-5ae0-a504-ca71d5461088 | note | Frequency - Each Lot
11d44802-531b-5e0f-8a92-16ac127528d2 | note | Acceptance Criteria - The minimum frequency of field density tests shall be in accordance with AS3798 table 8.1 and not less than 1 test per 50m of compacted backfill in each layer of pipe trench fill.
fea8b0b3-600d-5862-8be3-750dbf4bd7a4 | note | Reference Documents - Drawings AS3798 Table 8.1
fec390af-5b73-5e04-a987-53e46dc8d15c | note | Inspection/Test Method - Verify
71e5dd2d-cd88-5c42-ad27-0ff37f2af590 | note | Record of conformity - This ITP Signed Test Results
7f139c6a-2e7c-5096-aee9-f0d998587d4e | note | TP
516aa523-194d-51db-8e17-86dec4438cb8 | note | Responsibility - Project Engineer / Principal’s Representative
43875871-eb4a-5648-b38e-547c51be41c3 | date | Date Completed:
58b9ed52-0183-41c5-970a-65fadd3e7aee | checkpoint | 6.3 - Surface Reinstatement
ebae4922-f6d3-5eb0-a2c8-ac693cbe6b87 | note | Frequency - Each Lot
046b12e6-58c3-52d7-92d2-9b3389afb0aa | note | Acceptance Criteria - Pavement Areas
84969a25-d46b-5401-abef-8c9e5d9da545 | note | – Final backfilling in existing pavement areas shall to 100% compaction
6940e089-6459-56d9-a2e7-8de27d6b3ce8 | note | – Mechanically compacted in max 150mm layers
7b62a47c-b401-5d88-b454-439bd5a9a881 | note | – Basecourse depth shall be 400mm or existing pavement depth, whichever is greater
89553e26-6299-5913-9ed6-672fb0645399 | note | ○ Grassed Areas
c9c00cec-c189-5416-a926-a28dfda4c69f | note | – The final 100mm of backfilling shall be clean topsoil
80b7788b-6328-5af8-b0e2-cc8ec641ceed | note | Reference Documents - ZULU-BECA-001-SPC-000All 05 C1772.6 .1 AS 2566
5654ca50-d931-5be9-828d-8a79a1973864 | note | Inspection/Test Method - Visual inspection
27c38f08-3efe-50e0-a17c-bf8466ed2039 | note | Record of conformity - This ITP Signed, Building Engineering ITC
12bc3994-0178-5a0a-b585-6cc649ad837d | note | HP*
d9bc858c-589f-59e3-a354-1e3003599a66 | note | Responsibility - Project Engineer / Foreman
9168f713-c112-56d0-98cc-f849e21df182 | date | Date Completed:
b63fb0ae-aedf-4f41-9cf6-54d0250ef2d8 | section | 7.0 - Construction – Precast Pits, Headwalls, & Underground Tanks
e9a16b50-db1d-4351-9e80-d48b07a61ba4 | checkpoint | 7.1 - Placement of Septic & SPEL Tanks
b9f9c4cb-e6b2-537c-90a0-b2032c2b6a4c | note | Frequency - Each lot
1909c6dd-a2c1-5eb4-a564-6c39d6236c7a | note | Acceptance Criteria - Ensure placement of tanks is as per manufacturer specification and as per design levels
6abd49df-145c-521d-9145-40247c7ccfbf | note | Reference Documents - Drawings, Manufacturer’ s Specification
601356bf-7049-5c4e-81d4-6029633a14c8 | note | Inspection/Test Method - Visual inspection
57632bc3-0cb4-5752-a02b-d7bc95c9fe7a | note | Record of conformity - This ITP signed
b5870f44-a6a5-5ec1-96f0-0f21c844ae2f | note | IP
686ba71f-ff41-5c89-836b-e064096b534c | note | Responsibility - Project Engineer / Surveyor
6397d9b3-2a82-506f-8ab1-12704413e8ef | date | Date Completed:
1b835e34-786d-4fae-8c1b-ff4a21434c26 | checkpoint | 7.2 - Placement of Pits and Headwalls
3c9770b5-9846-518b-a0cf-cfc95422ed12 | note | Frequency - Each lot
aea96644-782c-5459-82e0-cb4a5c5daed6 | note | Acceptance Criteria - Pits placed and levelled as per survey set out
558f354d-a694-5ddf-b616-63d91894172b | note | Reference Documents - Drawings
0f974dbb-10aa-54d1-ab77-e319bb8ba432 | note | Inspection/Test Method - Verify
7d0dd19a-8163-5731-a354-4a6ded4ecbb2 | note | Record of conformity - This ITP signed.
a901e1c9-d700-5aa2-ac6a-fde143f76ca2 | note | HP*
4852fa40-84ee-52db-b18b-493c0e801126 | note | Responsibility - Project Engineer / Surveyor
9fdced34-b459-50fb-a47e-e5333a6b79b4 | date | Date Completed:
4b7199b5-ec6c-4661-8adf-88775109d70e | checkpoint | 7.3 - Bedding & Backfill of pit surrounds
491a2254-d951-5a20-a4cb-43111c804f9e | note | Frequency - Each lot
70cd62b5-6ed4-5321-a5ff-d771aabeb42a | note | Acceptance Criteria - WITNESS POINT
a13d0159-b532-5a22-8176-674402d197ef | note | ○ Each pit/headwall shall be bedded and be backfilled with stabilised sand for grassed areas.
51cd9c6d-49d5-5f40-89e7-676129c08bab | note | ○ Principals Representative shall be notified to inspect installed pits with all connections prior to backfilling
dd56d547-8b6f-5c49-821c-433c75077ce0 | note | Reference Documents - ZULU-BECA-001-SPC-00004 Drawing 00201
b3cd6eb6-cbad-59b1-bf9f-7aa9dff0dbf6 | note | Inspection/Test Method - Verify
a10d794e-d1d9-5788-83d1-75b1e8bbfb2d | note | Record of conformity - This ITP signed
f9e711e0-aa38-5042-94eb-1238979b606d | note | WP
f823c198-3a30-5be4-93e1-348005daf2b1 | note | Responsibility - Project Engineer / Principal’s Representative
2076cd90-a3f8-532f-8e2a-486cc5d271da | date | Date Completed:
0bf232dc-2b46-4f6f-b371-a25fd0e73b5e | checkpoint | 7.4 - Pit Close out
03d8b536-4452-55f7-9895-31b240c47c6c | note | Frequency - Each lot
0bd307ba-7dbb-5d42-a0d0-0a60e826435f | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished
daf720c2-73e5-56fb-bf47-05c64d64ad84 | note | Reference Documents - ZULU-BECA-001-SPC-00004
3af00308-ba8f-5ae8-b192-0b1443880898 | note | Inspection/Test Method - Verify
a244b536-edd4-581e-9d1e-024481d0f797 | note | Record of conformity - This ITP signed
bd18a973-f699-57ea-b421-6e51ce22805a | note | IP
6fd38751-2b0c-5a99-bdba-ddb861a0c597 | note | Responsibility - Project Engineer / Foreman
bfc9c50e-bf0a-5e92-b128-ca44187e5c4e | date | Date Completed:
d08703af-c3ed-4d80-bb62-7ab3063625b1 | checkpoint | Final Inspection
e8d02f10-c3df-51e3-a112-260136929242 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
eef03edb-87bc-5217-9f85-849473fca17e | textbox | Print Name:
490b2658-d57f-507e-9bfd-92c569e044bb | textbox | Position:
9037209b-09e3-5d81-aeba-402cc1a94e93 | date | Work Completed On:
e9bb53cb-110d-5264-88f7-ad6532d986d8 | date | Date:
d00908ec-06f5-531d-80b7-513b040c8fbc | checklist | FH-ZU2-QU-ITP037 - Miscellaneous Concrete Structures - Rev 0 | itp | ITP037 - Miscellaneous Concrete Structures
d7d6e24a-41e3-57a2-9551-08a3da3fcd83 | section | 1.0 - Preliminaries
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
b002ba69-0846-5329-95ce-92f03f564abd | note | Frequency - Prior to Start
d8391e9f-1a44-5702-aef6-8577473f863c | note | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
ba926b1d-10b8-58fb-a7bc-9b6a8d9899ef | note | Reference Documents - Drawings and drawing registers
6beae9ca-6003-5dc0-8b00-9ca675b37513 | note | Inspection/Test Method - Verify
ff5f5844-0a83-50a8-9c95-0b825d27f00c | note | Record of conformity - Up to date drawing sets and this ITP signed
1e654ed5-18c9-562b-87f2-c955c4c71664 | note | HP*
8012b25b-e817-5a3f-8ee6-bfe51d9af523 | note | Responsibility - FH Engineer
4365fa68-3bd9-5848-9e9e-533dcc9f0e1f | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
1d9cc5c7-0673-5e58-88a8-60c4d75582a2 | note | Frequency - Prior to Start
634d8de1-d01f-561a-9505-1d0b8205b529 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
6e079538-eb45-5aea-887c-cc9c4f74e3c9 | note | Reference Documents - CEMP, TMP, SWMS, & WP
c692070f-9ea4-5141-bc9f-c65f7ffd125f | note | Inspection/Test Method - Verify
f5968200-60cb-5ba1-9094-752543eb917d | note | Record of conformity - Site and office Inspection
06401db3-a8ee-5ef0-8fc4-edb90f316767 | note | HP*
794f01f8-8193-57c3-b868-48dc722fedc9 | note | Responsibility - FH Engineer
cc491c4d-c944-5731-9871-48b7c14f518b | date | Date Completed:
ddc68377-ad92-57e5-8ab0-c671f713640c | checkpoint | 1.3 - Excavation Permit
51936bbc-89ac-5300-b17d-a44005c8c819 | note | Frequency - Prior to Start
acc161e6-c2d7-5969-9825-e697f799d996 | note | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
48e02164-f603-59a3-b0ea-242bdd0383ff | note | Reference Documents - Approved permits
3ff52c1c-655b-5826-91a1-39bb19b0455d | note | Inspection/Test Method - Verify
cf0672b5-9c02-58d7-bd8a-b83d9c93ac64 | note | Record of conformity - Proof of & permit ITP sign
cf001051-31d8-5980-9f25-7e0560163a74 | note | HP*
3adbc93d-03e7-5bed-abef-f2776deee7a4 | note | Responsibility - FH Engineer
db49ea9c-6ec0-5611-9344-5007c07330c3 | date | Date Completed:
e7d6a2c5-dfe1-564c-bad6-fb4b3c19c030 | section | 2.0 - Supply of Materials
4efdd4d4-52fc-5940-a0b5-06a09948b577 | checkpoint | 2.1 - Reinforcement
6dd6df10-7cfe-5e8d-afee-e3e7b54830f2 | note | Frequency - Pre- commence ment
9ffb0ef0-8d49-5f7b-a4ed-90e614c70010 | note | Acceptance Criteria - Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
5a748777-13fb-5181-bece-6b8cc438ffc0 | note | Reference Documents - Drawings and Specification
4d91bbf2-c284-5e3d-94e7-0a04c1ab6c6a | note | Inspection/Test Method - Verify
5b2a4c52-5f7b-50ee-8f20-43d8faa7ad4a | note | Record of conformity - Aconex Corresponden ce
0af55697-203a-5361-9e22-256e4cfe8da5 | note | HP
951c0b47-36fc-5543-8442-0f0e8ecb09be | note | Responsibility - FH Engineer and Beca
8e7a6589-ad12-52a1-90d1-32380abf4a18 | date | Date Completed:
1e9728dd-8dcc-5f23-9080-8091cd6934b0 | signoff | AUTHORITY HOLDPOINT
bd5c6996-6a22-5c02-8b2c-9467cb09ea22 | checkpoint | 2.2 - Concrete Mix
05b5a876-6948-5102-acb6-334622009e75 | note | Frequency - Each Lot
882bc682-54c0-5930-9599-b66fd67c952f | note | Acceptance Criteria - Mix design to be submitted to contract administrator for review and acceptance.
beaf99eb-1d35-5b05-867a-de0471448acb | note | Reference Documents - Drawings
be7ef34d-785f-53f5-a7a3-cea6573f64b9 | note | ○ ZULU-BECA- 014-DWG-00201
18de00ac-d5b6-59e3-a39e-9be1cf27d974 | note | ○ ZULU-BECA- 030-DWG-20001
c2e5796a-863c-5b85-a118-fdcca1081a20 | note | Inspection/Test Method - Verify
714d9154-957a-5b59-a557-b60ef3a2ae9c | note | Record of conformity - Mix Design
8f171c0b-7de9-5954-9053-3e7d62187d50 | note | HP
2431fc77-5022-5730-9e24-5c59a6c6e101 | note | Responsibility - FH Engineer and Beca
2aae881a-8ed9-523b-a4e5-c218cb27eac7 | date | Date Completed:
36b14944-6e88-561e-afa6-593f076ee8f1 | signoff | AUTHORITY HOLDPOINT
a5f0f7e3-a1a9-5d5a-b4c7-f7af01a7861d | section | 3.0 - Construction\Erection of Formwork
eb40cfd1-0f1d-5fe1-8994-e0241de1ab9a | checkpoint | 3.1 - Setout
cb4664e4-487f-53de-aa32-acba96015630 | note | Frequency - Each Lot
33d4cf1b-28f4-5c78-b033-6390eedb8469 | note | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
85eef7fc-9248-54d5-85c3-f5437cf815ad | note | Reference Documents - Drawings
252acc84-8359-5556-9cbc-c26c32ab5e35 | note | Inspection/Test Method - Verify
36355643-4806-5297-a104-ee063e497057 | note | Record of conformity - Survey Report
38e3e112-a3e5-5b29-94a0-0662954157f0 | note | SCP
5bd9fa8d-b965-594e-bd97-03b423689422 | note | Responsibility - FH Engineer Surveyor
70e6cd01-f7de-5761-b30c-bb38a9d347c2 | date | Date Completed:
e9ad5079-1a8d-53f6-8a56-43fcffd1e2ce | checkpoint | 3.2 - Excavate
322c8298-b2fa-5059-b3f3-5826bb211460 | note | Frequency - Each Lot
a22ca8d8-49b1-5073-97d0-33dcde9e2494 | note | Acceptance Criteria - Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
9d45e13c-9688-5560-b325-5c5428592a70 | note | Reference Documents - Specifications as per Drawings
43e7751b-257e-5a6c-a831-2abdca374e77 | note | Inspection/Test Method - Verify
da445de3-a803-53aa-89be-29edbcc332d8 | note | Record of conformity - This ITP signed
d57e5973-35c0-5703-b69d-911e946b7593 | note | IP
397d5975-c942-5cf9-a7e5-3c7185cb4a18 | note | Responsibility - FH Engineer
e89f4d3b-5145-5c80-8df8-723b301359e0 | date | Date Completed:
86d44e27-ac01-56fa-afcb-52c35ccaab9b | checkpoint | 3.3 - Confirm Ground
46baabf9-0a9e-53de-a0c0-fcf4b622e5b5 | note | Frequency - Each lot
97b9c041-e7d5-527f-8cbc-0b430f7c3fc6 | note | Acceptance Criteria - Completion of excavation and inspection of subgrade materials.
30960d7f-c649-5339-bac2-6e827bc07af1 | note | ○ No soft spots, unsuitable material
aefa6754-73e4-578e-a804-e759637e8a02 | note | Reference Documents - Specifications as per Drawings
01b9c0a2-2b40-5a2b-8aab-609423388437 | note | Inspection/Test Method - Verify
faa64974-476c-54af-8f12-d6fc764c49ea | note | Record of conformity - DCP Test Results (if required)
b2f7662e-fece-5afa-875f-f9993f948509 | note | HP*
dd7c4fc9-4f64-5572-b779-5ed2219ed47c | note | Responsibility - FH Engineer
586c461c-9afd-5edc-943c-5a278c9e6cf0 | date | Date Completed:
5703acb3-5611-53ad-af4e-6d13ccd382ba | checkpoint | 3.4 - Formwork
e127324e-adb3-5d9c-bf9a-b0b4e56c0743 | note | Frequency - Each Lot
45f3589f-3933-545d-acb4-fef602f9e8bd | note | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
a61bb31a-062d-5370-98cc-d23e7493d056 | note | Reference Documents - Specifications as per Drawings
9cab4f30-f75e-5034-8d49-da596e80a40c | note | Inspection/Test Method - Verify
7b436f07-e3c9-5bb5-a6e2-0c035a2bdda4 | note | Record of conformity - This ITP Signed
92e5a57b-7738-5394-b8ce-1681795b1ac5 | note | IP
1d7c03e0-82ae-59a6-9827-71639098fc4b | note | Responsibility - FH Engineer Surveyor
c8d76fee-e5eb-5767-9311-87caa8f8c7ed | date | Date Completed:
adeebccf-6b68-5500-9d1e-f9eac973e561 | checkpoint | 3.5 - Penetrations/Cast in items
bf19c4ef-18bc-54f7-8b9e-5edef28b24a3 | note | Frequency - Each Lot
9c0fc27a-9bef-5e55-88b8-1c55c67d9448 | note | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
c8545872-ae2b-5d9a-a16f-ed32383c1068 | note | Reference Documents - Drawings
cf71dbe1-53b7-5974-91ec-3cac5232f8bc | note | Inspection/Test Method - Verify
4c3e5912-07bc-5588-b3ac-7e8c846bb328 | note | Record of conformity - This ITP Signed
9a242af2-de27-5e33-b6bc-de8a275d4503 | note | IP
20b8f032-b3d2-5389-94c2-1f32e4de4f98 | note | Responsibility - FH Engineer, Surveyor
cb544ac7-6e46-5a24-9da8-2ccf03183ed9 | date | Date Completed:
f41a2245-b899-54e2-bb9f-e76b7215b2ea | section | 4.0 - Reinforcement
512b0bdc-7032-5766-8b6d-3372bfa7e3ec | checkpoint | 4.1 - Reinforcement installation
8fd9431d-02db-5e3b-8092-18313e55918d | note | Frequency - Prior to concrete pour
78d14bd8-1a1b-527d-af58-09cc231d8436 | note | Acceptance Criteria - Pre-Pour Checklist Completed:
2aa385ea-f6ef-5fb5-a2ce-8dcdb29e80b8 | note | ○ Position and spacing check and recorded.
89e1959f-7517-5e7e-bf37-9304178d7bca | note | ○ Cover checked and recorded.
3776f8f3-f157-5ae4-b1b9-3d0b477ccc07 | note | ○ Reinforcing supports checked and recorded.
f707f26b-b8f8-5d7a-8f12-e7b3f11a01e4 | note | ○ Laps at required length.
e1d1b015-7e2d-5e59-91ac-b7c6b87db2a2 | note | ○ Penetrations/cast in items
20d5cfc4-2a13-59de-8730-9a43f649c067 | note | Reference Documents - Specifications and drawings
e2555919-a29a-5ef2-8f65-da84fb8f07d8 | note | Inspection/Test Method - Verify
19649ed9-c55e-5769-a6c8-add8e6b20fe9 | note | Record of conformity - Pre-pour inspection List, CLA37A
7d322283-b189-5fea-8c72-afb768a1102a | note | IP, HP*
174f4201-bf3d-5f42-af73-2a6b154558cb | note | Responsibility - FH Engineer
f213532c-5214-58fd-850d-e5097ed96bed | date | Date Completed:
90bb8dc2-5a3a-51ca-a065-52ad2ad32000 | section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
928544de-658c-58de-82ea-71841e5b0101 | checkpoint | 5.1 - Pre-pour Inspection
cfc4eb44-5ca5-5665-ad86-50a9d4a3e147 | note | Frequency - Prior to concrete pour
88462cc6-bec5-5300-ade2-4131b5969922 | note | Acceptance Criteria - Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
6fb00c53-aef0-5d94-b851-ef4e438d7510 | note | Reference Documents - Specifications and Drawings
55f4e114-6c5b-5d87-b449-f7e20d6bb744 | note | Inspection/Test Method - Verify
3165fbed-7c58-54ed-a53d-7f8d86108f71 | note | Record of conformity - Pre-pour inspection List, CLA37A
e0882f08-8cc5-5e22-b64e-4fecf6c1e587 | note | HP* WP
b5238538-31a9-5400-a80b-d3cf7e826de3 | note | Responsibility - FH Engineer
39cd7b95-5e90-5250-875e-0c6f127226c0 | date | Date Completed:
edb492b0-0eae-5705-bd33-a10de3855a95 | checkpoint | 5.2 - Pour in-situ
89dd0caa-9a3f-544f-b8fd-d9a1412b757f | note | Frequency - Each Lot
ff9ec6ae-f6af-59f6-a7e2-210a24136436 | note | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
2718c38d-36b6-5d35-a289-ac3e1133b283 | note | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
fe15d65f-b580-5d16-9b31-da24c225f54a | note | Reference Documents - Specifications and drawings
15e0bf2b-36e7-545e-9d84-6b5fb087ae92 | note | Inspection/Test Method - Verify
8f133827-c2c1-59de-88ce-8c575499a238 | note | Record of conformity - This ITP signed
adfb4b9f-cc62-579b-a54d-567565e2f47b | note | IP
24b1f373-a4fe-5053-bb67-cf3cd5e001ba | note | Responsibility - FH Engineer
3bd96a6f-7074-5a47-9cc7-6e6a336eff88 | date | Date Completed:
65a98220-5434-5fe0-af42-69dd7525cf8a | checkpoint | 5.3 - Concrete Testing
4452631d-37c2-5909-915f-fba055363fde | note | Frequency - Each Lot
a1760154-9536-5337-84c2-31fe92d069cc | note | Acceptance Criteria - 1 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
0bbdfac9-b805-5c30-b04f-c5ddbafe4712 | note | Reference Documents - Specifications and drawings
1fe14439-bcb0-5b9b-8f6e-68c7601989ce | note | Inspection/Test Method - Verify
dde80bfe-a25c-54af-86e3-67ed0d000b08 | note | Record of conformity - Concrete Testers Sheet/Results
bcc7a6e2-f826-5f77-b3e3-6a71bebfdb84 | note | TP
d307e6be-c353-5543-928a-54465e8f0b87 | note | Responsibility - FH Engineer
bf20fdbc-fc84-5337-8872-e50d1efe2bc9 | date | Date Completed:
2d730bb0-a0c9-5bf9-8741-c1d322ef6473 | checkpoint | 5.5 - Finishing & Curing
5123af1d-eb68-593f-8e99-276fa702cf55 | note | Frequency - Each Lot
1c7b4f41-794d-5ffa-890c-ce8a5bbefd90 | note | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
a7df4d8c-c931-5099-af0e-27329040c70e | note | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
6317a0da-e5ca-50e5-b8b5-58561832257d | note | Reference Documents - Specifications and drawings
657bf579-b764-52fb-8d25-68827f8fcc6f | note | Inspection/Test Method - Verify
076f546b-3a68-5fd4-9e0f-68d7196f50ce | note | Record of conformity - This Signed ITP
6dde9b4c-e5da-53df-85de-ebba798dd290 | note | IP
6b18dded-1116-5dbe-a95c-e4fc443edef2 | note | Responsibility - FH Engineer
7faef982-f091-5ce8-82a2-4126d3ce3355 | date | Date Completed:
17539653-d776-53de-bfd3-447b816c62c0 | section | 6.0 - Post Pour Details and Inspections
02678ea3-cea5-5a84-ac58-34fff2215224 | checkpoint | 6.1 - Removal of Formwork
a6db7816-ff3c-5c5e-96cf-396d11f05153 | note | Frequency - Each Lot
eceda214-c95c-56eb-8abb-789fc22da409 | note | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
8d67bdf9-1be6-5e86-8cac-1c908186c57d | note | Inspection/Test Method - Verify
d58b5ae9-f06b-5951-9e7e-beb62712dd4d | note | Record of conformity - This ITP signed
e025797a-e93d-585a-ab61-6bc1ebfefaef | note | IP
8142acc9-cef6-5637-8b28-3e40a1dba1ff | note | Responsibility - FH Engineer
18055ab2-5f70-5619-8492-84dc6b888d1b | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
cfe2ee0b-7871-501f-9116-490a2f406f57 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
c0b07b42-38e4-5cac-bd5d-71842dfc70e2 | textbox | Print Name:
ba181add-0945-5b9d-ba3d-3e1f62886868 | textbox | Position:
99be15b3-36a2-506d-8fdf-82a92df837a9 | date | Work Completed On:
ab7e37fc-72bf-5311-be07-2b569d866995 | date | Date:
1efdf959-8248-5807-8569-01db5e6ceb81 | checklist | FH-ZU2-QU-ITP038 - Native Grass Protection - Rev 0 | itp | ITP038 - Native Grass Protection
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
216f13c0-631a-5de2-b0e8-fa6c90d79a55 | note | Frequency - Prior to site establishment
4865a96d-3c1c-56af-ac3c-5e4505e5a0ca | note | Acceptance Criteria - Review whether a preliminary report has been completed for the project which will outline where the Significant native grasses are and what protection has been specified.
a8a796cf-5317-54bd-91f0-127b840b229c | note | Reference Documents - Consultant reports
dfc0e17f-a7fb-5399-964b-061ad1ddcade | note | Inspection/Test Method - Visual inspection
b60740c1-039b-5ee9-ad44-5eb87146d68c | note | Record of conformity - This Signed ITP
a12a05ea-f6c1-5ec7-90cf-9d30a6834ce0 | note | HP*
d8df4a35-931a-583d-9715-e1beb93e2b7d | note | Responsibility - FH Project Engineer
46867ecf-e671-59a9-882b-a222ccf7f921 | date | Date Completed:
a6a1e302-9d33-53a4-be2b-e1ef735da4c4 | checkpoint | 1.2 - Check the Google Earth Mapping
7d49b9ed-235a-52ce-a8f4-2de6272b0539 | note | Frequency - During site establishment
0935c216-bfa9-53fa-aa5e-6a24aadf877e | note | Acceptance Criteria - Review the Google Earth / GIS mapping which outlines the boundary of the native grasses at the time they were mapped.
890b0dca-2ad6-57f6-a256-cfbac6c3fd1e | note | Reference Documents - Google Earth Mapping
e828aed7-b6b9-5af5-b39a-7cfd2ba13139 | note | Inspection/Test Method - Visual inspection
4c63015d-0410-5dfe-84b1-0f2a44f6494f | note | Record of conformity - This Signed ITP
3f02a3d8-03b7-52b6-bcef-69cc7373f799 | note | HP*
5fa5b223-a8d4-5c5f-a979-66255446357f | note | Responsibility - FH Project Engineer
66c722a9-7fb1-53a7-a3c3-49221e73ac68 | date | Date Completed:
44272205-ef92-5f59-a531-1196a8a07cb4 | section | 3.0 - Implementation of Controls to Protect the Native Grasses
42562f14-5665-51df-93f1-f6c8326afa31 | checkpoint | 3.1 - Mark out the exact Significant Native Grass Boundary area
7b9cc617-651f-548d-84f2-c5bfa7195818 | note | Frequency - Prior to commencing any activity
9e5247df-1849-5d0a-ac94-738ed0a240e9 | note | Acceptance Criteria - Work with the surveyor to mark out the Significant Native grass boundary. FH Project Engineer must verify the set out survey data file matches the ECP and GIS.
cd48b603-4e2c-5241-977e-2b838e386106 | note | Reference Documents - CEMP & ECP
f03b23f5-4e4f-5063-9515-445644e52b43 | note | Inspection/Test Method - Inspect
9c11c12f-352e-5db0-92c6-9953921e13eb | note | Record of conformity - This Signed ITP
604250c5-a2c0-5718-be33-25a53ed49fc6 | note | HP*
9405f436-a806-556a-ba3b-73cb5cfa7103 | note | Responsibility - FH Project Engineer
9d3efbad-6c9d-5657-8277-15af080be725 | date | Date Completed:
4e01a72f-07ff-5070-a5d3-484e91bdc8b2 | checkpoint | 3.2 - Use temporary fencing/bollards and signage to block access to the Significant native grasses where we are working in close proximity.
55b2ead0-5305-5d1f-ba70-df0cc5ef6528 | note | Frequency - Prior to commencing any activity
d56d6f01-1109-59d9-a58c-202e8297dc02 | note | Acceptance Criteria - For works in close proximity to the native grasses, use temporary fencing or purple bollards to block access with signage stating “NO GO ZONE NATIVE GRASSES”. Where possible, this fencing will be installed at a distance (1-2m) away from the actual native grass boundary to act as a ‘buffer zone’ but still allows works to progress.
231e9034-3722-5440-abdd-2a691a73f168 | note | Reference Documents - CEMP & ECP
a6e5d715-ee40-54cb-b489-1074dc6ab1ef | note | Inspection/Test Method - Inspect
684fa277-9e04-5df0-973b-bd4fabbba96d | note | Record of conformity - This Signed ITP
de894924-de20-55a4-b2fe-e3e9090e645a | note | HP*
6518d271-ff9d-52a6-968d-1aad7fb2d35d | note | Responsibility - FH Project Engineer
2ecb63d8-d93a-5324-8656-94f77f649fcc | date | Date Completed:
af813026-2a0e-56b8-b954-2a26dfe86740 | checkpoint | 3.3 - Implementation of control measures required to protect the significant native grasses around our project area
ce3ec308-c40b-5654-b01b-fa9c462bc99b | note | Frequency - Prior to commencing any activity
70eb4d5a-2c35-533f-ba80-b2090e69c2d5 | note | Acceptance Criteria - Inspected and validate native grass delineation has been installed correctly using GPS mapping and against the design drawings.
8c06eace-458d-5889-9803-a0bfb7305238 | note | Reference Documents - CEMP & EMP
2ce81219-11a7-53b2-a7c1-08a4a9fa3dff | note | Inspection/Test Method - Inspect
57032812-6950-579e-9bdf-0d3204896163 | note | Record of conformity - This signed ITP
15f24092-ef40-59e0-ab53-bbc888e9c3b8 | note | HP
590151ac-7781-5df5-aa78-61f32f38673c | note | Responsibility - FH Project Engineer
62376a53-799c-5c5d-8b46-8a01aacbcda3 | date | Date Completed:
cf3529b9-ad34-5792-b2a0-f66e6d945212 | signoff | AUTHORITY HOLDPOINT
e7187eb1-074a-53f4-9d79-9ca9cfcd975b | section | 4.0 - APAM Hold Point Release - Second Inspection
3fad56da-64fa-5bd4-a2e8-866684b1f99a | checkpoint | 4.1 - Release of Hold Point for Native grass Protection
1514a478-e8a2-5956-97af-5aac277f7c60 | note | Frequency - Prior to commencing construction
16698acc-f712-57d3-b446-36cc47b8d676 | note | Acceptance Criteria - Arrange an APAM inspection to confirm that the native grasses are protected with the required temporary fencing or bollards and correct signage where required.
aaf09a0d-10a7-5d7f-a40f-7880b7f29fff | note | ○ All parties are to sign off on this Hold Point
a554ba14-e259-5b74-b82d-e33ccc278e93 | note | ○ Release document
67135554-3eb0-59e4-a017-9fb6cf9b2ec2 | note | Reference Documents - CEMP and ECP
caa3d8fb-e362-53c7-9629-09e294870f5e | note | Inspection/Test Method - Visual
ed9995a5-92ad-5c82-9a71-76ef981f15f0 | note | Record of conformity - This Signed ITP
1d5a99cf-1eba-516a-bf5d-b9c2d13d1c2a | note | HP
bfc9749e-effb-5925-9977-03a5ebc89408 | note | Responsibility - APAM, Fulton Hogan Environmental Manager or Project Manager
848286a1-04f4-5425-ba4c-0c33c6fc3015 | date | Date Completed:
adad0398-bccf-511a-a4c3-0cbadb72ff49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
c1cfe4e5-b9a8-5a77-804a-a216757322c9 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed above have been reviewed and implemented in accordance with the Construction Environmental Management Plan and conform in all respects with the requirements of the Contract.
1686e2cb-e6db-57e3-9eb5-1b42be8b4ad0 | note | FH Environmental Team
e2acd868-285d-5070-b4a5-44cdc9e52994 | textbox | Name:
359709b0-92ea-5762-b403-eb9708784de7 | textbox | Position:
a0ff56c3-768f-5bb6-8989-1c9828e97505 | date | Date Completed:
c839de23-6ced-54fe-91ad-70b2eca78835 | date | Date:
543635cb-6dfd-4f0f-b2bf-d8544fabcb8d | signoff | Add Signature:
c9944d37-6106-4e50-9742-85b7454d1fcf | checklist | FH-ZU2-QU-ITP039 - AGL Boring Installation - Rev 0 | itp | ITP039 - AGL Boring Installation
1dd2d3d1-1568-4aa4-9bb3-841f3043c321 | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
4dd46308-4b6e-4750-8634-aaab33d7b382 | checkpoint | 1.1 - Check for correct documentation
8ab37f9f-8f1b-51de-912e-b6fa76a6d279 | note | Frequency - Prior to commencing activity
75fbddfc-db58-5dc5-a182-cd4888907403 | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
465ea8e6-eef1-5bc8-b9cd-d348239521d7 | note | – using the correct and complete set of drawings.
9fa3feee-ce9b-5618-93fd-885eab9c4247 | note | – all drawings are the latest revision.
2a2a2801-a222-599e-9cf2-b17a2037ec87 | note | Reference Documents - Drawings / Aconex Register
22ef2956-07f3-5335-bf04-bd472e44747d | note | Inspection/Test Method - Verify
31ffa833-4c77-5e2a-a8ae-5f92105aeec2 | note | Record of conformity - Drawings and drawing registers
16eb0b6b-cd98-5f3c-81ed-5701eab898ea | note | HP*
afa681a4-9f46-59f8-b3ec-d3db808d3c6f | note | Responsibility - Project Engineer
8cbadbdf-73cc-5676-a9ef-3cf257352b0d | date | Date Completed:
abe7982b-b654-4048-954a-438f87e9420b | checkpoint | 1.2 - Implementation of all measures and controls
6b48f58b-3080-5a7f-af80-f5bce9ebbcb8 | note | Frequency - Prior to commencing activity
5183872d-f4d6-54cd-9015-258e0e7c2608 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
5ca885fc-c26c-5326-a5b3-bd944bb64bb0 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
04e699aa-2ece-53b6-b501-a1be308fd83a | note | Inspection/Test Method - Visual inspection
68a6dffe-3eef-58a5-a80e-254252f5f1be | note | Record of conformity - This ITP signed
1d37e191-ec2f-5849-a090-3869956bddeb | note | HP*
2bb1f8b4-e62c-5d48-9da0-8195c755f81a | note | Responsibility - Project Engineer
6e1e9fd9-32f1-563e-a3d0-fe7669073b8d | date | Date Completed:
02ca07be-eefb-4b88-a161-b3f81f7e6415 | checkpoint | 1.3 - Definition of the work area (survey)
e4923513-5907-56b9-b6e6-da742579ef89 | note | Frequency - Prior to commencing activity
591feb0a-23c6-5959-8943-8b44f2f99442 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
a41765cb-bd08-5558-a2fb-587b4e9ed264 | note | Reference Documents - Drawings
3ed0ff72-f241-5ff1-a02f-70ad13618c68 | note | Inspection/Test Method - Visual inspection
740124b6-c4e4-5959-a122-921bd454e14d | note | Record of conformity - This ITP signed
1bea879f-6b5a-5cb4-820e-c46154b126ad | note | HP*
0ea5da2e-bcf6-5e52-8117-93fe5f457478 | note | Responsibility - Project Engineer / Surveyor
a08d871f-1bcd-5213-9a16-9f3842f9dc3e | date | Date Completed:
f50ceda2-8ab9-426e-81cc-44566ee02ffe | checkpoint | 1.4 - Material Submissions
bce64033-335c-5624-abd0-7b012cde628f | note | Frequency - Prior to commencing activity
92102d15-1c0f-540a-b38f-296a0414c404 | note | Acceptance Criteria - – Ensure material submissions for the conduits and grout are submitted
95230e63-7f50-5239-89a5-37fb7abc2309 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl. 3.4, AS 1477 AS 2053
444d8bcf-3a7b-5ac1-b15f-754d1a07777b | note | Inspection/Test Method - Verify
e5a44b90-a2dd-5789-bd22-ed96d774abe2 | note | Record of conformity - Aconex reference This ITP signed
203a6394-9e8b-55e3-b454-137b1ed7160e | note | HP
3ba7f3a0-4385-5edc-bda4-f4bced7fdf97 | note | Responsibility - Project Engineer / Principal’s Representative
0557817b-f687-5567-b560-ef3a4b76354b | date | Date Completed:
40d34b22-12e9-410f-95cf-45c48b9e81e7 | signoff | AUTHORITY HOLDPOINT
1c1e652d-09e0-4918-ad23-daf1c74bc0cc | checkpoint | 1.5 - Methodology
c4e5bb14-dcfc-5429-905e-486592ec573e | note | Frequency - Prior to commencing activity
25875e28-5521-5d9a-bff1-46c7f7334c2f | note | Acceptance Criteria - Prepare and implement a Methodology that includes the following at a minimum:
1fac605b-b0e9-5da9-8bed-3e64d62c3632 | note | – Full details of the steps to be taken for the underbore works; and
07e46cbe-1259-5bc2-828d-d0da7fc29042 | note | – Details of equipment to be used.
5ef0eea1-08f6-5c1c-ad38-7c0e3d1deefe | note | ○ This must be submitted at least 7 days prior to the commencement of site work
c7b48d2c-219f-5a42-b959-5aba0646338c | note | Reference Documents - ZULU-BECA-001-SPC-00004
9005ee01-e0e2-520e-9c54-cc7db47d6db6 | note | Inspection/Test Method - Verify
89f49906-aeab-5dfb-9f24-c5ff47b11624 | note | Record of conformity - This ITP Signed
feec2805-9347-5a5f-8850-ae713c11e28b | note | HP
c3bf587b-51c5-5c29-8d96-499045132975 | note | Responsibility - Project Engineer / Principal’s Representative
802a744d-5d88-51ee-a4e5-320de14e8643 | date | Date Completed:
11d9840d-c7a3-478a-8e1d-f0bc43d0f045 | signoff | AUTHORITY HOLDPOINT
237d8f23-d932-4e1a-a619-6be77c884cfa | checkpoint | 1.6 - Locate and prove existing services
a8216cb3-1b29-5ab3-8052-853646695259 | note | Frequency - Prior to commencing activity
e8ee3b84-9831-5338-b685-722cfc90c623 | note | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
ddb38a73-fe74-568a-b554-8d29c31f9b7f | note | – Contractor to obtain excavation permit from APAM prior to any demolition works.
4059bfa4-2d34-58bf-8671-4aa124a815f1 | note | – Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
8be4cfe0-9f45-5b74-8ac2-9d07967b1163 | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.15
c9616e44-bfd5-51e2-85ee-b0147e4962ae | note | Inspection/Test Method - Verify
d83d4485-e6dc-5ea9-bf1c-bc7edabbc5c2 | note | Record of conformity - Melbourne Airport Excavation Permit
43fd562f-805b-5bf3-bcd1-2d1ad15929db | note | HP*
32363155-b144-578a-92ca-e576d638b1f0 | note | Responsibility - Project Engineer / Surveyor
a06f6d05-e6ed-58e4-ac7e-cea6566b3240 | date | Date Completed:
dbe230e1-8c49-4353-9c66-454e99afff55 | section | 2.0 - Construction
95a05716-6f49-49d1-9154-913f03de96b5 | checkpoint | 2.1 - Excavate trenches for Entry and Exit Pits
686c449f-56be-5291-967a-e75169edb20a | note | Frequency - Each lot
ec58db07-ca1a-5ebf-9d8d-8315a9b6343a | note | Acceptance Criteria - Trenches for entry and exit pits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
c25550dc-47f9-57d9-99e1-17155a84781b | note | – The level at the bottom of the trench shall not be above the required level at any point.
991b7411-471c-5aa3-9a15-9ae3de8e844e | note | – Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
98a952ca-5afc-5492-9fc1-6948a43f0458 | note | Reference Documents - Drawings ZULU-BECA-001-SPC-00004 cl. 3.6
396c5c05-ed8a-5c44-9784-3dcc16e65fe0 | note | Inspection/Test Method - Visual inspection
ca7f27c8-47f7-5599-b5b1-0d5801a1510d | note | Record of conformity - This ITP signed
517c0393-3370-5c30-99e6-f61683e0d559 | note | IP
98fe19c7-7845-5348-b10b-b42d18175b10 | note | Responsibility - Project Engineer / Foreman
706104a7-b532-5398-ba53-6c9cf0ce3ba9 | date | Date Completed:
d05caa38-7965-4f4b-a2c0-9ccf70697fb7 | checkpoint | 2.2 - Existing services crossing new conduits
8cf2c76d-d351-5897-a313-880e01d8d078 | note | Frequency - Each lot
8c9bc625-6825-5989-a71c-43e45d0a5ba8 | note | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
a0232d63-2440-5bde-9df4-0c35fb362a99 | note | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
48bb5b33-b1ee-5f40-b555-ada1832b0fef | note | Reference Documents - WMS002 – Working Near Existing Services
8d0cf3cb-d4e4-5455-ba17-705f671386cc | note | Inspection/Test Method - Visual inspection
d79661f9-e176-58d1-a939-9c9ab5af8d3c | note | Record of conformity - As-built survey report
837479af-7c03-50e4-8545-6c66c2af19a7 | note | SCP
1dabdde8-ed9f-5807-911f-5591df133963 | note | Responsibility - Project Engineer / Surveyor
fe7fbaf5-1f6b-59f6-b347-ee6c6c1a34cc | date | Date Completed:
b55e9f73-72c7-4b27-afdf-e5cda015f1bf | checkpoint | 2.3 - Survey as-built
c91f79ce-676d-5b56-bb34-1e31f99c5042 | note | Frequency - Prior to backfilling each lot
a4d26a17-4845-5b97-93cc-b0b0f444d0ae | note | Acceptance Criteria - Surveyor to pick up completed conduit runs
40e53e11-5ea4-57e2-8e00-b5d25048d12d | note | Reference Documents - FH QMP
ba82ad69-493c-58f3-864c-3082d71c52e4 | note | Inspection/Test Method - Verify / Inspection
28fc3ee0-d912-5087-abd8-44fc4528dc38 | note | Record of conformity - Survey report
e68205fd-517d-5409-9304-061840ca6721 | note | SCP / IP
73202358-8197-55d7-9f44-5753f724e472 | note | Responsibility - Project Engineer / Surveyor
6263a239-dcb6-5fe9-bee0-8ce279363cac | date | Date Completed:
54db02b5-57c6-4391-bb41-0211e766da10 | checkpoint | 2.4 - Cover
b16395e7-6fc5-5972-b03d-78cbfbb000d9 | note | Frequency - Each lot
25feb980-cf61-53ab-821d-a9e2468f8660 | note | Acceptance Criteria - Services installed under road and taxiway pavements and shoulders by under boring must have a minimum cover below the surface as shown in the drawings.
c7d5181b-f22b-59ed-b98d-4d0dc3e977f6 | note | Notify the Contract Administrator at the following stages of construction:
be157b8a-03c4-5e5f-b712-b060c91c957b | note | – At setting up for the commencement of drilling; and
b3c89995-374a-5e36-8377-1e7587296aa6 | note | – At completion of drilling prior to connection of ducting to pits and backfilling
0327f377-edbe-57b9-9a8b-aa1395f9ec7f | note | Reference Documents - Drawings, ZULU-BECA-001-SPC-00004
dcac4b05-5629-5b30-8e30-ec177ba30132 | note | Inspection/Test Method - Verify
cc44090c-f732-5a51-8da5-c3bb91895ebf | note | Record of conformity - Test report Aconex reference, This ITP signed
3617394d-9a26-5174-be97-5e31cfc5958f | note | HP
ac16a190-8944-5ac0-88a4-1b820c4f6835 | note | Responsibility - Project Engineer / Principal’s Representative
ba41df33-3667-5308-81ec-0ad91f909b2b | date | Date Completed:
09b1a7ab-4988-4f4e-83d7-5bf6e52c2670 | signoff | AUTHORITY HOLDPOINT
a2393ced-944b-458e-8af1-36418a08136c | checkpoint | 2.5 - Conduit draw cord
b453fe96-68d3-579a-ab20-9fc4a46a2f50 | note | Frequency - Each lot
76c513a4-1a74-55a6-b40c-17cd7eb814cb | note | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
f8c625a1-18f9-577e-bde9-c3015de6ee3a | note | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.10
b40c5c56-a51f-50fa-b36a-248bb853cbb1 | note | Inspection/Test Method - Visual
62fc937a-c367-5f55-bcab-934b1a0c9918 | note | Record of conformity - This ITP signed
86d9371e-5255-5336-8323-93fee565e904 | note | IP
44559499-2f22-5a5b-8a35-a7bb8f5710bf | note | Responsibility - Project Engineer / Foreman
18f27341-aaee-5895-ba9c-807e0a1036b0 | date | Date Completed:
f31bfbfb-bda3-4ed4-a964-defed583f84f | checkpoint | 2.6 - Grout
30c37451-82ca-5273-9af7-4dc06c9cb8bc | note | Frequency - Each Lot
6c9ff11a-7526-5071-b3c7-149152e59e9b | note | Acceptance Criteria - 1. Verify that pulling back of 63mm diameter grout lines are limited to 10m.
a67aefb0-9b97-5a6e-9427-8142592f1333 | note | 2. Measure volume of grout used per pull back to identify where full encasement may not have occurred.
e1d5acaa-210c-5291-93d8-a3da69aa3784 | note | Reference Documents - DCWC Mgt-CONTIN-000853
e71a527f-d8d4-5e16-9495-5acded646ec8 | note | Inspection/Test Method - Verify
f7bf587a-f081-56e1-b79c-dce078d4860c | note | Record of conformity - This ITP signed
710a10ba-198a-5506-9b1f-a616b9a9468a | note | IP
7f082b04-28dd-5541-ab37-bf8e3029fbd3 | note | Responsibility - Project Engineer
e3665cb0-8a64-57a0-9d47-b236b6ac3bfa | date | Date Completed:
4feae5f2-ef45-4abc-9b89-190686aed4d0 | checkpoint | 2.7 - Bore Logs
f20aec68-ad33-584d-bdc9-ca94b7d20bdd | note | Frequency - Each Lot
1cf635ce-8018-58f1-b451-6aa4ce559c43 | note | Acceptance Criteria - Submit bore logs for the underbore
e764a2b8-7242-5335-bf79-95e38ed83c81 | note | Reference Documents - ZULU-BECA-001-SPC-00004
7b3529b8-1fa1-55b0-8182-2019641d2d01 | note | Inspection/Test Method - Verify
c017e335-524d-5683-9e07-b783034db6c1 | note | Record of conformity - This ITP signed JLM Borelog
722a52df-3377-5d10-913d-4ca809e2ee17 | note | HP*
bf9311e8-993c-582d-a842-e2d25fb46893 | note | Responsibility - Project Engineer
daf10916-402c-5ebc-97df-3c85381374fe | date | Date Completed:
fd8db534-8151-4f78-9713-0afd67efe047 | checkpoint | Final Inspection
36a76881-262c-5507-9686-ce76864e1264 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
87a7b0b4-a4c0-5539-a492-03b4962effbd | textbox | Print Name:
ed54656c-8099-5a22-a661-ccf1834e7219 | textbox | Position:
f02942b5-5b3f-5ea5-826c-002d5d54533c | date | Work Completed On:
9b29e317-e4e0-5d14-b289-e5defc57984f | date | Date:
d97f0d59-b93c-5191-a93b-57e1bf473bb0 | checklist | FH-ZU2-QU-ITP040 - AGL Pit Installation - Rev 0 | itp | ITP040 - AGL Pit Installation
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
93a3c36d-9405-521a-981f-c0e2f20861af | note | Frequency - Prior to start
8f81ed97-d054-58ad-83df-7bd70705e3bf | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
4acb2f82-cd70-5f2e-932f-efb2463644cf | note | – using the correct and complete set of drawings.
0f18b6ec-606d-52bd-8758-1a828ec9a50f | note | – all drawings are the latest revision.
a6514ab2-6b1c-5870-bad0-40911095837b | note | Reference Documents - Drawings / Aconex Register
24ce4b84-a465-5dcd-b5a5-ba1fb795ea18 | note | Inspection/Test Method - Verify
08e0dba2-b0f1-5910-ace8-6343b28d0b5c | note | Record of conformity - Drawings and drawing registers
e67b0def-bce4-5026-be58-258ae961d0b9 | note | HP*
c4f30c0d-24a8-5049-9c8b-3e58702e2c72 | note | Responsibility - Project Engineer
2ad62c75-b770-5f05-8546-e8dec48a678c | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
cb44b0ee-ddc3-59a5-9b01-fd796455120b | note | Frequency - Prior to start
a04b67ab-d134-534f-a12b-0ce3e1ec2961 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
32b1c5c9-92c0-57b9-b152-6da10866cd3f | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
eb80c0cc-4ae7-5468-9978-37b054b2ed94 | note | Inspection/Test Method - Visual Inspection
488ae265-0f75-5ebf-864d-20506f94586a | note | Record of conformity - This ITP signed
3338f42c-ed1f-5c39-ba8d-67191b026722 | note | HP*
45ba5fb6-9913-5512-910b-83373fcc3239 | note | Responsibility - Project Engineer
27c5d8b1-df3f-5a38-bb30-9fddf7a16688 | date | Date Completed:
ae6436fe-7531-56f0-a722-60b6fb9a6221 | checkpoint | 1.3 - Definition of the work area & survey check
21a4bd21-1d6f-5969-af07-a6cf15a0b448 | note | Frequency - Prior to start
382cbcf8-fcdb-5a4c-8e44-0f53767fded9 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
7967d7c7-151b-56da-a6f9-a13f3d54555c | note | ○ Ensure excavation permit obtained and (if required) services in work(s) area isolated.
e1fbbff1-43d8-5caf-b475-76f3a375d74e | note | Reference Documents - IFC Drawings, Excavation Permit
29fc7d55-3be2-5c93-ac6e-07fec38f05d9 | note | Inspection/Test Method - Verify
6554d266-2afd-5a6e-9811-3fb0dc801fb5 | note | Record of conformity - This ITP signed
f0167f8e-1fbc-55c1-b8d7-5b5a29db7ab2 | note | SCP
975ce107-a7b0-5ec1-b4fe-2846662d0894 | note | Responsibility - Project Engineer / Surveyor
aa08de9b-0d4d-5231-98e1-73a73ae08dea | date | Date Completed:
99f218db-300b-5379-a490-7ab3b2cd49e9 | section | 2.0 - Installation of SIT Pits
a3a9bb2a-fe1c-55a8-8745-a8c59cc3b6b8 | checkpoint | 2.1 - Pit excavation and placement
b1aa87de-8941-52c4-ae1e-cbd6c3386fe2 | note | Frequency - Each Lot
7f00b3ee-82cd-50a6-ab8d-da13544ebe19 | note | Acceptance Criteria - Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out.
88320882-d267-5c65-b0c9-ffeb4aa09f6e | note | Reference Documents - Drawings
a08ea9e6-e9bc-59bf-bd9a-3ca6a327682e | note | Inspection/Test Method - Verify
4b9e583e-e91a-5ab8-9cd0-98c0c8e8a504 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
498a3e52-d1e9-5c15-8635-8ede62e2ad61 | note | HP*
a1e6a782-300f-557f-935f-3b27a02f2b4f | note | Responsibility - Project Engineer / Surveyor
a39cfd65-f408-5691-b6b2-5bba04c37e05 | date | Date Completed:
0c5c50bd-1203-58f5-b22f-20573c0cc028 | checkpoint | 2.2 - Conduit positioning
825c3163-719d-514a-a4c5-6fb033ea5244 | note | Frequency - Each Lot
cb486f7e-0b4f-5291-8777-81c0ce18c878 | note | Acceptance Criteria - Primary, secondary and earth conduits (and subsoil outlet) positioned in pit according to IFC drawings.
7767da57-ad8d-5f4b-a0d7-f29a1e24c799 | note | Reference Documents - Drawings
0bd9bf46-de3d-5080-a48c-79e232dc507b | note | Inspection/Test Method - Verify
34dc86e5-6784-5fc5-a53a-2e12ad8b88a6 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
e34fe305-f865-5b19-943c-072efdcd8ec1 | note | IP
9310505d-1daa-593e-8cb6-72f741b454ed | note | Responsibility - Project Engineer
1982680d-1f45-5a51-ba83-79b92a3d18a8 | date | Date Completed:
092214eb-c6d0-5808-bbbf-c0491fc4b589 | checkpoint | 2.3 - Bedding and backfill of pit surrounds
4b186fa2-f184-590d-ad55-5105f504257b | note | Frequency - Each Lot
ca07663d-cc5e-56ea-a1ca-24222408e656 | note | Acceptance Criteria - Each pit shall be bedded and backfilled with stabilised sand.
eb30b916-c418-575e-a787-abbad059487a | note | Reference Documents - ZULU- BECA-001-SPC-00004
9fcc546b-8bb3-53d7-a3aa-38aa72c315ae | note | Inspection/Test Method - Verify
11eea8d8-40c8-59f6-a612-b9150f4527e1 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
3977f371-0ecb-5b6c-84bf-c2f351cf5af8 | note | HP*
951ea51d-91e8-54e2-ba6b-e51cd7bb4609 | note | Responsibility - Project Engineer / Site Supervisor
34932360-fa14-504d-acb7-5a8f9b3a809d | date | Date Completed:
0f3fde11-e097-5dde-ba07-77f40f8d8cac | checkpoint | 2.4 - Pit close out
11a6e9cb-0d23-5a95-b7f4-e5b658de2aa7 | note | Frequency - Each Lot
637cc6a6-2df5-5e42-8ed9-c4676b149da9 | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished.
070d84fa-0983-518a-b7ca-f09814c2b9a6 | note | Reference Documents - ZULU- BECA-001-SPC-00004
5f93bf0b-6961-5c0b-adb9-1335fe96ab69 | note | Inspection/Test Method - Verify
9499f1b4-8ea2-5dab-ad5c-70aec5570da5 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
7a970c99-db2b-5a0a-af7e-7e88c582fd8a | note | IP
b8ce93ae-69f0-5952-84d3-2632120a4018 | note | Responsibility - Project Engineer
3d54c413-8f03-51df-9bf9-49ec49b9a002 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
7d42f0e4-b240-5f8a-a1ee-10f6db69d435 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
34d9fe97-fdd9-5dff-8883-1161c772b954 | textbox | Print Name:
fc50cc42-87b8-565b-8c8e-57447d8be83c | textbox | Position:
4f666da9-4ed6-5496-b82a-dfcf4d3df362 | date | Work Completed On:
d1df7862-b616-5d7c-a8ce-c03826bac0c1 | date | Date:
6fcaf60a-5b72-498b-bbc2-d8dd3440f930 | checklist | FH-ZU2-QU-ITP041 - AGL Pit Fit Out - Rev 0 | itp | ITP041 - AGL Pit Fit Out
e3e69a5f-a70c-4446-a566-b4e2fa174f5f | section | 1.0 - Preliminary Works
e7aaeb7f-0529-4696-a275-e897e7645de9 | checkpoint | 1.1 - Check for Correct Documentation
9938f68c-882c-508f-ad9d-11628639465c | note | Frequency - Prior to start
b714c4d6-9600-5712-9898-30b23674da8f | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
60b4b1e3-465c-5c72-bfc9-baa57fb06ac3 | note | – using the correct and complete set of drawings.
d0fb0b9c-6e11-5e4d-93b0-8da374e5b87f | note | – all drawings are the latest revision.
d84e82dc-de29-5916-8d19-a6c733bdaa6c | note | Reference Documents - Drawings / Aconex Register
e26c7269-157a-5718-adc4-f0ac4c1bc4ad | note | Inspection/Test Method - Verify
4903ca76-4a3f-5cac-aaf3-85e29e3cbf50 | note | Record of conformity - Drawings and drawing registers
96078eea-8943-517e-80e1-bdc4a287ec8d | note | HP*
34e8073f-7486-5397-a512-794fbe4cc99f | note | Responsibility - Project Engineer
cec84d2d-925c-5b24-8c1a-b017769d315c | date | Date Completed:
6146396d-1a46-4094-97fb-ba388a4e8a22 | checkpoint | 1.2 - Implementation of all measures and controls
7bd9dd9e-4534-582b-92fd-9ccc10748c3f | note | Frequency - Prior to start
b1bb67cb-d279-59f5-ad30-946cbb48d2b4 | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
696e5f06-8a98-5803-bad0-5a0c8e82ff38 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
388684ad-2125-5cc0-bb03-241f35fe7073 | note | Inspection/Test Method - Visual Inspection
f9904c9d-5f7d-528c-9f87-2c27e410902d | note | Record of conformity - This ITP signed
43575bdf-8acf-526c-9c28-8b0cdbc04d17 | note | HP*
e34f371b-71a7-53ba-873f-aa2e586d7814 | note | Responsibility - Project Engineer
e0601152-d3ff-5baf-9c2c-9bbd361ab10d | date | Date Completed:
2c0efefb-7cd1-4f97-b240-1c3d0f558a3d | checkpoint | 1.3 - Definition of the work area & survey check
631648cb-134d-58fe-8769-03ca5b4be7f9 | note | Frequency - Prior to start
d90d03cf-7739-563a-bf5b-53bc033b4d0d | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
fe44393b-1844-5e6a-a188-935c01dc9b95 | note | ○ Ensure excavation permit obtained and (if required) services in work(s) area isolated.
cab015bc-7680-57fe-845c-c048ac04dd60 | note | Reference Documents - IFC Drawings, Excavation Permit
3084b2d7-059e-5bf5-8064-caaae1c50503 | note | Inspection/Test Method - Verify
d3fe0067-82f4-50e5-839d-1ef64c96f5c2 | note | Record of conformity - This ITP signed
8b509f8a-f7b4-5472-bc69-1cd67ac5934e | note | SCP
4293ede1-c836-5f07-b535-f25cffc15416 | note | Responsibility - Project Engineer / Surveyor
fc62d973-7c89-55bb-9e15-ec0a17b6553c | date | Date Completed:
d9cb289c-630a-4663-8648-e8115dd48b9b | section | 2.0 - Installation of SIT Pits
c6de2c07-9046-4eba-ac99-fba960383690 | checkpoint | 2.1 - Pit excavation and placement
46d02a2b-6f3c-5bb3-9b5b-a52faa18e168 | note | Frequency - Each Lot
92fabfd1-db51-545a-acb7-3288ecd20709 | note | Acceptance Criteria - Dig zone marked out and excavation undergone in accordance to relevant permit. Pit placed and levelled as per survey set out.
8b0a9d5f-031c-5ce7-9b9c-56ad7605db06 | note | Reference Documents - Drawings
0d8dfceb-476a-5669-bc3a-2a910430e082 | note | Inspection/Test Method - Verify
a10c07e1-e046-5159-a94d-f438fc6cbea0 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
202cd08c-487a-5e71-9be9-4aedf30172e7 | note | HP*
2086ca64-7529-53fc-8c20-e1cc464d745d | note | Responsibility - Project Engineer / Surveyor
2057c85f-4e75-5e26-a67c-f93fef89c724 | date | Date Completed:
9fdb35ba-57aa-4b97-b10a-9a2d468de54a | checkpoint | 2.2 - Conduit positioning
ec15a841-1601-5cfe-bafa-de9c2dd4acea | note | Frequency - Each Lot
4f3193bc-ce44-562f-876d-e46321dccb1c | note | Acceptance Criteria - Primary and secondary conduits positioned in pit according to IFC drawings.
85a0747b-7a86-5688-9539-37c08398028b | note | Reference Documents - Drawings
9a23f126-f192-5b1a-a6e9-f77426dd8e03 | note | Inspection/Test Method - Verify
dda215bd-412f-5d4b-8895-eb96c5a5abbb | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
4895e570-adf7-5f74-9847-fc548a3726f8 | note | IP
09ae9fea-ff2c-53c3-8010-d6e7da0b3963 | note | Responsibility - Project Engineer
641f6876-1650-5382-b06c-b717d5532769 | date | Date Completed:
ba3f0693-c4db-4a77-a128-89ba8a2b53ec | checkpoint | 2.3 - Bedding and backfill of pit surrounds
53e79679-3522-5863-9d39-3a4a90e0728b | note | Frequency - Each Lot
3983aa13-74be-5a74-a15e-8827c1e5e8ed | note | Acceptance Criteria - Each pit shall be bedded and backfilled with stabilised sand.
5a70875a-0728-5481-82b3-8324c8b09f3d | note | Reference Documents - ZULU-BECA-001-SPC-00004
d477dc77-566d-5c08-82fe-e6e61405476a | note | Inspection/Test Method - Verify
9d3e6f21-0fe5-5af2-ad5c-f99dcce19350 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
a748e5f6-e463-5e0c-ad88-186be65c6b42 | note | HP*
99dcf07b-ed8c-5197-a202-1b7a8ddf420e | note | Responsibility - Project Engineer / Site Supervisor
9b98b593-8e9f-5a2a-b420-9f8eabe29c0f | date | Date Completed:
5ea599e7-59e4-44c8-b4fc-62fd23f4b41a | checkpoint | 2.4 - Pit number labelling
73368c57-aa68-51fb-986e-701110f35720 | note | Frequency - Each Lot
89d708e7-39da-58e5-8194-136b2b3f9fe4 | note | Acceptance Criteria - Each pit shall be painted with the pit number with black waterproof paint on the inside and top half of the pit wall. Characters shall be 50mm high.
970ff74b-98bb-5ba5-bd2c-8bac754f52b2 | note | Reference Documents - Drawings
18249689-3ead-5a24-a946-20382347f0c9 | note | Inspection/Test Method - Verify
c48f05a7-d5e4-5d5f-ac31-c140589a0449 | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
84f6a03e-3d4f-5050-acf7-c92f299a4929 | note | IP
609eefc5-6c61-51bd-8c78-bb8cdb190242 | note | Responsibility - Project Engineer / Site Supervisor
08e2f6d3-f96b-5b45-9de6-98ff11101a89 | date | Date Completed:
624f5035-07a1-4abc-81af-a7fa12f7fcca | checkpoint | 2.5 - Pit close out
8c1de8f1-1e5b-5cd7-9384-26bf8396e388 | note | Frequency - Each Lot
2ce581a7-5bc5-52c7-9734-449fcb2cdb53 | note | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished.
61cf3af4-2577-5385-aa1d-b3b84f2f0ea0 | note | Reference Documents - ZULU-BECA-001-SPC-00004
43dc711a-7110-551b-b6b7-31aeb55d22bb | note | Inspection/Test Method - Verify
073b2afa-590b-5438-b9d8-5bd029a50e6b | note | Record of conformity - This ITP signed, Avionics SIT Pit Installation checklist
6a216ef2-e2a8-51b5-b25f-2c101bafe9ef | note | IP
42c8065f-ed43-5adf-a0d0-318afa8fa8f8 | note | Responsibility - Project Engineer
a8d66af0-0537-5897-a7ca-c4f8c668949d | date | Date Completed:
339df2dc-42e4-41c7-a001-35dd364e219e | section | 3.0 - Earthing & Fit Out
4c6333f2-193e-454b-8403-9b5f4651360a | checkpoint | 3.1 - Earthing & pit fit out
f3d6b092-136d-5a2c-87fe-b817e5d966ff | note | Frequency - Each Lot
f77b8688-e7b9-50af-b1eb-6082b714a092 | note | Acceptance Criteria - If no SITs:
360d29a9-ee56-5324-96ff-ed2a6033a09e | note | ○ 16mm Earth Cable Terminated From Earth Rod to Earth Bar
424d18a2-9da0-58d1-b77c-00eb9b528e59 | note | If pit houses SIT:
fe9454ef-1256-5b03-95a0-400a66a31bcb | note | ○ 6mm Earth Cable Installed From Earth Bar to SIT, 10 holes to be pre drilled into Earth Bar
1e56f727-cfc9-5dc0-b751-d5ee8b148475 | note | ○ SIT Mounting Tray Installed
554ea88c-cd51-5b11-83b1-0c0fe951ed1e | note | ○ SIT installed on the same tray which supply different circuits to have a 300mm gap clearance (Second tray to be provided if 300mm separation cannot be achieved on a single layer)
bbac32b7-579c-591c-bb1d-2689279708a4 | note | Reference Documents - Drawings, ZULU-BECA-001-SPC-00004
b1f07e2c-f391-5299-83b8-b735169f6302 | note | Inspection/Test Method - Verify
5446aafd-2955-59ab-b34a-511705f0f118 | note | Record of conformity - This ITP signed ADBSG, Earthing & Pit Fit Out checklist
6bfb6867-ce1b-50a1-a6bf-bfee2455b759 | note | IP
471e6096-fc6d-53c5-a2ba-838d641696a9 | note | Responsibility - Project Engineer
8ceb9e9e-49ff-5d4c-8717-ac85fd8d1f9c | date | Date Completed:
e018c3b9-6d65-45b1-aa32-71cd4f29f521 | checkpoint | Final Inspection
3ff28426-670f-54ba-bb5c-51f3db742023 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
805cbee4-258a-5d83-a469-0d55f38a61c6 | textbox | Print Name:
abf44f54-d65a-5244-bdbc-dea7376f5af1 | textbox | Position:
87faa2b3-1f35-5e73-866c-429725f22dd5 | date | Work Completed On:
1339a5b2-c4f5-5f49-981d-d6bbddad505e | date | Date:
5d3de49b-e505-5ec6-a691-69b12b12bf06 | checklist | FH-ZU2-QU-ITP042 - AGL Shallow Base Cans - Rev 0 | itp | ITP042 - AGL Shallow Base Cans
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
c2322c0b-6788-5c16-a6b2-b5f52c3f4b1a | note | Frequency - Prior to commencing any activity
582e3dce-a077-5116-bcb1-896a02192280 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
e3466404-cd66-5ad3-816f-0b07f2710d0a | note | Reference Documents - IFC Drawings
e0254087-d69f-5d9e-b0cb-32aaaa397665 | note | Inspection/Test Method - Verify
9672afbb-f6c7-55d5-be1c-0648961a7f7f | note | Record of conformity - Drawings
1f7997ad-9e29-5091-99ce-a1541b6d5d23 | note | IP
0f48af26-3a1b-5468-b326-e04676008e08 | note | Responsibility - Project Engineer
17a5140c-a227-53b6-bb1b-930c20c4a914 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b1c8abe8-5e01-5fce-ba7d-ae2080b43e87 | note | Frequency - Prior to commencing any activities
d13eb50d-6a5b-516e-8197-610276251445 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
75185538-73d0-5990-9d9d-4de1b0ad90f3 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
abf06095-7bf1-5c21-bbc7-171952b56fb6 | note | Inspection/Test Method - Verify
f78c7b91-f167-5da4-979c-0d175be305cc | note | Record of conformity - Site and office Inspection
dea835b8-8a32-59f0-beb9-f1d6afb64e7c | note | HP*
492d3161-69b5-5d5c-b5c3-3b0b54bb4fda | note | Responsibility - Project Engineer / Site Supervisor
1a761cb6-1739-5231-a304-1740c04bfc65 | date | Date Completed:
de40263c-b7c8-53dc-ae47-1287cd4a5c25 | checkpoint | 1.3 - Material/equipment approvals
f50cddb5-c152-5829-b45b-46febd125cd2 | note | Frequency - Prior to start
9b9f59a6-e8f0-53ee-84c8-344032349d0a | note | Acceptance Criteria - Materials and equipment that shall be used in the construction of the works as nominated on the Drawings.
d3e7a9b1-4753-514a-acdc-719b7b8baabd | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
deaae5fc-d4fd-5b67-b374-f50cda576d3e | note | Inspection/Test Method - Verify
60f0ecfc-7eda-5125-9186-7f4484e139e7 | note | Record of conformity - Aconex reference(s)
afb90af9-7b48-57f7-97f4-dfe8a2d92a0c | note | HP*
45e049bc-b21a-55b3-85f9-28c9957fe7d6 | note | Responsibility - Project Engineer
13a07e97-e873-5875-8467-feebff81f3cb | date | Date Completed:
37da4ca4-9059-5f77-8956-6bc7d9cb93e3 | checkpoint | 1.4 - Setting out for airfield luminaires
05c67439-9b8e-527d-aa6f-d013651a46bf | note | Frequency - Each Lot
05e3861b-0b08-51b9-9b46-9486ebf45c5c | note | Acceptance Criteria - HOLD POINT
77631a20-328d-56ae-ac12-a64728a96660 | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
0a596d91-2dfe-5bc6-8fe7-22f2ae1fd00b | note | Reference Documents - ZULU- BECA-001-SPC-00003 cl 5.4
5a1db113-abf6-5054-9267-2175089641f7 | note | Inspection/Test Method - Verify
273ff0cc-a6d6-5d2b-a98f-307add13e94d | note | Record of conformity - Aconex reference
f2c6079f-dc6c-5b72-b54e-628f8ee13d59 | note | HP
126f27ca-e90c-5898-937b-a1d6cec09c28 | note | Responsibility - Project Engineer / Beca
29a46fe9-1a00-5314-8e2a-9ffc79f66e50 | date | Date Completed:
96ed5756-8212-581a-b233-9f7850a3696d | signoff | AUTHORITY HOLDPOINT
8c74635c-11ca-5e3f-b186-c4ce6584e1d4 | section | 2.0 - Removal of Existing Can
2ddc3560-ccc8-54c3-96ec-d2cba7a29714 | checkpoint | 2.1 - Removal of existing AGL can
430c3dec-bc91-534f-a831-530fce96f995 | note | Frequency - Each lot
7a4bcd73-9144-5287-9688-89bdb8158b09 | note | Acceptance Criteria -
09135dc2-cdfa-5033-bc59-d13b78cad3e4 | note | Reference Documents - ZULU-BECA-024-DWG-07513
d45ff866-c0a6-5483-91bf-ae3aeca5db68 | note | Inspection/Test Method - Visual Inspection
a3ae43c8-d83d-5aa1-b568-4ffd04218050 | note | Record of conformity - This ITP signed, Avionics Removal of Existing Can checklist
09d4764e-d758-55da-92a6-c02dd52b601e | note | IP
cf42774b-72d0-56f3-aaac-ec33b6793345 | note | Responsibility - Project Engineer
9753c511-dbf4-5b88-a085-a690b4c87e47 | date | Date Completed:
17b9e06c-4a3e-5c10-a953-5d92439f9591 | section | 3.0 - Installation of Shallow Base Can
8226183b-768c-53b8-93be-03436d29a4a4 | checkpoint | 3.1 - Inset luminaire base can
07f4f2fd-e8ed-5279-8e03-7dc69393e65c | note | Frequency - Each lot
ba6cec38-004d-54e3-81b3-9f937287b7f2 | note | Acceptance Criteria -
756cd43f-e403-5130-92bd-300646fcb8bd | note | Reference Documents - ZULU-BECA-024-DWG-07501, ZULU-BECA-024-DWG-07506-8
4648c9d7-554a-5a50-81a0-f4f9d000642d | note | Inspection/Test Method - Visual Inspection
f49a4d2f-8208-586d-ab8d-d784a61594c7 | note | Record of conformity - This ITP signed, Avionics Shallow Canister Installation checklist
eb7f1abb-7df6-5b5f-af4c-4a31f7d1d498 | note | IP
d81b5b99-8c22-5f87-8dc3-7e2b103720a5 | note | Responsibility - Project Engineer
abf7e728-7c3b-5bc4-93ab-576a1813ccd6 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
59e9a41a-9eca-5958-a226-24d2700db36c | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
e1bf6fce-a9da-5ac8-a650-36374942bd25 | textbox | Print Name:
acbb9cd2-1435-5789-a7ee-fbc848bcf068 | textbox | Position:
24ac43bf-4f9d-5dd1-9a2e-d681c5f24931 | date | Work Completed On:
86ff4a10-6933-5b1a-9f8b-9d3c47bd350b | date | Date:
b1fdc53a-5ffc-4304-888c-9ffc226e0e7d | checklist | FH-ZU2-QU-ITP043 - AGL Deep Base Cans - Rev 0 | itp | ITP043 - AGL Deep Base Cans
e6cc6117-6ed6-4dfc-87ed-ba1cfc18e02c | section | 1.0 - Preliminary Works
a50f456f-91f7-4961-9d53-faa865dbb952 | checkpoint | 1.1 - Check for correct documentation
5074af79-1571-5ec8-8010-37d63cae3c7f | note | Frequency - Prior to commencing any activity
c08ead4f-d9ad-5c73-85bc-dc6bb085aa50 | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
4fb23805-6d69-5c73-aa34-206b158af6f0 | note | Reference Documents - IFC Drawings
2d53516b-c556-5b2f-a16a-c424a8b0ba06 | note | Inspection/Test Method - Verify
f2d4e1b9-2b76-5ed5-8876-05e7fb2144ef | note | Record of conformity - Drawings
3e2d0df8-7f93-5c6c-ba4c-6883f2385680 | note | IP
6a5bc82b-f5d1-5275-8d3f-ddaaf1b48428 | note | Responsibility - Project Engineer
b9a184ed-c40d-584a-afb7-92b701458484 | date | Date Completed:
1cf67ab2-fea9-4a6a-8de5-c244f63269e9 | checkpoint | 1.2 - Implementation of all measures and controls
1519c568-7584-5746-abcf-2e2ac85ad298 | note | Frequency - Prior to commencing any activities
3d2aba6c-6ade-536d-8d53-2e0db144331b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
64dbe181-56ff-526a-a607-2b0d427ae2b5 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
1f2cbc98-56de-5050-bcd7-42c78796631f | note | Inspection/Test Method - Verify
40190f73-d45c-536b-9b7f-ae4196ab03e9 | note | Record of conformity - Site and office Inspection
be40eae5-84e1-5ea5-bf0a-1d7a44cb1bc2 | note | HP*
76ee91c2-9ba2-5408-8169-c5564cf3dfbd | note | Responsibility - Project Engineer / Site Supervisor
986e0914-1a4e-5c55-b895-68fefc9a6a5d | date | Date Completed:
47eb3408-405f-4ab4-9ff4-92f62840c625 | checkpoint | 1.3 - Material/equipment approvals
4eac630c-59b4-593b-a7e8-fa0956d40e38 | note | Frequency - Prior to start
5f5c0080-c594-5ca4-bb4e-22f72dfa8ea9 | note | Acceptance Criteria - Materials and equipment that shall be used in the construction of the works as nominated on the Drawings.
67fe21ee-290e-58a3-b537-6511d20f09ec | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
b5cefb43-4b29-52c8-b35f-d856f28a20b5 | note | Inspection/Test Method - Verify
8a2b08da-02e4-5033-b72a-8e4155cee58d | note | Record of conformity - Aconex reference(s)
f4d67820-e7a5-57d4-8606-84cc77c9f6ff | note | HP*
05b11070-956e-5d53-b591-884f55f777c6 | note | Responsibility - Project Engineer
f8ef6f06-1915-5764-bec0-95038c0b9bde | date | Date Completed:
ae597d14-9ea5-4676-8246-bd51e6d3105e | checkpoint | 1.4 - Setting out for airfield luminaires
4ecb2dd0-d6f1-5fe8-ac17-96306aa05e86 | note | Frequency - Each Lot
2a0ba7ba-ce99-5303-bc90-ed5ffb0cc54d | note | Acceptance Criteria - HOLD POINT
2d05ec6b-d338-5f73-a3c3-4410b4316d9d | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
254c23e8-d466-55b7-b73f-9c7c12ad53cc | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
ea11f233-3f36-56cc-9d6b-6facb8a598ed | note | Inspection/Test Method - Verify
18dd6fd2-57ef-59d4-923d-5d6b20e5a06b | note | Record of conformity - Aconex reference
5b0768e2-c8a9-57a8-aaeb-f7882ac1d8e4 | note | HP
ee8979ef-7d0f-5ace-9c7c-b2cbae159de1 | note | Responsibility - Project Engineer / Beca
72e770f6-622c-55f1-bb54-6ecc73e288e4 | date | Date Completed:
8133b17c-5508-4afb-abea-8df67e051dc9 | signoff | AUTHORITY HOLDPOINT
a75122ca-44f2-4ed7-988c-d39fd75e70c1 | checkpoint | 1.5 - Installation of Initial Light Base
14849f58-2a58-5787-ae50-51668b27dfc7 | note | Frequency - Once
fe4e759e-d670-59c8-8f1d-52f3cb8bb9db | note | Acceptance Criteria - HOLD POINT
4f690bff-f3f5-5081-be85-cea430784fae | note | ○ The initial installation of the light base shall be witnessed by the Contractor Administrator
f3f105b7-3586-5616-a4d3-b9c5df50aee3 | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
a27a3526-4e65-517c-9f62-d1bf251c55ef | note | Inspection/Test Method - Visual, Inspection
0a75a122-9858-5937-9668-4fbbc8f33a94 | note | Record of conformity - This ITP Signed
00fd9954-2160-5097-b0e3-95199a1d4655 | note | HP
6d118091-c10a-5348-bcdb-ba12ac1878a1 | note | Responsibility - Project Engineer / Beca
3831a8d9-8183-568d-b639-55f6b8f0c159 | date | Date Completed:
568e7e69-ebfe-4a01-9a9b-5fa7bd6d5448 | signoff | AUTHORITY HOLDPOINT
80883239-f8e8-4a50-b726-853a96322501 | section | 2.0 - Installation of Base Canister
93670678-455a-4f17-a58c-8bb2fcdf2eb0 | checkpoint | 2.1 - Steel Reinforcement Mesh and Reo Cage
73e50650-31ec-5fb4-804d-f9fa311d004b | note | Frequency - Each Lot
d82cbaf2-e9e8-53d5-8d55-a773ea8cfdb3 | note | Acceptance Criteria - N12-150 steel mesh installed on both direction with 43.5mm cover.
df54a1af-ad32-58b1-9276-b6733d555337 | note | ○ N12 reinforcement cage to be installed as per AGL details
27433d2e-5a21-51bc-abc3-50ad8f5b3345 | note | Reference Documents - ZULU-BECA-024-DWG-07506
2c281575-5f59-56cf-8dc9-1df83d3e65e2 | note | Inspection/Test Method - Visual Inspection
418cf77f-9c27-58be-8816-b9ec18c2391f | note | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC
a3b734d1-65fc-5423-a41d-8a2aa8e6ac0e | note | IP
f878d91c-00da-5a14-b967-dedbd39214cf | note | Responsibility - Project Engineer
a256e952-b782-52db-b17f-4e3c5f3cf47b | date | Date Completed:
dcb518d8-6c3a-40f1-bb12-b96def728c68 | checkpoint | 2.2 - Base Canister and Conduit Installation
0065f323-13a1-50eb-87ed-437306a2b60a | note | Frequency - Each Lot
d8602f9e-cfdf-5432-8667-5850a9c2e4b0 | note | Acceptance Criteria - Concrete encasement for electrical conduit shall have a minimum cover of 40mm.
048453c5-ffb8-5867-8844-d70ace2c11ae | note | – Ensure bottom of can is 200mm minimum to the bottom of foundation.
30077fec-9c72-5967-a178-01fb8286a7d0 | note | – 700mm x 700mm 40MPa concrete foundation
539e29ef-e4c1-5212-a67d-614716a5ff64 | note | – Compressive Strength Test Sample to be conducted per 50 m3 of concrete
3fffc3a7-8f5c-5462-9bf2-e67dd43469f6 | note | – Install 19mm plywood cover with mud plate (sealed and bolts torqued to 40NM)
28887fa0-a15b-5276-bf47-d90c1879c5fa | note | – Check the elevation (RL) of the bottom canister (top plate) relative to the FSL of PCC concrete.
0cab612c-4ddc-5fd0-b6d7-d05f6aaba59d | note | Reference Documents - ZULU-BECA-024-DWG-07507
114e331b-cb96-5dd7-836c-aa5cfe4846a1 | note | Inspection/Test Method - Visual Inspection
d98c9ced-9dc7-5ee6-9f59-4c26ebf252d7 | note | Record of conformity - This ITP signed, Avionics Base Canister Installation ITC, Concrete Test Results
6d64a834-09e5-50a7-96f2-e90ff797dd3a | note | IP
8c0a43ba-1c92-5777-93cf-1abf5a22f325 | note | Responsibility - Project Engineer
4e62385b-debd-5d73-9a4a-d8e696b977d6 | date | Date Completed:
a4bc4f18-5ef5-4419-85da-5787173044e1 | section | 3.0 - Installation of Top Canister
bb71c0a4-e382-4fb0-8564-aa54aa0e2588 | checkpoint | 3.1 - Top Canister Installation
b51ffc26-d3a4-5bd4-8194-accf3d0dc791 | note | Frequency - Each Lot
bc67bcfe-0872-5d28-8588-2a4c4962174e | note | Acceptance Criteria - Core pilot hole (150mm) down to target ring and establish exact centre.
742aa7df-b625-53bf-9c26-f7201df8f207 | note | – Core diameter of approximately 355mm
913dc5ca-f5dc-5271-bfef-8481053f85c1 | note | – Install top canister with spacer rings and dam rings
e51a8eab-e6ab-506a-aee7-d1d47bd41ce9 | note | Reference Documents - ZULU-BECA-024-DWG
ee4a8ce9-8ef3-5297-b123-71780a04b1c5 | note | Inspection/Test Method - Visual Inspection
529f1d5c-ce3a-55b1-b324-c819a6fcfdd4 | note | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
87565df3-27c5-560c-a315-2974be6ecb6f | note | IP
0fc7941d-2c87-5273-b62a-d30bbc66a3c6 | note | Responsibility - Project Engineer
84259f21-6b0d-514d-8aee-69203abf4f78 | date | Date Completed:
12e378cc-0816-41ed-9355-e6e2b08e644c | checkpoint | 3.2 - Top Canister Close out
f3600858-01a5-5554-8c82-c64c33317ff1 | note | Frequency - Each Lot
0b06a1e8-7ab6-5100-82e6-0045b918cd19 | note | Acceptance Criteria - Install bolts and tightened to manufacturer’s recommended torque using a calibrated torque wrench.
1c29aa2d-763c-511f-bb3a-cd5725b90449 | note | – Apply Webertec FG epoxy sealant to the void between housing and side of excavation
73e0db55-1628-54b3-8895-2fdca41f54c6 | note | Reference Documents - ZULU-BECA-024-DWG
889221e7-b290-5b62-b302-2f1ca5b279ff | note | Inspection/Test Method - Visual Inspection
f97c2aac-c16f-581b-8462-8252ea09a81f | note | Record of conformity - This ITP signed, Avionics Top Canister Installation ITC
030fa07f-961f-5847-9eac-cdbf2d492c24 | note | IP
e26fe6f0-0717-57c9-9997-5958bfcc2ccb | note | Responsibility - Project Engineer
5dfcc4e9-24ff-5452-8d17-09f6c0a7003a | date | Date Completed:
177e2408-5080-4356-a9de-c059a5fab9b3 | checkpoint | 3.4 - Elevated Luminaire Base
5c844d21-6134-5535-b315-cebaad799520 | note | Frequency - Each Lot
65e1fa80-ca79-5e1f-8713-44d02029cad8 | note | Acceptance Criteria - Installed and backfill in accordance with drawings.
7bb0efa7-3f7c-58ea-9cb8-9547c1f50bd3 | note | – Two piece deep base cans to be installed.
08526876-f80d-5488-b081-9ec6154b2fe1 | note | – Min. 500mm cover from finished surface to top of conduit.
86b3c4c4-d36d-5479-8bf0-7bdc77a089f4 | note | – Can fitted with frangible coupling and FAA type/secondary socket retaining arrangement plug and socket.
86fc4c5f-eb35-52e9-b52a-6c13afc83cfe | note | – Foundation and reinforcement installation to match Deep Can Installation for Rigid Pavement
f81a72f0-f127-5560-bb7c-0dca93952647 | note | Reference Documents - ZULU-BECA-024-DWG-07507
b1f1c133-54f6-59a0-a3a8-4d9706cd4544 | note | Inspection/Test Method - Visual Inspection
8ae34061-289a-5cdf-af17-98cf8de4a14d | note | Record of conformity - This ITP signed, Avionics Base Canister Installation Checklist
4dfa7517-d9e8-5af0-952c-3ccbd11c2ba3 | note | IP
58d199e9-125c-5a7c-83c2-31cd43907d1c | note | Responsibility - Project Engineer/Site Supervisor
c84a9d00-1e76-5e31-90ce-99bd34d40327 | date | Date Completed:
c458edb0-a87a-44ac-b39e-0a4ebe256377 | checkpoint | Final Inspection
3a394ce0-6732-5efc-8f4a-efa6d0cc5ae9 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
59e87fb8-765f-564c-a341-2d8585a02867 | textbox | Print Name:
fbfaeccc-44bd-5a0e-beeb-3d6ddca69a69 | textbox | Position:
203c876e-8d96-5b6f-a8a7-ba4c6abb1831 | date | Work Completed On:
601b9e4d-3f1a-5f75-9efe-76e455372458 | date | Date:
40cf46e7-9eac-49b5-a467-46b8a185e084 | checklist | FH-ZU2-QU-ITP044 - AGL Luminaires - Rev 0 | itp | ITP044 - AGL Luminaires
e5362d3e-440a-4c88-8ffa-301e7d7b852c | section | 1.0 - Preliminary Works
31e7f0a4-c455-4f88-a1ff-98420fc51895 | checkpoint | 1.1 - Check for correct documentation
a6e38f86-3110-5c45-b083-15de92494eb0 | note | Frequency - Prior to commencing any activity
844751bd-ae8e-53c3-ae3d-b6ecacf6334b | note | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
dd12bf58-1e2f-574b-b398-293c033c6389 | note | Reference Documents - IFC Drawings
41ea9812-c297-5ad4-946b-0f4baea30da3 | note | Inspection/Test Method - Verify
f178b106-5210-5f40-8710-817c32bbde6c | note | Record of conformity - Drawings
4d061b82-05ad-5073-be4c-cc006440bb66 | note | IP
fab5e148-9dbc-5f0d-aad3-b7fb6e1e5b2e | note | Responsibility - Project Engineer
db3fd7f5-4a6b-54c5-ab22-e906f30fae5d | date | Date Completed:
20524f49-2c79-4e24-8df5-549c4e2d321c | checkpoint | 1.2 - Implementation of all measures and controls
4777ae02-73c6-52fa-8d58-5792e59f7ef1 | note | Frequency - Prior to commencing any activities
8487d5b2-a3ab-5267-b4e6-b181ef8a825b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
034bebef-9f96-557c-831a-03a205998114 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
37b643bc-f822-5372-ba03-e0d57ea4e2f6 | note | Inspection/Test Method - Verify
8e79ae68-abed-5ea5-b836-957597c88a89 | note | Record of conformity - Site and office Inspection
e620c074-111f-57e4-9e99-341e6c1eb91a | note | HP*
c3c4c7a3-3f71-5b78-9733-e8d61ff8d786 | note | Responsibility - Project Engineer / Site Supervisor
3793b7ea-53ec-5e47-a52d-edd67a6accdf | date | Date Completed:
a98ed0a1-0267-4280-b1f2-b450e2ff58d5 | checkpoint | 1.3 - Material/equipment approvals
7ca5155c-68e2-59b4-b653-bd961ec5d417 | note | Frequency - Prior to start
f6f8eb81-3795-5365-afdd-df40efded5e8 | note | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
dcc589f4-e58c-5383-a871-1a18028d7f74 | note | – MAGS shall be from ATG Airfield guidance signs range
1b4cbea6-022a-5b39-8ab3-8120f28c116c | note | – Taxiway centre lights shall be
fa5df35d-d7f2-520c-b72d-da80e3239a09 | note | – from the ADB Safegate range only
c71627c2-9cd2-521e-ab5f-92dd802a73e0 | note | – Runway guard lights shall be from ADB Safegate only.
5025ee73-399e-5b3d-b8f9-4c7166f8f1a6 | note | – Intermediate hold position lights shall be from the ADB Safegate range only
8cad9a53-ea10-540b-acd7-aecad35af350 | note | – Stop Bar Lights shall be from the ADB Safegate
4ea0c8b3-595b-5f70-b383-2b7a38bec3fb | note | – IWDI shall be from ALS
6a9ed3cf-e8a0-54ec-adfa-b3a75cecca92 | note | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
d9ab9d92-e642-539c-9229-96bac8f37d1b | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 2.3
961ef6ce-e2a6-5863-80c8-a6e4f45c374a | note | Inspection/Test Method - Verify
ef7bcae3-6aad-5ff0-a052-56cda408f893 | note | Record of conformity - Aconex reference(s)
fe236a95-2375-52a9-b348-d0951808a12a | note | HP*
6b23cd21-bf33-52f6-b3d5-d97af1e2be0d | note | Responsibility - Project Engineer
9b18b9e4-9afc-57eb-b25e-4a82ab2f659d | date | Date Completed:
18dd092a-730f-4cf2-a606-b6740af5c3e2 | checkpoint | 1.4 - Setting out for airfield luminaires
83e50014-8881-58cc-8457-e9a9a60ee8c8 | note | Frequency - Each Lot
479dcd7b-9b7a-5074-8332-60ebaeca5ded | note | Acceptance Criteria - HOLD POINT
eac1abfd-9163-55ce-9bac-cffdb8648911 | note | ○ The Contractor shall survey the proposed light locations in conjunction with the new and existing line-marking to set out the proposed lights. A schedule of the proposed lights shall be produced and submitted to the Contract Administrator.
9e739e4d-5103-5378-83c1-09e45c4eb0cc | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 5.4
74715ca1-b763-5113-8d01-877ab6432915 | note | Inspection/Test Method - Verify
707e4dc4-8f3c-5822-9d97-d5a9a87ff51a | note | Record of conformity - Aconex reference
3072a521-95bf-50ce-b0ae-389847bc651b | note | HP
04c1edf1-bda8-56ec-8a63-20496dd11d7e | note | Responsibility - Project Engineer / Beca
3ffb6f28-b7b4-521a-892e-37d033c9ce71 | date | Date Completed:
8923ea71-dce3-4309-8883-7365bb4ad439 | signoff | AUTHORITY HOLDPOINT
d8219702-29a7-4775-85f4-6b20e84138f1 | section | 2.0 - Installation of AGL Luminaires
aa23ac61-fe19-46f4-9f99-7d14b9c6f225 | checkpoint | 2.1 - Elevated Light Installation
c2c0e67b-24fd-5188-8f79-b0c451c5d9be | note | Frequency - Each Lot
5f845435-8070-51d0-99c7-98583a5d8046 | note | Acceptance Criteria - Components of elevated lights shall:
b42999df-f20a-531f-a749-20278d413889 | note | – Be less than 360mm above the pavement level including the frangible coupling.
e58238f3-5ce9-50a4-a042-9a2158404d2a | note | – Be suitable for installation on a threaded connection when installed.
769e7879-72ea-5a30-bf4e-4964cbc80b2a | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.4.4.1
1b4b2361-bab6-542f-b9b0-fc6520c0e12b | note | Inspection/Test Method - Verify
4c3444fd-d92c-5e1d-b384-95b75d4fb01c | note | Record of conformity - This ITP signed
4bfa64d3-b32d-529d-90ba-6277adf5837a | note | IP
bbbc11de-e167-5a35-a3b5-573c353e9ddc | note | Responsibility - Project Engineer
8be6ee96-8abe-511b-8c7c-7b1fe5d2605e | date | Date Completed:
29807ad5-0d91-4cb4-8e45-3b45d86004a0 | checkpoint | 2.2 - Inset Light Installation
b8727966-1933-50ad-b986-6b16de0560e5 | note | Frequency - Each Lot
dcec0426-348b-5d54-a53a-740001b9d9ee | note | Acceptance Criteria - Components of inset lights shall:
5a4ebf54-c4bd-5992-9640-b8b845306bb2 | note | – Be less than 13mm height above the surrounding surface.
be85313d-6056-5ac6-927e-583d7345e8e2 | note | – Have a slope of surface of the unit to be less than 20 degrees (not including any recesses).
f7c4e446-4e9d-5766-86d0-0250a57b777b | note | Reference Documents - ZULU-BECA-001-SPC-00003 cl 4.4.4.3
2d2df26c-ef50-53c3-b0f2-a39a681aa183 | note | Inspection/Test Method - Verify
beb57f01-7f57-5faa-aea7-b9bd533b6a4e | note | Record of conformity - This ITP signed, ADBSG Installation of Inset Light Fittings checklist
d07ce993-9da5-5eaa-a747-a928edd6d3c0 | note | IP
e409c5ee-92c0-5282-8ac3-69e56bac2f25 | note | Responsibility - Project Engineer
67e52dad-c049-5a33-825d-f4beea4d9493 | date | Date Completed:
32664a1a-4029-4bcb-8706-19d973aafb45 | checkpoint | 2.3 - Series Isolation Transformer (SIT)
4830ae71-e313-5466-b4ae-58031081ff8c | note | Frequency - Each Lot
4dd73a3b-ae96-50b5-8599-e9bd16d15cc5 | note | Acceptance Criteria - SITs shall be installed in specified deep base cans or pits
54395ba7-7d93-538b-8bd6-08bf67f571f7 | note | Reference Documents - ZULU-BECA-001-SPC-00003 Cl 4.3
6d816e99-b430-54ae-badd-7d0d1b9cb525 | note | Inspection/Test Method - Verify
6bbc2fc8-c1f4-5f15-9517-a64e44bb9bb6 | note | Record of conformity - This ITP signed, ADBSG Installation of Series Isolating Transformer (SIT)
3c398358-16e6-54b0-8604-1d89b220ec28 | note | IP
0dbc49cb-39a1-5f62-bdf3-258b2611cef8 | note | Responsibility - Project Engineer
14c0430c-f05a-5c1c-aa1c-66d0e475e361 | date | Date Completed:
e8d6688e-9dfe-46f0-a1f2-a154c1a16828 | checkpoint | 2.4 - Luminaire Circuit
817cbc8a-5372-54a8-9444-2056fc5d2829 | note | Frequency - Each lot
a0938b02-2819-58b6-b7fb-3187a9b9b4ec | note | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
d7399dfb-4e9d-509c-8b4c-7b0c2f59131e | note | Reference Documents - ZULU-BECA-024-DWG-09001-16
a4c88368-9055-5498-bfa5-d1598d91c25b | note | Inspection/Test Method - Verify
9f5cb6b6-f789-5e76-92eb-fca4394666b5 | note | Record of conformity - This ITP signed, As-Built Documentation
c6abf804-b828-57aa-8e39-47f893482815 | note | IP
447f8e9f-5ef3-555e-a519-47046b37d707 | note | Responsibility - Project Engineer
870c302e-4cbd-5067-b169-c229133d4520 | date | Date Completed:
66e139b6-7301-4c10-9c82-8bdee84ac825 | section | 3.0 - Post Construction
2c8cff63-7f20-4ed3-aaf4-143e15e5f2eb | checkpoint | 3.1 - As-Built
1e720d91-6aed-5eaa-8350-faee5f426bdc | note | Frequency - Each lot
d211e718-c1a1-5f04-968a-d3859807c45a | note | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
bbe1e46d-b474-57f0-8544-4c3801e76f75 | note | Reference Documents - WP-001-09
d6b3bdb9-8642-54a6-99ca-d74a61e9f3eb | note | Inspection/Test Method - Verify
89e30b3d-9c47-5a21-837d-274f9e34532c | note | Record of conformity - SCP
a63a45c5-f437-509b-9644-042653df2cbb | note | SCP
eab90674-47cc-53bf-a91c-8fea1e8a1105 | note | Responsibility - Project Engineer
7afdc925-e9fd-50d8-957e-5b545c4e9029 | date | Date Completed:
d1d73c77-6a47-41c6-ae35-7f78df043d9b | checkpoint | Final Inspection
63e52dc8-6d0c-5a2d-90aa-e6c7e550ff2d | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
0b3603ab-6b22-50ee-914d-449c3e5fa5e4 | textbox | Print Name:
23824264-d6c3-59ac-92cc-621bd8f206a7 | textbox | Position:
9516638f-d636-5971-a29f-fc2dfc27fd57 | date | Work Completed On:
7cf975b0-7dce-5e21-972f-4c8f943ffe5f | date | Date:
8845def4-38cb-503b-93bb-770aeb7e2a71 | checklist | Order Acceptance Certificate |  | Order Acceptance Certificate - Lot:
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
7718e601-4a4a-5c86-9399-63c49d4ed075 | checkpoint | Order Acceptance Certificate -- Details:
12a7c1e5-72a9-5807-befc-b9efc424750a | textbox | Subcontractor (full name of Subcontractor, ABN, Subcontractor's ACN and ABN)
5af93389-f25c-5d80-b77f-39a4818315e4 | textbox | Order No.:
4133d23c-5515-5362-b530-be47a6518f52 | textbox | Delivery Site/Location:
cd8c425f-9f53-5c2d-ad08-4b2c599e8049 | date | Date on which materials delivered:
c0097141-a841-55bf-8ae3-c53f2873beca | dropdown | Inspecting Engineer: | Abdallah Saidan, Abdul Saad, Alex Soo, Angela Julianto, Brad Carroll, Chris Cappelleri, Cristin Swar, Fadi Hanna, Faiyaaz Ahmed, Giuliano Follacchio, Jamal Khodr, Jasman Singh, Jihad Barbar, John Kakoliris, Jonathon Rock, Jordan Nicolaou, Marianne Sales, Michael Natalizio, Owen Tieu, Patrick Croagh, Tirrell Slaney
45e3f212-8d1c-543b-9a35-0358266c0e47 | textbox | Inspecting Engineer (if not included above)
4966c6cb-3e3d-5752-bb82-0a115d0656d6 | textbox | Subcontractor's delivery personnel (full name)
6b811dd6-6dc3-548c-b57f-0364a98d27a7 | textbox | Delivery vehicle registration number
62c93c34-0246-563a-b324-2ca2b6e4a8ae | checkpoint | The Subcontractor has checked all Materials included in this delivery and is satisfied that all of the Materials comply with the Subcontract.
8c958ecf-1640-539b-b8e3-d3a57349e5a2 | section | Packaging Inspection
5e80b1cf-5f85-5eae-9226-9c6c53dea384 | checkpoint | Inspection Result ID:
5af37914-7f8a-57ac-b8eb-af8f32f81e30 | button | Special Storage/ Handling Requirements? | Yes, No, N/A
d472a224-2992-568f-9627-b4deeee5931a | textbox | If yes, provide details
5c6b6948-bc83-52c5-9b75-ea98613e1ad4 | note | The following is for completion by Fulton Hogan
6d4bcd5e-6127-574d-a9b9-fb512def9611 | button | Confirmation of receipt of Units delivered. [Subcontractor does not complete. Contractor will initial on receipt.] | Yes, No, N/A
70fd54d0-3acd-5341-b686-5705578dd7c0 | button | QA/Compliance Docs Delivered? | Yes, No, N/A
49ff98bb-f0fa-5156-a58c-e12bcb2510f0 | button | Defective? | Yes, No, N/A
200f6892-fac1-5fdf-b1aa-f27f539f27ab | checkpoint | 1)
14fbd31c-3ed8-50d5-8bdf-b1544e387fea | textbox | Item ID:
2994839b-a721-5165-ac58-c135d99c2709 | textbox | Item description:
65816c8d-705e-5e01-a0e3-31d06a01fe72 | textbox | Units ordered:
2a8a3e58-1dff-56b1-9a34-9c5d3d05d8c9 | textbox | Units delivered:
d727198e-a11c-508d-b0e2-c3d4c1563815 | textbox | Number Accepted
d0755175-ee3f-501a-a373-48d612f07c5b | textbox | Number Rejected
111ddf99-8375-57e2-92b4-62eb39931b6b | note | Inspection Result ID (select below)
eb186f37-07fd-507f-a68b-4eba6d0d570c | tickbox | OK = Meets all criteria
d18323b2-c7d1-5115-a09c-544c7bdfcd3b | tickbox | QI = Quantity incorrect
0d812c22-f0a3-5d0c-9055-d001df447d3f | tickbox | IN = Item incomplete
bd28b41a-6ae4-5899-b676-258553c470b5 | tickbox | MI = Make or type incorrect
aab47e5e-1a43-5442-b958-df4ebb9be7ee | tickbox | TD = Damaged in transit
98d6ddf2-47e8-59a0-9158-0dbdfaa17086 | tickbox | NI = Not properly Identified
d6144275-4bd2-5780-83d0-a0e828e846d1 | tickbox | CD = Compliance docs not provided
200db96a-bdae-5e06-9fba-d8ee29460a36 | checkpoint | 2)
bcb8a80c-62a2-5601-8016-580bbc87704f | textbox | Item ID:
1b8dc746-448e-5455-895a-f55bcd8ebb83 | textbox | Item description:
4c97d56b-02c8-5d15-b1b2-77fb99e0d5ec | textbox | Units ordered:
a7fc8070-6e1b-5dba-bf70-313ca170f523 | textbox | Units delivered:
932ae001-ff39-554d-9551-288cb472e167 | textbox | Number Accepted
415e27e9-065d-5622-b00d-a2681ed2da3d | textbox | Number Rejected
f9f13e5f-856f-534d-a759-79009afd7c7c | note | Inspection Result ID (select below)
29b66bee-d998-50b8-bc4b-51bcc0a4b891 | tickbox | OK = Meets all criteria
4df1d900-41f1-5892-9255-6196f48f45b2 | tickbox | QI = Quantity incorrect
b6316236-2594-55a7-8f43-05628dd24ba8 | tickbox | IN = Item incomplete
0260be27-5d9c-5126-9cd6-2bdb101cfedc | tickbox | MI = Make or type incorrect
99b072dd-aa0b-5134-90bb-cb8ce550164e | tickbox | TD = Damaged in transit
53310f68-ca19-5463-a84e-fbb01226322e | tickbox | NI = Not properly Identified
3d1740fb-d64a-5717-8671-52a78e10fb91 | tickbox | CD = Compliance docs not provided
b5f9cc86-4177-54ea-a1ac-7dad72d6be28 | checkpoint | 3)
7d0b2e97-16e6-5457-98d3-76cd64b0f7e4 | textbox | Item ID:
eaca7272-0657-5d88-ba36-14ecc6e4f300 | textbox | Item description:
bfcf3a2f-2700-522c-82fe-c8b1bfd41064 | textbox | Units ordered:
c85741be-5e1d-508b-9596-988eabaa0f2a | textbox | Units delivered:
edd2e7e2-63ef-5942-ac19-b879a6054401 | textbox | Number Accepted
ba9cf8c6-51f0-5fea-a9af-e267a9c2954d | textbox | Number Rejected
1a5019de-b026-5684-bb61-9054252a1b79 | note | Inspection Result ID (select below)
18eb4d14-d9f2-5767-bd57-95ef30adb9af | tickbox | OK = Meets all criteria
a5db3abf-a7d9-5d87-ba79-115540460781 | tickbox | QI = Quantity incorrect
e3505139-cebb-5419-a051-7ef94dd7113c | tickbox | IN = Item incomplete
b2ff2970-0289-502b-bad3-211bbc4fd855 | tickbox | MI = Make or type incorrect
592bbd0c-4513-567e-b6bd-330459126e7d | tickbox | TD = Damaged in transit
9f04d024-b4de-5d63-9de0-e34bb90ecf2e | tickbox | NI = Not properly Identified
4278a3d3-eb65-553f-b192-ad44788bbdf1 | tickbox | CD = Compliance docs not provided
06fc7414-b417-521a-b0cf-51877a6d64be | checkpoint | 4)
02030a4a-e9f9-5de5-b134-e3c68ff5647b | textbox | Item ID:
0adef97f-9057-5939-ac0e-36f39d8591bf | textbox | Item description:
f1deff30-74cc-527b-97ac-ca8758e545bb | textbox | Units ordered:
bad31414-c790-55f1-94df-e9b3e7db8d0c | textbox | Units delivered:
6126b4ab-c1a1-5e47-803d-d37b5714cefb | textbox | Number Accepted
2608bb75-8749-5221-b1ae-e7e03b904cf1 | textbox | Number Rejected
cb797cad-1ab2-5fa4-93b8-5639b0145c17 | note | Inspection Result ID (select below)
485a4c56-ea86-5699-a275-6085cba522d1 | tickbox | OK = Meets all criteria
3657c271-31a4-5827-b9be-83ccb17cfea9 | tickbox | QI = Quantity incorrect
aea79501-99ea-5d7c-a344-23456988306a | tickbox | IN = Item incomplete
375a4393-fb27-5712-85d2-a3d39c6bea58 | tickbox | MI = Make or type incorrect
014225a6-fd62-55e4-a7fc-248b025fa0b5 | tickbox | TD = Damaged in transit
9e770ae4-cb01-5510-8737-fa33711c1bfb | tickbox | NI = Not properly Identified
dabc3c4d-271a-52e4-848a-b6f31b0f5dd6 | tickbox | CD = Compliance docs not provided
fe0c543b-2411-5c6d-86bf-c4f032ef97ed | checkpoint | 5)
ee3e5da8-de72-531e-95b5-9d20e807142c | textbox | Item ID:
8e7052af-a398-5e46-92b7-a2e49a4d9b3d | textbox | Item description:
89b51c1b-da9e-5489-8e93-95759094bd01 | textbox | Units ordered:
839dbb10-e1dd-5507-befe-477e8984beed | textbox | Units delivered:
b255ed66-3db3-518b-9402-6788fc4751b1 | textbox | Number Accepted
9ca98e0a-965c-5b4a-931b-555565640b79 | textbox | Number Rejected
2b9365df-3a69-5e77-9670-c4c1643e71dd | note | Inspection Result ID (select below)
83b4e2c3-6d8a-5719-a07a-3f29a40bd4c0 | tickbox | OK = Meets all criteria
0f572fc2-39e3-5ccd-a238-48068a967c0f | tickbox | QI = Quantity incorrect
1b0d93e3-fbf6-56d6-9ebd-234da000b0a4 | tickbox | IN = Item incomplete
9d4ab8e8-64d7-51e9-bceb-3aa3845370a1 | tickbox | MI = Make or type incorrect
b81b70ef-1498-5b95-afa1-955a18d41376 | tickbox | TD = Damaged in transit
880ad6fd-7a04-5537-8145-e9ec30b0af67 | tickbox | NI = Not properly Identified
5947b083-7280-51a0-bbba-ef46a1b46c3d | tickbox | CD = Compliance docs not provided
f3e7f541-2469-54e2-b778-ef8fe4bcac9a | checkpoint | 6)
f5213d94-b80a-58ad-9e02-f4c55d406424 | textbox | Item ID:
edd20faa-cb86-5256-bc0a-01f72d478ff4 | textbox | Item description:
777534c3-f873-5c72-b8bc-84a8652d31c5 | textbox | Units ordered:
c70ed69f-7b0f-51a7-9ebc-8e8780ed4eba | textbox | Units delivered:
bf72f1f5-fd8a-5f81-bfa7-30ec85b2b7b4 | textbox | Number Accepted
c066d4e0-a8b8-55e3-80b1-95163a7f00d9 | textbox | Number Rejected
f4a433b9-bedb-535f-afb2-38b96236e638 | note | Inspection Result ID (select below)
78f4fb22-5dd4-53c8-ae6f-45f0e5bbec26 | tickbox | OK = Meets all criteria
76a89976-b7bb-58ec-9dd9-5273687c8bb7 | tickbox | QI = Quantity incorrect
e3057735-dba9-579a-883b-f54c31d4dda4 | tickbox | IN = Item incomplete
b1e39859-58b0-57c7-a46f-b8dcece44ae6 | tickbox | MI = Make or type incorrect
317c7343-d44b-5e6f-ac4d-14777d996856 | tickbox | TD = Damaged in transit
22d1c960-40b1-5717-a111-2733e94a093b | tickbox | NI = Not properly Identified
5627b1ca-a2cb-569b-b8d7-4b4fdf5390e5 | tickbox | CD = Compliance docs not provided
50256c4d-11e5-54f7-9e72-dfc39a625998 | checkpoint | 7)
24420331-8897-5df8-8e20-28850ce6820b | textbox | Item ID:
050f2298-60e1-597c-ba41-19f372d6f9ea | textbox | Item description:
4aed13e8-5b70-5ac5-b063-27682e4b1e7d | textbox | Units ordered:
a8455a7c-3e34-5fe2-9484-44265dbc6270 | textbox | Units delivered:
c96e5370-3e8a-546d-b3ba-30efbbacacd3 | textbox | Number Accepted
2ef35f51-cea1-59a0-a464-7b59d63adaef | textbox | Number Rejected
8d6998f0-ae2a-550b-9a35-ce9a90bcd907 | note | Inspection Result ID (select below)
38731218-084d-5300-8ed7-2fa488172541 | tickbox | OK = Meets all criteria
f5fab120-e143-55d9-98b3-47b141326437 | tickbox | QI = Quantity incorrect
1bbc596b-6778-5be7-be40-a3679ec04117 | tickbox | IN = Item incomplete
59d81aa0-cf54-5156-96b1-253b1feaf6aa | tickbox | MI = Make or type incorrect
a2040892-0694-53d0-bcd2-55ecc0661f89 | tickbox | TD = Damaged in transit
5ff1772d-def4-5790-807b-814328b8894d | tickbox | NI = Not properly Identified
4aee0408-6d70-5ad6-a317-4bbc96d33a65 | tickbox | CD = Compliance docs not provided
f5eb9f57-0331-5249-85d0-33af4c854139 | checkpoint | 8)
0a389b74-9f90-525d-8b0c-2552b759cf12 | textbox | Item ID:
da5d972b-2633-569a-ac0d-39ab45185063 | textbox | Item description:
5225212b-ed5d-5287-97df-f33b1afb8849 | textbox | Units ordered:
93ccb08d-1a0e-5bbd-b3fe-401d00e9b93f | textbox | Units delivered:
efe49955-ccdf-5024-a811-8666f33136b1 | textbox | Number Accepted
ded9f1eb-3668-56ca-b5a9-a52244bb2ade | textbox | Number Rejected
ae08ee64-0f14-5936-97e7-b66bc37e6886 | note | Inspection Result ID (select below)
369bd422-e8d4-5e79-93e2-fec34f9dcbe0 | tickbox | OK = Meets all criteria
36c62b89-9687-5b3e-8bae-397801b4f57c | tickbox | QI = Quantity incorrect
db8728c7-e9ea-5d6b-b0e6-ebd0d5eb6d8d | tickbox | IN = Item incomplete
ed22784c-94c4-5299-b9ac-d91e57c69287 | tickbox | MI = Make or type incorrect
5a8fff9f-6801-5421-98eb-2215df843cbe | tickbox | TD = Damaged in transit
676893f2-c88c-51b8-80f3-69b2dc890cfc | tickbox | NI = Not properly Identified
67c8e16c-c8f8-588a-9ee8-31eb20893fad | tickbox | CD = Compliance docs not provided
9718bee2-a89a-568e-81da-fd28f3920a98 | checkpoint | 9)
65eae4e7-939c-5ce5-9db2-eece6a4a649f | textbox | Item ID:
974acc2a-4b50-5eee-9e15-9ba65a782a7c | textbox | Item description:
21e915b9-fedf-5b73-a47d-be5243581d53 | textbox | Units ordered:
0cced952-00de-55ce-8584-6be8030a25ee | textbox | Units delivered:
f3a96a9e-67cf-55a6-8f0d-bf09c6d85ef8 | textbox | Number Accepted
d3a1489b-5278-579a-9a15-15c1cea2f994 | textbox | Number Rejected
f383bbb4-9354-50cb-b763-6b692204c157 | note | Inspection Result ID (select below)
05656c8c-a056-5d75-971d-973831c209d5 | tickbox | OK = Meets all criteria
aee89344-f771-5ce8-8c50-075d95882fce | tickbox | QI = Quantity incorrect
377a752a-da2e-5870-83e8-7d570544216a | tickbox | IN = Item incomplete
8158ea5b-dcb3-5a4a-970a-029eebc1a66c | tickbox | MI = Make or type incorrect
9fe0fffb-3708-50b7-a9ce-0792b5913c20 | tickbox | TD = Damaged in transit
f81eae3f-8b92-5308-9e64-456dbeb343cb | tickbox | NI = Not properly Identified
6857182b-1b54-522a-a5d4-8dbdcedde131 | tickbox | CD = Compliance docs not provided
d32e9f98-55c9-5057-9b0a-904c60fdc129 | checkpoint | 10)
f31045c7-1532-5996-9539-a059c44e9143 | textbox | Item ID:
bf14bf6a-0c22-5298-acce-1b1e76efa58b | textbox | Item description:
275633ff-23c0-509e-994c-a32a2affc4d8 | textbox | Units ordered:
f4f913e7-857f-587d-853a-582fc5c6cea6 | textbox | Units delivered:
0ad7f80a-763c-56c2-a5d0-fccc379240e3 | textbox | Number Accepted
728face4-b70a-51ba-9372-5306f854b124 | textbox | Number Rejected
09e54c31-f69e-559c-9836-3041d059feb5 | note | Inspection Result ID (select below)
f83dc770-5925-5f78-8f97-99ada5109ef4 | tickbox | OK = Meets all criteria
24966949-b70a-5c70-8b17-e0f2631cc6df | tickbox | QI = Quantity incorrect
4f31970c-fe9c-5c41-b197-736cf33848ba | tickbox | IN = Item incomplete
26817fea-ad8e-5d03-ab40-a2308c1e1b90 | tickbox | MI = Make or type incorrect
aa968b3c-f799-56e7-b410-ef29880b0530 | tickbox | TD = Damaged in transit
a7e94359-1c7f-51d6-b0c8-688f94b72d28 | tickbox | NI = Not properly Identified
945ea484-67de-5837-a72f-5e3f7a05d714 | tickbox | CD = Compliance docs not provided
3ceadcd6-d779-5c97-8426-53dd865a89c4 | section | Sign Off
2511984d-74dc-51b8-9984-3f4226eae93c | checkpoint | Accepted by Fulton Hogan
afd289e2-65eb-5256-927e-e1c2ccbc0bb3 | signoff | Sign Off
67acbde0-1dfd-558f-bb6b-eb900bac2f6c | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0009 - Unbound Pavements (FCR & RCC) - Rev 1 (3.5 Signed off) | itp | ITP009 - Unbound Pavements (FCR & RCC)
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
9ddd2561-c351-5c44-858a-2e4143344a3b | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000825
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
f1bd1704-9d65-5504-9073-a58e0fb450e7 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000893
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
282695af-0cd0-5fe3-8b64-3dcbc3207e5e | checkpoint | 1.7 - Testing Determinations
435afed8-b133-50ef-9159-3038e4e9ce4f | note | Frequency - Prior to works
36ad8297-35ac-522d-abb9-b2825c174034 | note | Acceptance Criteria - 1. Basecourse and Sub-Basecourse thickness test points selected randomly.
23450c8f-eb32-5958-a1f6-4c1070f0aa49 | note | 2. Field dry density test locations selected in accordance with AS1289.1.4.1.
b46d1e09-9f04-5e91-94c9-e815bb795a73 | note | Reference Documents - Cl 4.21.1
523cd7eb-bebb-5653-b8f3-ced01627075f | note | Inspection/Test Method - Verify
a6984f74-007e-5d32-81f4-43d2d0ae7149 | note | Record of conformity - This ITP signed
9d271944-3ad5-5014-8b38-573d1b5c08db | note | HP
c4dc7eef-31c3-51c3-8336-cd5de23a3ab5 | note | Responsibility - Project/Site Engineer, Principles Rep
4e0c42ad-439e-5855-9604-6d597d69fa7b | date | Date Completed:
466d62da-b64c-5642-9815-ed935f373305 | note | Principal’s Representative - Aconex Ref: BecaCPL- GCOR- 000890
83a1d299-f349-508e-bab0-117c246c15aa | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP, HP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
b4b288d4-a5a3-5645-a157-30ee8075f492 | signoff | AUTHORITY HOLDPOINT
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | note | Principal’s Representative - Aconex Ref: FHPL- TRANSMIT- 001750
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
676a23e6-b816-500c-bd22-fc4a3c2512aa | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0009-LOT-001 - Stage 1 PT1 - Rev 0 | itp | FH-ZU2-QU-ITP009-LOT-001 - Stage 1 PT1
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
22b60133-d07e-5778-afbb-3104cb451e98 | note | Frequency - Prior to commencing works
90628709-661f-5c1d-808d-3f9633505536 | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex
bc77cecb-25db-54e2-a46f-f50316ce64bd | note | Reference Documents - Aconex
248e7c02-a029-5336-9878-3422c829cf56 | note | Inspection/Test Method - Visual inspecti on
505c13d3-3958-55d4-b28a-dbe56fcb6509 | note | Record of conformity - This signed ITP
d9b9a31e-4fc1-55c9-8cf1-e24191b8f35b | note | HP*
577c368a-5703-5a58-b59c-18e92dbc9be8 | note | Responsibility - Project/Site Engineer
0ca55223-b839-58b1-9ea2-63b876b41d8e | date | Date Completed:
0ee48894-54ec-5653-949e-3aecb94d8a6f | checkpoint | 1.2 - Implementation of all measures and controls, weather, and material properties.
d49a7852-f9a9-5121-afd2-663081afa613 | note | Frequency - Prior to commencing works
1e3e4950-6df5-54d8-b002-d4b18ac8c1d9 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
46aa07a5-24fd-5c8d-8bf3-189213104141 | note | ○ Check weather prior to starting any works.
4274f253-54a3-50bd-9ec8-7b1601fe3d02 | note | ○ FCR material used for the works in accordance to VicRoads Class 2 Crushed Rock.
9351f45c-6020-5acc-acdf-0786a7e52f32 | note | ○ RCC material to be used for the Works in accordance with VicRoads Class 3 Crushed Rock.
67de20a2-0256-57b6-850f-aadb800e0d07 | note | ○ Checking underlying layer ITP’s (subgrade ITP008 and select fill ITP004 has been completed)
337e8923-b57f-5282-856b-d3a6b8d18b41 | note | Reference Documents - PSP, EMP, TMP, WP SWMS, Spec Cl 4.19, Spec cl. 4.1, VicRoads Technical Note 107 Spec cl. 4.6
b918f1ef-0da1-5bc1-8bb8-6c02335de461 | note | Inspection/Test Method - Visual inspection
6f531f46-a05a-5c16-b04e-195d1c3f4a93 | note | Record of conformity - This signed ITP
3b7b3517-c997-5002-97c8-f1aa5f1e7cae | note | HP*
2de72f79-4994-57b6-a35f-9b3e18858774 | note | Responsibility - Project/Site Engineer, Foreman
baa8b9fa-f889-5d30-8dea-a71cc722d564 | date | Date Completed:
b55c3da7-c29e-50dc-b5c6-6c3d6d4c85da | checkpoint | 1.3 - Material Report - Fine Crushed Rock (FCR) Material & Recycle Crushed Concrete (RCC)
08f8e815-db8e-5c04-a20e-779ea9c698a3 | note | Frequency - 7 Days - Prior to works
f23fc5f1-f6fb-5435-ad79-c5ecdcd035c6 | note | Acceptance Criteria - Material Report to be submitted 7 days prior to works to include;
1344dbf9-3674-54ba-b047-2f9a512d67de | note | ○ Source and Quarry location
dc8222db-ef8f-5c16-b274-2905dc7a31d3 | note | ○ Quarry material is sourced from.
a8449f49-f55e-5365-8100-695b2068f934 | note | ○ Material rock type and petrographic description
8b784087-184c-59ef-b6b6-040c79a2a485 | note | ○ Historical test results
836aacce-c6f4-5341-b85b-04b293e861dc | note | ○ Method of processing and transportation
52202e1b-799b-57e1-bfb2-b5a8c390d48f | note | ○ Material summary of the results of recent test on samples of the material from the source
e2e34f1e-e0b2-5faa-bb77-6746fc484680 | note | Reference Documents - Spec cl 4.20.1
c4580524-9128-5583-a7bf-4fa86d4a90ec | note | Inspection/Test Method - Verify
6f6417f1-69f8-5ad5-984c-fd198378675f | note | Record of conformity - This ITP signed
c8da58f1-5852-54c6-b606-35386ce293d9 | note | HP
27f7bd55-d87c-5dde-b69a-8a690d4a1c5c | note | Responsibility - Project/Site Engineer, Principles Rep
98351715-983d-55b6-b5e4-29818398c2fb | date | Date Completed:
f90cc78c-5577-584a-bf6f-2baea0a79d8a | note | Principal’s Representative - Aconex Ref: Holcim RCC Class 3 - DCWC Mgt-GCOR-009582
6ed4e75b-7d7c-59d4-860f-84f44b2920d0 | note | ○ Holcim FRC Class 2 - DCWC Mgt-GCOR-009581
f1140fed-3d65-5000-a675-33f0cf450936 | note | ○ Stirling Class 3 - DCWC Mgt-GCOR-009565
8b2d5395-ceb8-53cb-8eb1-c7add6510501 | signoff | AUTHORITY HOLDPOINT
ec34d278-5586-5c2a-99c8-01e2abad83a0 | checkpoint | 1.4 - Reference Samples
525ba691-af22-5b05-b06f-d97f2febed12 | note | Frequency - 5 Days prior to works
d6fbd216-8984-5446-82cf-f06bf7078519 | note | Acceptance Criteria - Reference samples to be submitted 5 days prior to works commencing. Two bags to be taken each weighing 25kg. One bag submitted to Client, one retained by Contractor
393a62fb-dc1a-51af-820d-43d92dcf2ed5 | note | Reference Documents - Spec cl. 4.20.2
81cb4669-886b-5347-b152-1895c2aef53c | note | Inspection/Test Method - Verify
3df23d20-62cf-5417-b4eb-60cb6864ab05 | note | Record of conformity - This ITP signed
afaad2f4-dbb5-5fd8-87e6-401b5bf4febd | note | HP
54753b28-df32-5121-a510-4e413fb619cc | note | Responsibility - Project/Site Engineer, Principles Rep
ee76c1dc-3531-5a2f-8c1f-475d8f250b39 | date | Date Completed:
d95e7d5e-6bf0-5924-b391-1cfea39c7d6c | signoff | AUTHORITY HOLDPOINT
86350ec1-aec3-5802-aaf3-a14a45b6d2ff | checkpoint | 1.5 - Trial Section
65684dbf-f369-509e-a5e8-b314c3fd8819 | note | Frequency - Prior to works
bafdae1c-25bf-5ae2-9cd0-6608d8ef0a98 | note | Acceptance Criteria - Trial section to be completed with Principles Representative approving the use of the spreading machine.
6c6faa28-2c6a-59b8-bc47-3393a4e05f95 | note | Reference Documents - Spec cl. 4.7
af7d6c18-3dcc-50bf-b3f8-53ce25ab318e | note | Inspection/Test Method - Verify
17a066a2-c53c-51e9-a713-f8604f6dba5c | note | Record of conformity - This ITP signed
eeb60278-237d-56da-890e-daecf0bb1cf4 | note | HP
b8253941-a061-5b59-a6f1-8d269d6fe801 | note | Responsibility - Project/Site Engineer, Principles Rep
a035e09f-3c92-5f13-973b-02f96ca5b1ac | date | Date Completed:
50b5aab5-7a04-53ea-a4dd-31d851a2dce3 | signoff | AUTHORITY HOLDPOINT
690716ed-b540-5814-804e-da1a18d341a5 | checkpoint | 1.6 - Compaction Equipment
b945be75-e6e9-57a1-8123-6e8633aab849 | note | Frequency - Prior to works
e74b505a-9f5c-54a0-aeea-6de10bb335eb | note | Acceptance Criteria - Pneumatic tyred rollers having a weight of 27t (min roller weight can be 7t spread across 7 wheels). Tyre inflation pressure to be checked. A 15t to 20t smooth drum roller to be used.
2801421f-e441-58d5-bb6a-16a4d3e6997a | note | Reference Documents - Spec Cl 2.4.3 Item 84 Tender Clarifications
7714caf1-b8f8-5140-a270-f11a742d03c8 | note | Inspection/Test Method - Verify
c68e6fd7-3cf1-58cb-b9e5-ef98680eb80c | note | Record of conformity - This ITP signed
1ca6e76d-4a10-59f8-9af4-a8cfd70ad21c | note | WP
de947921-e38e-5dbb-98de-20d29f6f2cf3 | note | Responsibility - Project/Site Engineer, Principles Rep
780ed8c5-c16d-5d7d-a120-b2874bf1d159 | date | Date Completed:
1d9506f5-f6c7-5206-bffc-81f4f4f90212 | signoff | AUTHORITY HOLDPOINT
31f3573f-3cd4-53a2-bab5-d81150ad14d3 | section | 2.0 - Placement of Sub-basecourse and Basecourse
520af3e6-6af9-53b6-9cab-e0a37d5ddeeb | checkpoint | 2.1 - Layer Placement Parameters
aaa3edf8-61eb-55f2-97a1-d0fb08386030 | note | Frequency - Every Lot
16c77b6b-81f0-5b20-ad8d-8506d7ec2d02 | note | Acceptance Criteria - Summary of Parameters for each Lot;
3f87eaec-bfd5-5113-a5dd-c989fed0fec5 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
ba7c17ca-eae9-5ba4-a3ff-214dac3491bc | note | ○ Max Layer is 200mm
322cb297-e6e8-5565-b3fe-48d519767cce | note | ○ Min Layer is 75mm
ce182ba1-c8fb-5c79-9cb4-9e7811cce7b1 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
3fcf686c-043f-5d65-9648-ea4b780b560f | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
2a7aa885-9c4f-5381-8ece-bb1b9ccba295 | note | ○ Material to be batched within 1% of OMC
2585bc1f-f9ba-51cb-839f-4f8d9b4863dc | note | Reference Documents - Spec Cl4.8, cl 4.21.2, cl 4.13
cced5364-2910-5d18-aa42-577b9981563e | note | Inspection/Test Method - Verify
8100ba46-80fe-5560-aca3-286dd0f42292 | note | Record of conformity - This ITP signed
be2c8188-b893-5606-951c-1d3052e63cd4 | note | IP
6d1c799a-1c5e-5479-95f5-52693cfb267f | note | Responsibility - Project/Site Engineer
c035320a-65e6-5da3-8edd-85233f228189 | date | Date Completed:
ab12b78d-7983-5acd-aa07-c177c46370e6 | checkpoint | 2.2 - Placement Checks
35f1d8ab-6103-59c1-8b59-7dbfdfd5a318 | note | Frequency - Every Lot
d330c613-67e4-5ca5-a41d-034019e87353 | note | Acceptance Criteria - During placement of the material check;
a0897ee6-0317-5245-b2d4-b7319354e90a | note | ○ Deliveries do not disturb underlying layer
c52be776-0b87-5bb4-9639-97923473720f | note | ○ Spreading starts from crown / high side where practical.
6558ad17-534d-5102-861d-33bdf6acdef4 | note | ○ Material does not get contaminated during placement / delivery
da1053c0-3a2a-5ac3-86fd-b3ecc6fd4402 | note | ○ Watercart is present to condition material as required
23130571-9585-5f82-a1bd-667592304329 | note | ○ Edges are cut / removed if dry of not compacted with abutting lots
25bb25f1-45b3-507e-b660-1bdfb628c3bb | note | Reference Documents - Spec Cl 4.8
35f5add3-e162-53d8-9bcf-6f098b9c662c | note | Inspection/Test Method - Verify
b7644ee8-0ce7-5f78-90af-aafeca592397 | note | Record of conformity - This ITP signed
5a905e00-c1e4-512f-9a17-ade2ccd58b44 | note | IP
19652dec-189a-5f21-8896-0766c8cb7a88 | note | Responsibility - Project/Site Engineer
2a0baffe-e984-564d-9c01-dab08964c6d6 | date | Date Completed:
03b653d0-0f2f-5bbe-ba99-60916a24386a | checkpoint | 2.3 - Compaction Check
58e6a7da-0a23-579e-adb3-07ffa5af4807 | note | Frequency - Every Lot
09efdcc0-9ad5-589b-9f7a-29a04ff56202 | note | Acceptance Criteria - During Compaction check;
112f68b3-7620-566d-bcbd-453cf4539fcb | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
156bec7b-d118-5098-80a4-9f9811800889 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
63744c10-259a-59ff-aa84-ed5a2ec11330 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
1dcab749-3f6d-5dc0-8b70-8e6ccc60521a | note | ○ Watercart Present onsite for conditioning
55bdb2c8-4342-5857-baae-a10bdc7ecac0 | note | ○ Materials are trimmed to required shape and level
d22c4f0e-7900-552c-8a73-ef0db6e4ae0e | note | Reference Documents - Cl 4.10
1993e4bb-389f-5674-aac7-b01ba95c1fb1 | note | Inspection/Test Method - Verify
669b9d6b-f3ad-50de-bde3-67155680d007 | note | Record of conformity - This ITP signed
14eaa2db-1f06-5432-8e0c-27042f49ab02 | note | IP
6cd03551-ea7e-545c-bfad-d40f0419bc20 | note | Responsibility - Project/Site Engineer
045eb3cb-4193-5ec9-b4b2-f7ded14ec478 | date | Date Completed:
56c1eb5a-a610-51e7-86f1-f05ba8e1b5bd | checkpoint | 2.4 - Services & Culverts
cad1544e-6b90-53e9-b346-5cdaec13789b | note | Frequency - Every Lot
6ade1825-13f6-521f-80f3-e6df0e156981 | note | Acceptance Criteria - Check if any culverts or services are with the influence zone for compaction.
f01b9dd3-612c-5a17-a57d-010ef1513183 | note | ○ A general rule, FH will seek advice from the Principles Representative if any culverts, duct banks or RCP pipe are identified closer than 1m from pavement layer surface. If identified, Fulton Hogan will maintain a 1m exclusion zone either side from centre of service for vibrating compaction activities. Hand held DPU’s/whacker plate to be used in lieu of rollers in restricted areas.
67c452e0-d6b9-5f8e-a3da-b3d574687983 | note | Reference Documents - CL4.10
fa8211c9-abd1-57da-b54f-de0c6e5dbe35 | note | Inspection/Test Method - Verify
ffa561c5-3a1c-5b2a-8fdc-90801c716515 | note | Record of conformity - This ITP signed
33423efd-62ae-5c89-b304-dd78ede7b634 | note | IP
54f78c92-1f94-54e5-9290-23165c7f8f9b | note | Responsibility - Project/Site Engineer
d6d1b5b8-e9d7-5583-8a85-3068b4699540 | date | Date Completed:
af9dc4f1-7e43-5752-b5a1-15b8f94cf295 | checkpoint | 2.5 - Protection of Layer
b5def97a-8a82-52be-9c54-498ac337f247 | note | Frequency - Every Lot
f5abe81d-8f4d-510d-8885-fa3cc5fca33b | note | Acceptance Criteria - Protect area from undue deterioration by;
f417fc95-2acf-5b5c-8b72-7fc970c8db29 | note | ○ Section off area for at least 12 to 48 hours to allow material to dry back.
59af82c2-ee2b-55ae-9f1a-84ba3d796d2f | note | ○ If unable to do so, keep traffic to a minimum
7b0a10bc-80ce-5720-b786-07441ed72b4e | note | ○ Or ensure any traffic that has to cross pavement layers, do not follow the same driving line.
98124425-bbe9-54b3-9173-c49ea88147ad | note | Reference Documents - Cl4.17
941d9051-473f-561a-bb5b-246c9d4cf08f | note | Inspection/Test Method - Verify
4ca87943-c62f-5a1b-b82a-fc898998e077 | note | Record of conformity - This ITP signed
fbcb7b46-d64b-5e69-8d4c-558089c333e1 | note | IP
86dbe21d-b474-525d-b7cc-73d45852ecfe | note | Responsibility - Project/Site Engineer
c1acb8c3-0d37-5859-88bb-9dc12a60a61b | date | Date Completed:
ed4dca39-7158-53f5-b80c-2934cf975618 | checkpoint | 2.6 - Proof Rolling
44460523-6468-5e7d-8f76-60c382cfa5cc | note | Frequency - Every Lot
b7f9cddf-e0d6-57dc-b450-1557ea5a71de | note | Acceptance Criteria - Proof rolling will be undertaken at the top layer surface of the imported select fill material for under pavements using a 16T smooth drum roller (minimum), or a 15kL watercart (minimum).
1d13e8cc-aca0-5c16-ade1-a98bb49c050a | note | ○ Principles Representative to be invited to proof roll 24 hours prior to inspection.
2bc6ddb4-edfd-5f91-8fd6-de65508b146e | note | ○ Principles Representative must witness the proof roll.
ebf5a59e-8e44-5291-8371-0f476cc2fda0 | note | ○ Following completion of the successful Proof Roll, Principles Representative will approve Fulton Hogan to place the next layer.
6134a0b9-74fd-5991-9fe4-7f7c835cb261 | note | ○ Placement of next layer can occur once lot is accepted following proof roll. Proof roll inspection will satisfy pre-placement CTB inspection
ed8f929c-5f3c-5d99-9d6c-e9ec5ff8a2c2 | note | Reference Documents - CL 4.11, CL 4.8, CL 4.16, CL 5.9
8853b58d-aa9e-5f04-8604-ca7be2a1e182 | note | Inspection/Test Method - Verify
9166191e-1d47-50c9-a1c2-aa87106416fb | note | Record of conformity - This ITP signed
8d54efd3-12ea-58c5-9db4-1ee9e840e530 | note | IP, HP, WP, HP, HP
b82ae293-b330-51f3-a3dd-5b0af50e15d0 | note | Responsibility - Project/Site Engineer
baa750f2-e49b-504c-a61d-2e359d14fe2f | date | Date Completed:
40f59b4f-71be-5a37-8b06-48355023e0f7 | signoff | AUTHORITY HOLDPOINT
18355098-3bb1-5292-9129-5d9c49ee19cd | checkpoint | 2.7 - Completion of Remedial Works (if required)
a6eea7f7-f90d-5f24-ba42-3cee0d13807c | note | Frequency - As required
10860f22-bd45-5045-b42a-51938225a3eb | note | Acceptance Criteria - Completion of remedial works or nonconforming Sub-Basecourse and/or Basecourse to be approved by Principal’s Representative before proceeding with the next layer of pavement Works.
b60361f7-65c4-5619-aaf9-fb1de60ca685 | note | Reference Documents - Spec cl. 4.21.3
a5be587b-5a31-5d92-87c4-2cf51d5227dc | note | Inspection/Test Method - Verify
ba4d1c10-00f9-5670-bb2c-33ef0baf1f43 | note | Record of conformity - This ITP signed
99acb4ef-c1fe-5a03-89cc-dff4993bedc2 | note | HP
a0e4e81b-9909-57d4-ba10-bc175a31943f | note | Responsibility - Project Engineer, Principal’s Representative
8a219366-a68a-5b60-8cff-5a38571304ec | date | Date Completed:
90a2a886-571d-56de-9a6a-670b0a14580e | note | Principal’s Representative - (if required)
c3655578-698a-581e-b5a5-f09c022177f4 | signoff | AUTHORITY HOLDPOINT
9b0000de-0289-50d5-8923-c7478a283c5e | section | 3.0 - Testing, Lot Size and Compliance
8ba74c27-2d49-528e-b53a-453ab30f277b | checkpoint | 3.1 - Survey Conformance
ce5c29e5-5140-5189-9eb7-e50ab50e5199 | note | Frequency - Every Lot
f272f98a-afa0-55a2-99ab-2926a15cf644 | note | Acceptance Criteria - Final survey level to be checked in a 5mx5m grid to conform with -10mm to +0mm.
df4c2108-63ab-5b10-b7f3-2e9c90d8b439 | note | ○ Survey report not provided for intermediate layers of the same material type (i.e. for PT2 where multiple layers of same material type placed).
12872338-4862-5c8b-9333-33b95e486659 | note | Reference Documents - Cl 4.13
53f1e0a9-3cd8-5987-afac-9955739ce2e2 | note | Inspection/Test Method - Survey Report
cfaa3583-94cb-5b87-a96f-4b0626c0b7ea | note | Record of conformity - This ITP signed
115ef3cc-0237-5ccb-b90f-4e1d03a9a55a | note | SCP
929cefd4-f1a7-5699-a3e6-84e1cfe5d6df | note | Responsibility - Project/Site Engineer
9d93fb88-69f1-59e3-929a-d5c9541b8328 | date | Date Completed:
80ed8158-99a3-513d-9e12-09880383a921 | checkpoint | 3.2 - Surface Smoothness
c0ec5a15-a8a0-51ca-90fd-d266a977ae28 | note | Frequency - Every Lot
d3bb6e9d-cacf-567a-bb05-bb6f85f87f76 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
c0794366-a9f1-513e-a322-e27e793bf4c7 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
428ff593-cbc8-5486-9adf-190d324ee211 | note | Reference Documents - Cl 4.14
916d282e-b4f1-5915-a1c9-84918bf87ad0 | note | Inspection/Test Method - Verify
f13e2c07-1d50-5bc0-b7a8-ec257e7c1c05 | note | Record of conformity - Report
0a56ea0b-1e1d-575f-aaaa-8362bd7334a7 | note | TP, HP
7c42df32-edf4-5349-9cac-0db15597dd49 | note | Responsibility - Project/Site Engineer, Principles Rep
7afe6ac4-7764-512e-b7a2-c8fe830be0cc | date | Date Completed:
ab521b67-11c2-59d8-a3c0-98ec86671180 | signoff | AUTHORITY HOLDPOINT
12ef7ba2-4a80-5164-a247-feedc5d67ff8 | checkpoint | 3.3 - Layer Thickness
c7d134cc-94cd-5822-9a24-cf05412661f1 | note | Frequency - Every Lot
dfdd1cec-5b69-565b-969b-13bfc3125815 | note | Acceptance Criteria - Check thickness of layer using survey at the frequency of field dry density determinations. Thickness shall not be less than what is shown on the design documentation other than allowable construction tolerances.
39ceb27a-a277-5db6-8968-85e5c122043f | note | ○ Total pavement thickness is to be checked. Intermediate layers, no check is required.
02cf8440-e7ce-5019-8d6d-f32d5fb3afbd | note | Reference Documents - CL 4.12, CL4.21.1
018a61a9-d71a-5691-a975-97cdb35c1e0b | note | Inspection/Test Method - Survey
7625b794-097f-518f-90e0-c3cf230ed64d | note | Record of conformity - Survey Report
381236eb-aca7-59e3-a405-b6edd1e665c5 | note | SCP
53f8aeac-1b5e-5448-811f-f523a49ae4ee | note | Responsibility - Project/Site Engineer
8bc84e71-cdd6-5f5b-afd0-1b535d392c96 | date | Date Completed:
9fdc7f62-f611-5a1d-a6d5-ee615e4ec42e | checkpoint | 3.4 - Degree of Saturation - Sub-Basecourse or Basecourse
88ac18ee-32b3-5465-8cd7-55615a26e84c | note | Frequency - Every Lot
9c74aee7-54c4-5afa-91e6-17f8b6c54a58 | note | Acceptance Criteria -  Degree of Saturation to be tested for information.
7d6d8edb-471d-59a3-84c9-22efe19673c4 | note | ○ Target less than 70% Mean Moisture Ratio.
5267ce29-e9dc-5467-8683-1ff409d3ea82 | note | ○ Test to be taken the shift prior
9ceab416-7620-5e4c-90dd-667de55b8550 | note | ○ If lot gets impacted by significant wet weather, tests to be re-taken
8589b525-694e-5da5-b255-316e9b32bc6b | note | Reference Documents - Cl 4.9
5fc35d50-782c-58c0-a03c-3e2d8632bc41 | note | Inspection/Test Method - Test
36e1d3a5-9404-5501-a43d-8d4439103d9f | note | Record of conformity - Test Report
5b334ed9-a6bc-5b9f-a9a5-188554ebf8fe | note | TP
57654c0f-8304-5154-aabe-6a53ae12880c | note | Responsibility - Project/Site Engineer
2fb7e3e4-a500-5dab-971f-da16c64f635a | date | Date Completed:
93d9ed7b-13bd-571c-b28a-b3e62bf41308 | checkpoint | 3.5 - Field Dry Density
ab290cab-8857-5299-aa93-394c9f7fa1cd | note | Frequency - Every Lot
44b41968-019b-5980-9048-f4b4803f2fa7 | note | Acceptance Criteria - Dry density for basecourse layer has the following acceptance criteria:
14d36e20-9b4e-51c7-b303-4820d35263fe | note | ○ Average of 5 consecutive tests exceeding 100% MMDD.
58de0ee5-78b1-54c6-8224-caf072eeab7c | note | ○ No individual test result less than 98% MMDD.
5d48328e-ac3a-5ad6-b3d1-2406a288f5b8 | note | ○ Principal’s Representative approval based on the results of proof rolling.
f93e1ad9-5cf4-5128-a858-cd7b9bd4cdbb | note | Dry density for sub-basecourse layer has the following acceptance criteria:
e55b6308-f7dc-5856-a542-efcc3c4daea4 | note | ○ Average of 5 consecutive tests exceeding 98% MMDD.
9bf576a0-bf13-5841-ab9a-3afc1935f1b8 | note | ○ No individual test result less than 95% of MMDD.
87da770e-45a7-5e52-8aa1-dda76aa5f24a | note | Principal’s Representative approval based on the results of proof rolling.
44ea133f-24b6-54a9-a30f-f261e13a62f9 | note | Reference Documents - CL4.10 Cl4.21.1
f280a436-de2a-53ef-93ab-b1e3225eeeeb | note | Inspection/Test Method - Test
52cdd929-b842-55ad-8145-5e9812049d33 | note | Record of conformity - Report
407dbe1a-efa0-5213-9bb6-8e6f36cbc3c5 | note | TP, HP
ab5827b3-767d-5dbc-a203-d030deba9967 | note | Responsibility - Project/Site Engineer
e7b37db0-a68e-5a1c-bb23-556cc134f8ee | date | Date Completed:
b4b288d4-a5a3-5645-a157-30ee8075f492 | signoff | AUTHORITY HOLDPOINT
78953ecd-84e7-5c05-ab3e-4b8357499fea | checkpoint | 3.6 - Quality Assurance Records
6006ffa3-1aa2-59bd-83dc-d6b805ff55b4 | note | Frequency - Each Lot
b2f55ca2-6a14-5a7e-82ba-84de49be30a1 | note | Acceptance Criteria - Submit test results on Aconex for every lot of Sub Base and Basecourse. Results to summarise each test (Moisture content, field dry density and layer thickness).
7bd5a9d8-f1f0-515c-9bd2-db15c58c3a89 | note | ○ Aconex ref to be submitted as Hold Point sign off.
37e3ac2e-1f70-5db3-af28-32a669466602 | note | Reference Documents - Cl4.21.2
c4470a88-b0fb-56dc-9525-ae5913364874 | note | Inspection/Test Method - Verify
e77eb85f-0ce5-5a4d-8372-d2a926cf0d3b | note | Record of conformity - Summary of results
425f643f-a056-5010-9038-22100d4cf06c | note | HP
199e0e4e-ff37-594a-a3d2-8836730d58da | note | Responsibility - Project/Site Engineer
76c8b366-beb3-55a7-bfb4-5516b9aae5c1 | date | Date Completed:
9cafd654-8c3b-5d53-b27f-4fd2723098a3 | textbox | Aconex Ref:
172816b0-0bf5-52f3-80f0-01074156ae49 | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
ed6b8455-38dd-51af-bd54-3125b5c47d2a | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
df9f428d-9eb7-515a-8ac0-5b3ec3fd6875 | textbox | Print Name:
f06a7fa1-f701-5396-b827-73e4dfa88863 | textbox | Position:
e17ead71-e36c-5c5b-8116-ea40ac9b8e17 | date | Work Completed On:
4f3c133c-1503-54e8-8324-f5dd13700c4c | date | Date:
177eeaad-3082-5a9a-a955-18da21d8a2ca | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0010-LOT-001 - Stage 1 - Pavement Type 1 - Rev 0 | itp | FH-ZU2-QU-ITP010-LOT-001 - Stage 1 - Pavement Type 1
518bd022-6f40-576f-bbea-4119f90755de | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
b3dbc564-f9cb-58c9-869c-b6ecf10bbc17 | checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
8aa88d4b-ee91-5ba0-8457-6ddccc0d3aa5 | note | Frequency - Prior to works
f596a299-9f58-53ca-9c69-525ee7c3cc5c | note | Acceptance Criteria - Current revision drawing is being used including the subcontractors copy. Current Revision to be obtained via Aconex.
e63a70e3-79b5-5073-95c3-410eeed9d6ef | note | Reference Documents - Aconex
66c5096d-0ffa-51b0-b947-f747cf16c41e | note | Inspection/Test Method - Visual inspection
5576b08f-da41-5fb2-928c-3099cdaa6f44 | note | Record of conformity - This signed ITP
bd555431-cb25-5b36-b645-bdbb62cd6733 | note | HP*
3b038d3a-33f6-557b-82bd-e7cd92c4d207 | note | Responsibility - Project/Site Engineer, Superintendent, Foreman
2f246865-c5bc-5edc-9639-3718d72b4815 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
b0b243f7-51c3-55b3-a663-0dc1b1e0b83a | note | Frequency - Prior to works
f696c199-a47f-5990-bd66-7861ff848da2 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
94fa6461-840a-5ed1-8c42-e091c2be9c8f | note | Reference Documents - PSP, EMP, TMP, SWMS & WP
77b7ee44-7821-5616-bd18-d2ce2cac25ba | note | Inspection/Test Method - Visual inspection
63a96ffb-32b4-5e4b-8a97-562a0fa2a122 | note | Record of conformity - This signed ITP
af9cf847-45a8-50a3-a06c-f3aa247d5f84 | note | HP*
1bb9c244-d14a-5e0b-ad9d-5e50f2486391 | note | Responsibility - Project/Site Engineer
20fe73d9-f13f-5d4b-9540-7726d2227e41 | date | Date Completed:
b9437d57-cad2-5d07-86bd-bc4cd9694fa4 | section | 2.0 - Cement Treated Base Documentation & Trial
f713fe9a-9690-5e10-a912-023f37ca0459 | checkpoint | 2.1 - Submission of Mix Design
f84701ba-8df7-56a7-bbf7-fd0108956189 | note | Frequency - 21 days prior to works
4c9630b9-e2f4-5db5-896f-1a0e63df22cf | note | Acceptance Criteria - CTB material and test results to be submitted to the Principal’s Representative for review to ensure that specifications are met and are compliant, prior to the initial placement of the material.
e094d516-039e-569f-9119-c1c7926abfa5 | note | Mix design results will include:
6e374311-1c48-581e-bddc-512318494010 | note | ○ Cement sample should include a CTB material within +/-0.5% of the specified cement content.
7554aa82-ddbf-5f1b-bdd1-acb07d6ad61f | note | ○ Aggregates comply with either Section 4.4 or VicRoads Class 2 or 3 material.
74caf24d-bc49-56b5-a014-a303fa78a0dc | note | ○ Cement shall be Portland Cement Type GP or Type GB complying with AS 3972.
4bd42f13-d34e-5934-acc8-df754cb1cd35 | note | ○ 3% minimum Portland cement content by weight of the dry un-stabilised material.
0998a3e8-f98a-5b9a-be32-e00b897df493 | note | ○ Mean seven-day unconfined compressive strength of CTB to be a minimum of 5MPa and a maximum of 15MPa. No single samples are to be below 5MPa.
42cad487-7e07-5ecf-9580-c34b1c0004d7 | note | ○ Water to be pot
1b7669d0-aaac-57b0-96ea-a1fcdf6df9ca | note | Reference Documents - Spec cl. 5.4, Spec cl. 5.5 AS 3972 VicRoads Class 2, VicRoads Class 3
873572a1-d8cc-565f-94c0-b94eb417573b | note | Inspection/Test Method - Verify
a66909ef-0334-52a2-bb86-0d40152f53e9 | note | Record of conformity - Approved Mix Design Report
2a6c4f49-8b5a-554f-8666-bcb24bd3eb89 | note | HP
5f8594b4-a8be-5f85-bfc9-24cd96c89d3a | note | Responsibility - Project/Site Engineer, Principal’s Representative
6f53238e-be9b-5995-8685-fd629656dbea | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
66263921-7ec1-5447-8330-44ed2cae7d71 | date | Date Completed:
5b68e915-fa91-5491-8e7f-3cf5fa1c57e8 | signoff | AUTHORITY HOLDPOINT
b08682c6-b8e3-5977-9b10-3b486b29efa1 | checkpoint | 2.2 - Supply of Information on Materials Source
72c22c59-df34-5e6a-8aae-a691c8b99d03 | note | Frequency - Prior to works
f06bcd80-cb39-5f6c-b7ee-acc980e2837c | note | Acceptance Criteria - Principle Contractor to supply the Principal’s Representative with supply information regarding the source of the CTB material via Aconex.
8162544f-1551-5f20-8f89-31e412124556 | note | ○ Material information will include the material brand, material type, material supply source, and a supporting test certificate from a laboratory registered by NATA to prove material suitability for the Works.
0fa3973c-f303-515a-83ef-710cdaa6e7b0 | note | Reference Documents - Spec cl. 5.21.1, Spec cl. 5.21.1.1 AS3972
f426f090-b259-5e95-9fe5-efd9491e0e42 | note | Inspection/Test Method - Verify
f4fd7777-24a4-5e24-8f03-2efc20b3adda | note | Record of conformity - Approved Supply of Information Material Source
2c108637-99ea-5b69-8af2-367b81ad171b | note | HP
77f8cbba-a50c-5b3b-980b-bc14c923226d | note | Responsibility - Project/Site Engineer, Principal’s Representative
737f78ca-d449-5e8e-9300-55c08726cd26 | note | Principles Rep - Aconex: BecaCPL-GCOR-000790
2deff7dd-cb7b-5ccf-9592-103910360dfc | date | Date Completed:
2be119e5-29ff-5f1c-b5de-c6aec4a7e549 | signoff | AUTHORITY HOLDPOINT
a3b266d6-20d2-577d-8bcc-cd0d95185e7c | checkpoint | 2.3 - Production and Construction Trial
2237b766-5dba-5d29-821a-e23e772d006b | note | Frequency - Prior to works
3851ad88-0336-50bc-9701-1a660bba0fbb | note | Acceptance Criteria - Construction Trial for CTB mix to be undertaken by Contractor and reviewed by the Principal’s Representative.
a16ae413-4a25-567f-a41e-e6d4836ce8bd | note | ○ Trial of CTB will be based on the first day of placement. Construction procedure to be reviewed and updated if there are any non-conformances associated with the initial trial.
b2ee570e-0077-5e08-a6d7-b9ab0e54b482 | note | ○ The size of the trial area shall be a minimum of 3.5m wide and 50m in length.
92a07a74-804e-50e3-927c-8e7863345b9a | note | ○ The CTB trial area may form part of the completed works.
9c4ed211-657f-57d9-81c5-2446d3c19ac0 | note | Reference Documents - Spec cl. 132, Spec cl. 5.6
717ed14e-d0fa-59c1-bb81-5da36d688f29 | note | Inspection/Test Method - Verify
2dee421f-a4d7-599a-92f8-3f4f57c30792 | note | Record of conformity - Approved Construction trial report
aae278da-12eb-5ac9-aa6e-efefd64eccb1 | note | HP
22a01488-e3ea-50b4-87f1-af2f3639ea98 | note | Responsibility - Project/Site Engineer, Principal’s Representative
05718d70-ae85-54e4-8dac-399b72b5185c | date | Date Completed:
b511eb0c-9811-5b67-89e8-b06a8ab74610 | signoff | AUTHORITY HOLDPOINT
36dd2170-94f3-5210-af3d-9abe62a51461 | checkpoint | 2.4 - Placement of CTB Methodology
8f31af96-a04d-519f-825d-c89d24070a0f | note | Frequency - Prior to works
22af0bf6-e6a7-533b-8b84-023de9149711 | note | Acceptance Criteria - Prior to placement of CTB the Principles Representative shall review this Work Method Statement for proposed methods of placement, compaction and curing
668d3fd8-fac2-52af-8caf-cb2488203135 | note | Reference Documents - Spec cl 5.9
9de3b2f3-7747-5f3c-baa3-785a2747e99a | note | Inspection/Test Method - Verify
c9bf8592-c08d-5316-bb18-160a3df6be87 | note | Record of conformity - Aconex Sign off
86c48c51-5b11-53ec-8c30-3f290786b3b5 | note | HP
da4ae08c-fac7-5e47-93e1-6f347419f540 | note | Responsibility - Project/Site Engineer, Principal’s Representative
7786b41c-8d21-537b-9856-adcc3eb88695 | note | Principles Rep - Aconex: BecaCPL-GCOR-000810
58f6c910-c461-5b65-a59d-decf015fc5c0 | date | Date Completed:
d887b5c3-5f02-5d22-ace4-5123e7694541 | signoff | AUTHORITY HOLDPOINT
ce085ba5-14a6-5251-aa31-3e4c7b381a10 | checkpoint | 2.5 - Provision of Material Samples
f34ea86e-e126-502d-b7d8-799a4d4501b1 | note | Frequency - At Least 5 Days Prior to works
dd7bb70d-a2b5-55c9-94b4-8dfc76fad08d | note | Acceptance Criteria - Principal Contractor to physically handover reference samples to Principal’s Representative of the approved CTB material. To be truly representative, the reference samples will be taken straight from the supplier of the material.
0c874d56-cf4b-5428-a181-0fb5c3e72280 | note | ○ The reference samples shall be divided into two representative portions, with one being held by the Contractor and the second portion by the principal until completion of the Works.
a7eaa790-89eb-560b-bb6a-42b034b9f4b6 | note | Reference Documents - Spec cl. 5.21.1.2
4123a350-addc-57f1-bedd-545a3336c7ad | note | Inspection/Test Method - Verify
e3479ff3-9d0e-5684-8e1e-0bf3b53ff2f0 | note | Record of conformity - Handover of Reference Samples and Aconex sign off
da9049f6-a774-5ab7-b2b1-03431ba9fadc | note | HP
92c0e4db-5ee2-5bbb-a183-8fea440ae72a | note | Responsibility - Project/Site Engineer, Principal’s Representative
ba3782a7-3abb-5d95-b86c-c78ef690149a | date | Date Completed:
ce0e26d2-cdbc-5212-b7b6-711abae7313d | signoff | AUTHORITY HOLDPOINT
3a93befc-813a-54fa-93e6-ed544f594f7e | section | 3.0 - Placement of Cement Treated Base
e6432367-fc0d-5d29-92fc-3e7e2637f723 | checkpoint | 3.1 - Subgrade, Basecourse Preparation
1d26deef-fe2e-5fdb-a424-a3909955245a | note | Frequency - Each lot
90173b31-4a14-50e9-93e3-3fed40bb5797 | note | Acceptance Criteria - Existing surface of subbase is maintained in compliance with tolerances on surface smoothness and level. The subbase is clean and clear of any foreign matter before the placing of the CTB.
c310d359-b226-5439-8830-9bf651637b3d | note | ○ Principal’s Representative will be notified 24 hours prior to the placement of CTB to allow the subbase to be inspected prior to the placement of the CTB. This will be recorded in ITP009 – Unbound Pavements.
65fd1623-8231-5854-aa9f-5cda3e8b9715 | note | ○ Principles Representative to be notified of the intention to place CTB.
b1ae7aca-a8e4-5915-b171-70d23878625f | note | Reference Documents - Spec cl. 5.7, Spec cl 5.9
35910732-4634-5050-a1f3-a7e82e567390 | note | Inspection/Test Method - Visual Inspection
a9a3fb03-d34e-5643-aeab-c7f7c06b097d | note | Record of conformity - This signed ITP
0061e970-f3a6-5f64-861d-4a3562876699 | note | HP*
b5dc517c-d7f8-5f6b-b8b0-6a317bdab769 | note | Responsibility - Foreman, Site Engineer, Principal’s Representative
de55df49-5ade-5de7-908d-27572a37eefb | date | Date Completed:
d5f5265f-9acd-5150-85f4-b8e0fd5c4c1b | checkpoint | 3.2 - Layer Placement Parameters
15d20a59-abb9-5a63-bbbb-ae10c247e7e7 | note | Frequency - Every Lot
a7549654-01da-5468-98c6-45fd6149d6b2 | note | Acceptance Criteria - Summary of Parameters for each Lot;
9b307856-48e1-5148-b00c-36535f9c5285 | note | ○ A lot is defined as one layer placed in a single days production of uniform material
443263a8-e71e-5b88-afb4-8b92e59bb419 | note | ○ Max Layer is 200mm
bed1a5bc-d098-5239-b2e4-030a8525d7c3 | note | ○ Min Layer is 100mm
187f4fc7-665d-5338-8487-8e92b1d07d02 | note | ○ Final Surface Level +0mm, -10mm (excluding intermediate layers)
7171547a-ee6b-53d6-b20f-7d3ad0a0d8c9 | note | ○ Shape: every 10m intervals, <7mm deviation over 3.5m straight edge (excluding intermediate layers)
01ea9862-06c3-54c0-8365-67d7ef6c4f5d | note | ○ Material is batched within 1% of OMC
154ea760-0093-5671-9a15-c4fb065e211a | note | Reference Documents - Spec Clause 5.9
23e30d10-91f9-5caf-bf9a-50c0b7a25197 | note | Inspection/Test Method - Visual Inspection
e3db2985-1629-55b1-86de-615aa90f8bca | note | Record of conformity - This signed ITP
92da49e6-752c-58e5-a3a5-368767d9eadc | note | IP
131f5628-0346-5a4c-830c-ee5d14e15223 | note | Responsibility - Foreman, Site Engineer, Principal’s
cc2418e7-c804-5128-ace2-e40bde4c6554 | date | Date Completed:
a791ad98-de04-56f3-baea-854bfe3fec6e | checkpoint | 3.3 - CTB Placement – Weather
a8945776-a6f4-5b36-b3fe-925c329ce3df | note | Frequency - Each lot
527d722b-c5b1-574b-81b0-1a2b37349e23 | note | Acceptance Criteria - Weather to be check prior to placement, CTB shall not proceed when;
8b6f23cb-bdd6-52db-9b80-19f7c3a85136 | note | ○ Ambient temperature is below 5°C
b5a25fd6-d1a7-555c-a444-784f86bdf94d | note | ○ Temperature is over 35°C
abb0ce29-4364-5f04-86af-c2c1030115d2 | note | ○ Heavy Rain fall is forecasted
e8bd97b5-51ed-58e4-b56f-93694ea86fc5 | note | Reference Documents - Spec cl 5.18
17631fb5-c95b-50f9-96d9-c8cb7cd5a4ae | note | Inspection/Test Method - Visual Inspection
d44b3070-6831-5703-af8f-496e3889538e | note | Record of conformity - This signed ITP
77032644-9c84-5d86-8fa0-8438ebe70d20 | note | HP*
19904e0d-6cd6-551f-af45-e992a7ccbd14 | note | Responsibility - Foreman, Project/Site Engineer
ccba4635-1cdd-5b1f-84fb-6f07cec24b9c | date | Date Completed:
a990dc3f-4e0f-51d5-8138-9ebb78589eff | checkpoint | 3.4 - CTB Placement – Checks
1bb2aa2a-c4ff-561d-a13d-7afbe13bc904 | note | Frequency - Each lot
32f8ef17-8490-50c9-9251-810682a3751a | note | Acceptance Criteria - During CTB placement Activities check;
40f02693-c8d1-535f-a199-ece05f6f73b8 | note | ○ Placement starts on the high side or crown of the layer where practical
048bd7c5-c004-55da-9bc4-93e115f79601 | note | ○ Material is spread in the direction of Taxiway across full width
4f433ccd-ee6c-524f-b818-eae38e7377da | note | ○ Underlying layer is not disturbed during deliveries
d08de34c-ea7f-583a-b415-47e596003fb9 | note | ○ Inspect Material for any contamination through placement activities
a61ff818-105d-5a4e-8680-ff9d042ce44a | note | ○ Adjoining layers are a clean face / vertical
8df5403a-2649-51c2-a3ad-c7303e4bb19d | note | ○ Segregation does not occur
b355b70a-b0ac-5a92-b3ac-1b8a400fe4a1 | note | ○ Placement to be completed within 120 minutes from time of batching and before concrete has obtained its initial set
f4942690-8cd5-558c-9f3a-44274fe159c5 | note | Reference Documents - Spec cl. 5.9 AS1289.5.2.1
b574633f-2bb1-5d4e-950e-ff2484b56389 | note | Inspection/Test Method - Visual Inspection
60226c75-b0de-5c5b-96e9-8673327b422c | note | Record of conformity - This signed ITP
b828ff37-ec7f-50be-94b1-ee32fc7cc07b | note | IP
d1b766ef-1c08-5b21-b039-7f9ab4683bf1 | note | Responsibility - Site Engineer, Foreman
2654885b-329c-5964-89f4-e465307a4a9b | date | Date Completed:
7401f6c4-9bed-5d6f-b4ec-db03b8a866c1 | checkpoint | 3.5 - CTB Compaction – Checks
d318849b-5618-597c-91b3-814e52d4f0e1 | note | Frequency - Each Lot
ae30e580-e65b-59b1-93b6-ceb7450cd2f2 | note | Acceptance Criteria - During Compaction check;
b10036b6-d4c3-53e6-a7dd-623f106280d5 | note | ○ Heavy smooth drum roller of 15t to 20t is used for initial compaction
d1f1c126-533a-5e6a-8dc4-2e235688e671 | note | ○ Pneumatic roller of 27t will compact material for final consolidation.
05876ce7-e80b-5055-948b-92633bd9b857 | note | ○ A heavy smooth drum roller (in static mode) may also be used for final consolidation
8a9f03d1-75fb-512e-bbdb-7318c1488415 | note | ○ Watercart present onsite for conditioning
65490f31-31f1-55fa-ba27-62cb0064acd3 | note | ○ Materials are trimmed to required shape and level
18e147eb-3edb-5867-bda3-b7734942fa05 | note | Reference Documents - Cl 4.10
a5cc52f2-9ea2-51e1-9d76-86f779782816 | note | Inspection/Test Method - Verify
4ed1fdbe-a813-5556-8b34-fa80b91e4a55 | note | Record of conformity - This ITP signed
d2cb62fd-45c5-53ba-a041-c81c964b747c | note | IP
8ca58966-39f3-51c1-9bf7-7cfb7924a9f8 | note | Responsibility - Project/Site Engineer
7d2e2bd3-99ca-5153-891e-45c4cf8e6ee3 | date | Date Completed:
2bddfd15-ae28-5cbe-bfb1-25a7421f7b98 | checkpoint | 3.6 - Curing & Protection
d9202bed-4ccb-5e6c-8eae-441e32bd0d2a | note | Frequency - Each Lot
3d18e78a-fbc1-525b-822e-0dad77056df3 | note | Acceptance Criteria - Curing to commence as soon as CTB has been placed, compacted and trimmed. No plant (other than curing) to track across CTB for minimum 24 hours.
3ff88ce5-7c4d-55c3-8a20-b2077108bb2f | note | Curing to follow one of the below methods;
426e9ca7-487a-5f20-a6ae-ffdc3fd8f5d4 | note | 1. Wet Method: This will involve a watercart lightly spraying the CTB surface for minimum 7 days.
ac0408e5-01eb-511d-bec8-72574746a26a | note | 2. Debonding Coat: The CTB will be covered with a bitumen curing compound. In locations of PCC, will be the C170 seal with 7mm aggregate.
dcc282aa-d774-5d32-a21a-2340833e3a7f | note | Reference Documents - Spec cl. 5.15
c185cb39-41db-5b74-bf4b-58039a1d2486 | note | Inspection/Test Method - Verify
5ed27476-046b-5d4c-91f4-9d6dc280e91b | note | Record of conformity - This ITP signed
4127c5e4-b820-5275-befd-3ba282773570 | note | HP*
90a1f255-e2f6-5258-82f4-a6608d585ead | note | Responsibility - Foreman, Project Engineer, Site Engineer
b29214e6-d20d-57e7-b892-48164a53e9e0 | date | Date Completed:
6e009c69-70d7-514c-b44e-f3bb3867a1e3 | checkpoint | 3.7 - Post Placement CTB Inspection
c133101a-b607-579c-b4f9-2cf71ca93f9b | note | Frequency - Every Lot
a7f09b74-8c7e-5e9c-8c19-390ba5710f6c | note | Acceptance Criteria - Prior to the application of the succeeding layer or installation of the de-bonding coat, CTB final surface is to be inspected with the Principle Representative
3dd631f2-a2a1-571d-a620-d5d946c8b5bb | note | Reference Documents - Spec cl. 5.9
84554310-d991-5d29-82f6-a3c07c5d5599 | note | Inspection/Test Method - Verify
09e8586b-eca6-5d3a-a226-2bcb388209a4 | note | Record of conformity - ITP signed
5ccaaf5a-f383-5dcb-9802-a10733a58443 | note | HP
905e8200-14cf-53ec-a676-f2ddc9f34212 | note | Responsibility - Project/Site Engineer, Principal’s Representative
d7a8daed-5a8c-5363-9fc5-cd375d53fabb | date | Date Completed:
1fbbaaa5-dcbd-58a7-a340-05841913c755 | signoff | AUTHORITY HOLDPOINT
131e830c-80ee-5bfa-ae6d-3cee6331c53a | section | 4.0 - Acceptance, Compliance, Controls and Quality Assurance
99e681f2-8a6c-56a0-be58-12603b6f7477 | checkpoint | 4.1 - Field Dry Density
f03186bd-59c9-5281-b6ef-20321711d5ed | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
102f1ebf-e51b-5ed9-ad43-a0896478ebdd | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
f5ceefec-34de-5727-916e-0b288c1aabd4 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
803c9230-1f43-5b08-9bac-c416ef40d10d | note | Acceptance Criteria - Average of Specified Minimum Dry Density Ratio (SMDDR) of 97% of the Maximum Modified Dry Density
0f72bb26-c4ac-5f47-9353-d47361c2c94d | note | – Average Equals or Exceeds 96% with no individual result be less than 93%. The lot will be accepted.
54e288c2-afc9-5831-bdd3-c814dbafdac1 | note | – Average Equals or exceeds 96% with a result being less than 93% - an additional 4 tests will be taken
7422857c-dbf4-5cde-8fcd-7a9eebb01ddf | note | – Average is less than 94%, the lot will be rejected
58937cc4-12d9-5cda-a665-45ab2a8da7e5 | note | – Average is in between 94% and 96% - an additional 4 tests will be taken
a9f58864-2561-54a2-bfa0-dab77c1e7259 | note | Reference Documents - Spec cl. 5.10, Spec cl 5.21.2.5
28029483-eb30-5e34-b3a9-ed80ee976a2f | note | Inspection/Test Method - Verify
71a6959e-311c-5755-aa07-77880c544a37 | note | Record of conformity - This ITP signed, Test Report Attached
16a6d560-db93-5e93-aac4-1ef0e3b58824 | note | TP
4d63e4ce-61af-549e-93cd-88e90439f6fe | note | Responsibility - Foreman, Project Engineer, Site Engineer
d729f33b-569d-5d94-bf25-bde0399b776e | date | Date Completed:
c083058b-dae6-5e3d-a513-cc68f715ae5a | checkpoint | 4.2 - Moisture Tests
48e1392d-43e6-58f5-af5e-7dedfde8269c | note | Frequency - Each Lot One test every 500m2 (or 250T) or part thereof
06c7fffd-057a-5683-a5f7-8a8c381a276e | note | ○ Minimum 4 tests for Lots under 800m2 (or 400t)
2b0ffe7c-a0d8-59f6-bebc-62ca95b1f694 | note | ○ Minimum 6 tests for Lots over 800m2 (or 400t)
ebec3e40-e3e6-5a4b-9711-f0369aaf6a53 | note | Acceptance Criteria - Target Moisture content of +/-1% for information only. Production of CTB to be within 1% of OMC.
b5ab453a-a9ac-5e01-bf8f-b88b1b412688 | note | Reference Documents - Spec cl 5.21.2.5
31eba2f8-121a-5f0a-9bbd-1df0d0fcd5d6 | note | Inspection/Test Method - Verify
1d86b1f4-11bd-5c0c-9580-e4d32aaf98f6 | note | Record of conformity - This ITP signed, Test Report Attached
6a896df5-fbe0-5c11-9572-3ea136c6b665 | note | TP
dd17bd53-ffd2-53b4-ac3a-23be9eb1f240 | note | Responsibility - Foreman, Project Engineer, Site Engineer
da840038-f33d-5214-8629-cc69fb864320 | date | Date Completed:
435a97a0-8348-5acf-b9b1-f34f54f87f6c | checkpoint | 4.3 - Strength Testing
27bc8c7e-95d1-5dcf-88ae-82823e1085d9 | note | Frequency - Each Lot, divided into four approx. equal sub-lots
2fddab20-aeb3-51af-80f7-3033426b797b | note | Acceptance Criteria - A total of 4 sub-lots will be taken as samples, with 2 being used for the 7-day strength testing, and the remaining being used for the 28-day strength testing. 28 day results are for information only.
53e841bf-eed4-57b9-9fbd-fd88b73d2b2a | note | ○ The mean 7-day unconfined compressive strength of the CTB shall be a minimum of 5.0MPa and a maximum of 15.0MPa. No single sample shall be below 5.0 MPa.
2750053b-5e5b-527a-927e-8e87f4aab69a | note | Reference Documents - Spec cl 5.11, Spec cl. 5.21.2.6, AS1012.9, AS5101.4
520a4d5f-8343-5414-af26-941844343fab | note | Inspection/Test Method - Testing
51ba2912-8e23-5929-9c94-7c2fc5b9173a | note | Record of conformity - This ITP signed, Test results
102a9d58-c7cf-58d9-a254-e2b57c059a11 | note | TP
62c9a368-385e-5f8a-a5fd-3173b78cbeb5 | note | Responsibility - Project/Site Engineer
cd63fc81-2748-5204-8c71-1ecdc8d7094d | date | Date Completed:
a63f0532-32bb-5725-9bef-0a20b43e1e13 | checkpoint | 4.4 - Process Control
c610b4ae-a285-5c6e-8fcd-207cb4c478c1 | note | Frequency - Each Lot
139d6cc6-0860-5d37-84ea-5eec2d18cc61 | note | Acceptance Criteria - CTB production and process control test results to be supplied to the Principles Representative
4cf57679-b162-55ad-abc5-71060624730a | note | Reference Documents - Spec cl. 5.21.2.1
a2362452-e6b9-50cc-8ab0-15193aa438e1 | note | Inspection/Test Method - Verify
6b11e16c-b89c-532c-8d84-0dde9b1f6e07 | note | Record of conformity - This ITP signed
f14b3625-4f6b-54d3-86cd-83ac17befadb | note | IP
cbabd8ff-86fb-5ea7-adaf-3d9bcd3a5cc2 | note | Responsibility - Project/Site Engineer
81b3934b-4a7c-5973-9a83-ac3ddb5484e9 | date | Date Completed:
2bcbf63d-6c13-5d63-acf0-f62700f979cb | checkpoint | 4.5 - CTB Layer Thickness
1799115e-1fc2-519a-85de-f01907f95ab3 | note | Frequency - Once Every 30m2
fb01f919-1253-50b5-bafd-444151f02c79 | note | Acceptance Criteria - CTB layer thickness to be measured, recorded, and included in the Quality Assurance records. No CTB layer thickness to be less than that shown on the drawings other than allowable construction tolerances
86aed6fe-a7e1-5bbe-b54d-a6febb6dcee1 | note | Reference Documents - Spec cl. 5.21.5, Spec cl. 5.21.7
1751b0ea-39bf-557f-a987-76db1c978ff5 | note | Inspection/Test Method - Testing & verify
8f655c65-eeac-573b-a41b-ff7a4763d512 | note | Record of conformity - Test results & this ITP signed
1edaa5b4-7fe2-53f7-904d-ef6ccb84713b | note | IP, SCP
440d35fd-e0b5-5913-b784-e8a1609522a6 | note | Responsibility - Project/Site Engineer, Site Engineer
8486d6a6-edbe-5b6f-ad1b-e3320c99b948 | date | Date Completed:
a65f8491-197d-5f8d-98e9-df0607f9802b | checkpoint | 4.6 - Quality Assurance Records
e28ad406-42b3-54df-bd45-1d533d8a6992 | note | Frequency - Each Lot
6bff1fb8-fc6a-5245-be5d-b0d34882f2da | note | Acceptance Criteria - Provision of ITP test reports must be submitted within 60 days after the completion of the Works. Principal contractor to supply electronic copy of reports detailing the results of the quality control and testing undertaken.
ff73a1e8-da4b-56d3-b9ad-dd3e0a5b5867 | note | ○ Reports to be transmitted on Aconex and Aconex Reference to be quoted as Hold Point Sign off.
901e3f69-22d4-5dff-a8fb-4777b97224e0 | note | Reference Documents - Spec cl. 5.21.3
dbe748d1-13fc-59a6-b11a-3fde2f3eafe5 | note | Inspection/Test Method - Submission of ITP reports
d186873f-c9c4-57e7-a8a6-10ef7c2b1f91 | note | Record of conformity - This signed ITP
ddbf53ba-4ba6-5162-a876-1db4a0b8cda0 | note | HP
6a8940a0-674a-51b8-a949-c153ebc3521f | note | Responsibility - Project/Site Engineer, Principal’s Representative
d26e1c20-cd8c-5956-8617-743c63ff978f | textbox | Principles Rep - Aconex Ref:
a6b55153-f7f0-5005-ad8c-0083e0fd459c | date | Date Completed:
ad2de4d9-5721-5145-9475-1d1edaefaba1 | signoff | AUTHORITY HOLDPOINT
39c190b7-b116-57f8-a2a7-da1cc234c6f0 | checkpoint | 4.7 - Survey As-Built Report
2275ba0b-0e87-5dba-a66e-9441454b85ae | note | Frequency - Each Lot
dbb59df4-c843-56b6-8c73-5f8a99b22177 | note | Acceptance Criteria - The surface level at the top of the final CTB layer shall not deviate from design level at the specified points by -10mm or +0mm. Contractor to provide Survey Conformance report of completed CTB surface layers per Lot.
61d1d193-4712-5f16-853e-4cf7e99a2d55 | note | Reference Documents - Spec cl. 5.17, Spec cl. 3.14.2
c5212fbd-57c5-5049-9e22-15468fa5c769 | note | Inspection/Test Method - Verify
b30b9298-b275-527f-83c5-0965084bdb9c | note | Record of conformity - Completed drawings, survey report, & this ITP signed
a9cbc0bd-f47a-5f26-81e9-5f5cb769aaf6 | note | IP, SCP
3d2bd58c-980e-593c-8704-511a08c99272 | note | Responsibility - Surveyor, Project Engineer
c5056a76-945c-5f08-b874-d76e1d320dbe | date | Date Completed:
0f7f576e-520a-5643-9fc4-f169fffc004d | checkpoint | 4.8 - Surface Smoothness
5d4acac4-2875-5596-93f5-1a785ba3e054 | note | Frequency - Every Lot
93786c44-4ebd-54d3-aca1-951acc07afb5 | note | Acceptance Criteria - Surface smoothness to be checked every 10m by placing a 3.5m long straight edged on the ground a checking any deviations over 7mm. Complete within 7 days of completion of each section. Document results.
91fb8cd2-d46e-5227-b807-708f1a461489 | note | ○ Intermediate layers and shoulder pavements are not required to be checked.
c01c18c5-37ba-58b4-a6a2-642d82ab94c0 | note | Reference Documents - Cl 5.17
58c12aac-2d98-5ac4-b686-7c9e9cfaa8e0 | note | Inspection/Test Method - Verify
ed18d16e-eb2c-55be-9c34-5b2c4fd34347 | note | Record of conformity - Report
3b7bb992-09a4-5bdd-9c10-fcc45ede27d4 | note | TP
f9ae33fc-2416-5f39-a778-8195e2fb3791 | note | Responsibility - Project/Site Engineer
effa941f-c08e-5def-b3a5-5ecdab676233 | date | Date Completed:
c801c62f-58a1-5837-8f7c-89512b249fce | checkpoint | 4.9 - Correction of Nonconforming Work
9ec784eb-353e-506d-9619-b27d85a09297 | note | Frequency - Each Lot (if required)
369bd2a4-9673-5e6f-b9a7-c89bb20602c2 | note | Acceptance Criteria - All CTB that do not meet all the specified requirements will be rejected by Contract Administrator. Materials to be removed full depth of the layer and reinstated, unless otherwise approved through the NCR process.
ac35cc23-2d07-57ea-aa08-9d3098856e40 | note | Reference Documents - Spec cl. 5.21.4
99ba277c-f48e-501e-89c3-e4675b0c7544 | note | Inspection/Test Method - Verify
55f90695-7572-5a0e-8395-fe465a26db9f | note | Record of conformity - This Signed ITP
db96ea5a-921e-5ed5-8c15-2a19c2d9a5bd | note | HP
6a3f2218-7f09-5a57-b7a7-c49b0d52d177 | note | Responsibility - Project/Site Engineer, Principal’s Representative
dba5f565-ca20-52ba-aca1-c9ea7c152251 | note | Principles Rep - (if required)
e18f55d4-6a0b-5027-bffa-6021233c4d87 | date | Date Completed:
a1f73c0c-47cf-52f8-abb9-28b1f1690f2e | signoff | AUTHORITY HOLDPOINT
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
f9a7189c-b860-50c9-ac40-38214720411f | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
2ed5916a-4453-538c-a5f9-3dc1b4870a03 | textbox | Print Name:
3b7bd65a-2e57-5fdf-babf-8993d668d7c2 | textbox | Position:
90d84dfb-f506-5b4b-b2a3-b1f9ce2894e4 | date | Work Completed On:
bbf80422-452e-53b5-8e68-f944166304fe | date | Date:
cf51d2f2-2033-5b12-9a4c-aaa56a5e7f9f | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0019 - Spray Seal Placement - Rev 0 | itp | ITP019 - Spray Seal Placement
6607cab9-33c5-558e-bbf8-f1706ae449f8 | section | 1.0 - Preliminary Works
fbd6ef58-7046-5030-bc38-d0da69c3974d | checkpoint | 1.1 - Check for Correct Documentation
0338091b-6849-5e91-ab24-288d05799d5a | note | Frequency - Prior to commencing works
f1c4bcfa-15fd-5082-b518-2f6bfe1a3c25 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors. Current revisions of these documents to be obtained via Aconex or ACC.
56761984-8b52-53a8-8822-50c863d43498 | note | Reference Documents - Current Revisions in Aconex or ACC
099c6cc3-ecd8-5d83-943e-4562fd5208bb | note | Inspection/Test Method - Verify
ade0a277-7020-5d2a-94b7-a292ef5478ea | note | Record of conformity - This ITP signed
341e8386-6719-57f2-9a54-37739b8f945d | note | HP*
19df1e36-01d3-55c7-becc-a83a2fa2c7cd | note | Responsibility - Project / Site Engineer
9349017d-0618-575c-bdb4-e285fd401f19 | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
d1bf2877-da5f-5876-b9fc-c31847f95bea | note | Frequency - Prior to commencing works
4e20f32d-dc92-5a56-b3c1-2592d032165b | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
f0514b64-ef11-5406-929d-d307acb2e68d | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
c5f9c362-259a-5a8a-bbd2-7ebdb8121eac | note | Inspection/Test Method - Visual Inspection
33394019-6e12-5d23-b044-82b76ee325ec | note | Record of conformity - This ITP signed
8b086da5-1a28-55e3-9f11-214f144f4571 | note | HP*
07c91057-9fde-53ba-8f80-73b73e39e6df | note | Responsibility - Project / Site Engineer
da1eeaf7-6b98-5193-a3b1-5f6458c1cc1d | date | Date Completed:
01fe0f38-b21a-52fb-bc33-d24ffdce9887 | checkpoint | 1.3 - Plant & Equipment Check
52451bc8-8fa5-5227-98c8-d3d0deb939fb | note | Frequency - Prior to commencing works
24b5ade8-68a9-5ac8-8c5c-b3ad20d181d6 | note | Acceptance Criteria - All equipment shall comply with VicRoads Section 408 and VicRoads Bituminous Sprayed Surfacing Manual.
83e8ea0d-fb35-5495-bcd6-9dca4a47221c | note | Reference Documents - Beca Spec 002 - 12.3
89d0dc0a-2ecd-5b17-a449-754396782cf9 | note | Inspection/Test Method - Verify
cb9e460a-9837-53ce-8921-e8afd339d828 | note | Record of conformity - This ITP signed
62f23a0d-83b7-5f21-9d28-1247cadf1ffe | note | HP*
0383f368-68bb-55dd-bbec-c764949d16a5 | note | Responsibility - Project / Site Engineer
db217685-0cc4-532c-8d74-629561e88330 | date | Date Completed:
378e9cc1-cd99-5625-8321-b480ee1a80c6 | section | 2.0 - Materials
7f7d3002-dbbd-5bba-8b90-ca19482036fa | checkpoint | 2.3 - Material Approval
36048218-ebba-5b75-bc93-16bd0d21a04b | note | Frequency - Prior to Works
9588d36e-1d96-5a41-8af8-fd13ad0ea4f6 | note | Acceptance Criteria - The binder used shall be class 170 residual bitumen complying with AS 2008.
9938bcd9-e8ca-5533-953c-1bc2616e5baa | note | ○ All aggregates used shall comply with VicRoads section 801 and 831. Material and Test Reports to be submitted to the Principal’s Representative prior to commencement of works.
c3abd480-94e4-5797-ab62-34fda3bddc67 | note | Reference Documents - Beca Spec 002 - 12.6.1.1 to 12.6.1.3
03b20b15-37cb-53e4-96e6-3c6595c4898c | note | Inspection/Test Method - Verify
6ad33181-3bc4-5705-a55a-b1b9497ff0a0 | note | Record of conformity - Test Reports, This ITP signed
cf0e6f2b-dc71-5d10-a3eb-9f65f11eeb28 | note | HP
53ae5648-9273-5cc6-ac92-b31bb6c24af3 | note | Responsibility - Project / Site Engineer, Principal’s Representative
6440aab1-856c-57ff-bc25-7f7131fba383 | date | Date Completed:
c0fb703d-700a-51c3-aa97-5c9392cf120d | signoff | AUTHORITY HOLDPOINT
d7be73a1-96ee-543f-9d6a-da9f3eb56961 | section | 3.0 - Construction
84b31f08-968f-52e4-a569-422bde1a1ac6 | checkpoint | 3.1 - Underlying Surface
3eebee34-1fbe-5403-8c42-4d4010c12a81 | note | Frequency - Prior to works
c419e70b-0b7b-5980-bce7-7cf2a80ae7fa | note | Acceptance Criteria - The pavement surface should be cleaned to remove all mud, carried on material, dirt and dust.
12e9e198-9b63-5054-8528-6b47f4eeeb04 | note | ○ After cleaning the surface should be swept with a suction sweeper, supplemented by hand brooms where required. Seal coat should only be applied to a sound clean dry surface.
35b9ca1f-8b6b-5878-9d6f-9221cb439ce7 | note | ○ Preparation of the underlying surface shall be approved by the Principal’s Representative.
0ac039db-423e-5f23-9e6f-c0268094e410 | note | Reference Documents - Beca Spec 002 - 12.4.1 to 12.4.5
3f8554d4-dc75-5643-8404-1463684c4e6c | note | Inspection/Test Method - Verify
f0ceec3a-c604-532f-871e-a530b25eb790 | note | Record of conformity - This ITP signed
c1d1704e-a365-5d2e-b5db-817215969479 | note | HP
416e0906-13a6-5ba4-b20b-b4087b73c12d | note | Responsibility - Project / Site Engineer, Principal’s Representative
f8a2683b-6a39-5341-9d92-90c14da8a1d5 | date | Date Completed:
486e988a-6d15-52f1-be0b-9d2371ced570 | signoff | AUTHORITY HOLDPOINT
d0b185fe-eb3f-560c-94a2-ac66313efd10 | checkpoint | 3.3 - Binder and Aggregate Application
46d85ea1-c304-5100-9c87-246ff6a83c14 | note | Frequency - During works
6a161514-f2d1-5174-9d98-2c10b3b48112 | note | Acceptance Criteria - Application rates shall be:
fe593034-64be-54d4-90d4-5c3eaaf31146 | note | ○ Binder: 0.8 – 1.0 L/m2
9d2c2fa6-d5e5-5f58-ae4b-3ff7166eb06f | note | ○ Aggregate: 8 – 10 kg/m2
a9f893e6-e430-59e5-8f3d-4782d9c75631 | note | Reference Documents - Beca Spec 002 - 12.6.2
e608d166-4c9c-5617-8ef6-8875835087e6 | note | Inspection/Test Method - Verify
c53d96b2-ca83-5b49-8488-179c251e1ddf | note | Record of conformity - This ITP signed
80c1be45-e4cd-5346-88de-53cd36ff02be | note | IP
087e4ab6-8a1e-5869-bdab-146f2b456660 | note | Responsibility - Project / Site Engineer
2c140901-e263-550e-8106-6da5f1b5b88f | date | Date Completed:
b202e282-3595-59ac-b16a-e799c765ba53 | checkpoint | 3.4 - Aggregate Spreading
360de500-a0c3-58ae-9e44-5cf64aec2ab6 | note | Frequency - During works
da6cba42-dc9a-5cc3-9313-f781c145627d | note | Acceptance Criteria - All aggregate spreading shall be undertaken using forward aggregate spreading and discharge plant.
361fa8c1-eba4-54dd-a451-62c80444a098 | note | Reference Documents - VicRoads Section 408 – 408.13(e) to 408.13(f)
19f40917-c682-5fb4-9902-726e9cfce912 | note | Inspection/Test Method - Verify
010672fc-b6b3-55d1-b9b5-768da0e2f368 | note | Record of conformity - This ITP signed
66a42d9e-9912-5e72-9f9f-47009903b973 | note | IP
6215b40e-1dbd-5998-b4df-ae2088f5401c | note | Responsibility - Project / Site Engineer
aa9fb1ce-a68d-5e5f-a943-677b79c35632 | date | Date Completed:
946d5fda-a1a1-5f46-9863-44dae4f5dd1a | checkpoint | 3.4 - Rolling of Aggregate
a43d4bb9-7058-5eea-ac7b-e5e628da8ef4 | note | Frequency - During Works
4518b789-9bf4-5581-beaa-0a0d4b093079 | note | Acceptance Criteria - Rolling of aggregate shall be undertaken over the full width of the pavement being sealed. Works to be undertaken by static rubber tyred rollers or otherwise approved by the Principal’s Representative.
7c58c4b2-29ab-5815-beca-47873a10793e | note | Reference Documents - VicRoads Section 408 – 408.13(g)
45fabd6d-a208-5ad3-8128-0653884c352b | note | Inspection/Test Method - Verify
8c9decdd-5dac-55ef-848f-12c23e105859 | note | Record of conformity - This ITP signed
9cea5468-74c7-5703-8b8e-8c1e4381a91e | note | IP
e6d83783-27c5-5256-8396-4ffbb37c539d | note | Responsibility - Project / Site Engineer
c3225380-19dd-5012-9895-f56263b181d2 | date | Date Completed:
26d067c2-aa89-5a54-bc39-3ef8a5d9d14d | checkpoint | 3.5 - Removal of Loose Aggregate
df14e7ab-bcbd-5004-af25-98c10d4ea0bf | note | Frequency - During Works
2a630df0-8c56-5d37-b998-cda5d3b73777 | note | Acceptance Criteria - At completion of sprayed seal treatment, the Contractor shall remove and dispose of all loose aggregate.
5abe8ced-7041-5092-9364-153adfb962f6 | note | Reference Documents - VicRoads Section 408 – 408.14
3cf93853-d5c7-5a59-9fb3-9c10d57b585d | note | Inspection/Test Method - Verify
a991d669-89b6-58dd-8128-79458c7a112b | note | Record of conformity - This ITP signed
c943f80d-44fc-5e60-b513-0646f5af80fd | note | IP
ce475f64-84c9-5d22-8531-52ebc44d3971 | note | Responsibility - Project / Site Engineer
ce7b8f6e-0579-5c75-980b-5f694f011b25 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
32497480-f3b1-5c2f-8a18-88a7a7a743b6 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
7628e703-c3b0-571d-b220-426fddfe55fc | textbox | Print Name:
90716a2d-8ead-50b9-91c7-b9f6ab0813d3 | textbox | Position:
d8ed759e-5f16-58e0-9e77-a58513e6c30d | date | Work Completed On:
bcae2680-09f7-5058-abb3-53df76875256 | date | Date:
e4d66131-e842-4969-8dac-30df36d96f43 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0020 - Prime Coat - Rev 0 | itp | ITP020 - Prime Coat
77c2a549-4048-4187-bf5a-cbd0237f6494 | section | 1.0 - Preliminary Activities
e6bd9291-ce69-4466-949c-d6d0d8063f8f | checkpoint | 1.1 - Check for correct documentation
3e28b716-2665-587d-86de-d28fb8b9dd9c | note | Frequency - Prior to commencing works
a2878d92-55b9-5fd4-9074-645b7059c720 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
72ffe1c9-9473-5a0f-acbf-9a9d3323b8df | note | ○ Current revisions of these documents to be obtained via Aconex or ACC.
83384688-a514-596b-9db7-8593f4d907f0 | note | Reference Documents - Current Revisions in Aconex or ACC
8c846aa3-c5cd-5a1c-a1eb-b0a775b09dc2 | note | Inspection/Test Method - Verify
15d02e57-f78c-514c-a965-2d6609a0fd06 | note | Record of conformity - This ITP signed
8ecf7fdf-6570-5673-9944-8f69427ae829 | note | HP*
601ab77e-f898-5cfd-a19d-b7aeeb9d630b | note | Responsibility - Project / Site Engineer
f8d67e0d-eef7-5796-9ba1-b0cd158e5a8f | date | Date Completed:
fac1c1be-542b-48df-a8fc-412903db3db8 | checkpoint | 1.2 - Implementation of all measures and controls
fd61bdef-3dc4-5478-950d-3f3ed5dd4fb4 | note | Frequency - Prior to commencing works
57674075-8edb-5562-8973-ef097f089d48 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
8ae25de7-7141-520b-9a1b-68cd7ba42fa5 | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
5956918e-348e-50e5-bae8-f6815a3cf00a | note | Inspection/Test Method - Visual Inspection
0c1cd28d-dfe7-5e74-af2c-35d58ef875c7 | note | Record of conformity - This ITP signed
3f65063a-8271-54bb-b412-d7f9668ad4cd | note | HP*
2c79d54a-6138-5731-b689-a14b68a4757f | note | Responsibility - Project / Site Engineer
bb0613ac-6d91-53a0-98a4-a15813d1100d | date | Date Completed:
c4372892-3c33-410f-a10e-314c6c8a4356 | checkpoint | 1.3 - Plant & Equipment Check
48b03e0f-1dfe-5a8b-bf87-ccaaeb4ea185 | note | Frequency - Prior to commencing works
dfe82327-01d7-5d90-b3af-65fd48c877b1 | note | Acceptance Criteria - The Contractor shall provide equipment for heating and uniformly applying the bituminous material and blotter material.
6c8b4d08-3b6f-5ca8-be4a-8fbe09eb8ffd | note | ○ The bitumen distributor shall comply with the requirements of NAS 70: ‘Bitumen Sprayers’
2024fdb5-2ab0-57c0-a846-3b6a65326676 | note | Reference Documents - Beca Spec 002 - 7.3
c82f184b-0e79-5f30-b0d5-c7f02464dda5 | note | Inspection/Test Method - Verify
c19e226c-977c-5c19-a6ac-a5c3bdc5dd70 | note | Record of conformity - This ITP signed
b0685503-e401-5ec2-beaa-424566373517 | note | HP*
98ee50b1-ed5d-58ec-a07e-e21c10fe35dd | note | Responsibility - Project / Site Engineer
9c9243c6-38aa-5049-831f-68b0369f2464 | date | Date Completed:
3bb99724-153a-4e53-8f17-f377c9ccd3bd | checkpoint | 1.4 - Weather Conditions
1757d7c8-7b9e-5f63-9e18-8a3b9f2894da | note | Frequency - Prior to commencing works
258c24fd-de63-5eb1-8b11-e788b3a15630 | note | Acceptance Criteria - Prime coat shall not be applied on a wet surface, or when the surface temperature is below 10°C, or when the weather conditions would prevent the proper application or adhesion of the prime coat
69bae7e7-0f2a-52d6-bb8b-44f360d5e261 | note | Reference Documents - Beca Spec 002 - 7.9
e1355026-7302-5287-a4b7-3ca26eca4c53 | note | Inspection/Test Method - Verify
1d8b15b2-1c86-5b18-9574-0a3eb8861fc0 | note | Record of conformity - This ITP signed
de46e4ac-35a1-56fe-9b90-80059a3153ac | note | HP*
c78e9ec0-1cb2-533b-b850-689ed4c43fc3 | note | Responsibility - Project / Site Engineer
bef7f574-7a99-5578-88ca-b7edc2392955 | date | Date Completed:
de348b1d-773f-463c-b540-9e82ba8a75e9 | section | 2.0 - Materials
bbe3702a-1de0-49d5-ba53-b1f9667b6c01 | checkpoint | 2.1 - Cut-back Bitumen
5a845578-274c-5c5d-9778-c478b66ec5d9 | note | Frequency - Prior to commencing works
47fdd202-1cce-5ca0-9d9f-61da5ea5f6d3 | note | Acceptance Criteria - Cut-back bitumen for prime coat shall comply with AS 2157 and shall be class AMC0, AMC00 or AMC1.
6e034720-761e-57c8-b234-a4ae2197469a | note | Reference Documents - Beca Spec 002 – 7.4.1
5afb3c07-8877-5d88-8d35-f5be1c4f9663 | note | Inspection/Test Method - Verify
02b3f534-0085-573d-ac1e-d7231d0232ed | note | Record of conformity - This ITP signed
83c4f1f6-251a-5fd6-8549-eed1d892a7ae | note | HP*
b9bae47a-9ff8-589f-b53e-9b539feb5010 | note | Responsibility - Project / Site Engineer
e5218776-941b-5734-95c8-d541afe46f53 | date | Date Completed:
3a26611d-32f8-45e1-85a9-9f5df9cf0941 | checkpoint | 2.2 - Cutter
2ec749d3-e4c0-5ba0-9b7f-e97cda92030f | note | Frequency - Prior to commencing works
44191fc2-4976-5bb0-9822-b17594bb3f68 | note | Acceptance Criteria - The cutter for use in cutback bitumen shall be a suitable petroleum-based material complying with the requirement of AS 3569.
a048271a-b023-5219-87da-15e93e767746 | note | Reference Documents - Beca Spec 002 – 7.4.4
280e28a3-c46a-5488-a7a8-0763ff10c1d4 | note | Inspection/Test Method - Verify
caf54b2d-b844-5db2-91f7-c4e3bf8449d2 | note | Record of conformity - This ITP signed
75a46fae-6394-55b4-9d9f-b48aa94b7896 | note | HP*
ed25d063-39c6-54bf-b5a0-207b05fa5bcc | note | Responsibility - Project / Site Engineer
bb370798-8dc3-5d38-ad79-e105606c7519 | date | Date Completed:
bcc1e27e-aff6-4b94-8d29-95ccd17bb3c1 | checkpoint | 2.3 - Bitumen Emulsion
76d445f1-48af-58b0-88f0-e6fcb925a7ae | note | Frequency - Prior to commencing works
9d0874b1-5782-561b-a5c7-c594ebdb1ad8 | note | Acceptance Criteria - If directed by the Principal’s Representative, bitumen emulsion complying to AS 1160 shall be used as a prime coat.
205fb309-6c13-5686-b85a-f192804d7535 | note | Reference Documents - Beca Spec 002 – 7.4.2
8c81b12e-747f-53a4-91e2-6838e33fd7ec | note | Inspection/Test Method - Verify
5ea3bb67-1b3b-5129-a2b5-d7383c64cfcb | note | Record of conformity - This ITP signed
4946ca3b-3790-5ce7-b9e4-f5561af79a99 | note | HP*
71e952ee-dce8-53b9-9eef-ec190898e94d | note | Responsibility - Project / Site Engineer
b0eedbc5-aadc-5c89-a5fd-eca364354b49 | date | Date Completed:
f576d954-49a0-42e9-ac80-bbfe9b7186db | checkpoint | 2.4 - Blinding Sand
0c428cd8-ee5e-5efd-81a0-76b1d574d74c | note | Frequency - Prior to commencing works
dd81b60a-4a4c-50b8-9e79-a4c147533df3 | note | Acceptance Criteria - If required, blinding sand to be used for absorbing excess primer shall comply with the following PSD.
c2fd285d-2476-5e8b-ad68-eb65fa989f70 | note | – – – – – – – – –
7f3456da-1847-5c0e-b994-a63ac1a5d4c1 | note | AS Sieve Size (mm) ¦¦ Percent Passing Sieve by Mass
7373b608-2a20-5b28-a2dc-45c227098ca8 | note | – – – – – – – – –
dee58195-b56a-5086-9c21-3317909095b5 | note | 6.7 ¦¦ 100
c89fb368-084b-5ccd-a25c-5e6648dfa48f | note | 4.75 ¦¦ 85-100
8c2ca609-efc1-53ee-bef9-a9baec78a423 | note | 1.18 ¦¦ 40-100
112cda15-adec-5d68-bff4-e7e054049ba3 | note | 0.425 ¦¦ 10-50
09f921e7-9bcc-5145-9e5f-241a1ca1d9bf | note | 0.075 ¦¦ 0-5
e39f3f4f-c1ab-5469-915e-991bb4a90a25 | note | – – – – – – – – –
f991a567-1f3c-5f5a-aa8b-40188453ed3c | note | Reference Documents - Beca Spec 002 – 7.4.5
ea483d90-6c58-50d4-beb8-598538458b7b | note | Inspection/Test Method - Verify
4c2327f9-2861-5eb8-9f41-a0eb74b66bb7 | note | Record of conformity - Test Report
9a2a6ca8-a9a0-5d22-8aa7-46a50e3c8322 | note | TP
e783442a-53e7-53dd-8c06-fd1c7f314069 | note | Responsibility - Project / Site Engineer
e71aa016-769f-5825-8d9f-f1865a9e7af9 | date | Date Completed:
961be67c-bf5f-4e52-aab6-63c629df32e8 | checkpoint | 2.5 - Test Certificates
5951c134-99c4-5126-8903-18c8840bcec0 | note | Frequency - Prior to commencing works
e47d554e-a415-542d-9de3-d4d9a63d5553 | note | Acceptance Criteria - The Contractor shall submit a Test Certificate for each material proposed for use in the Works indicating compliance of those materials with the properties or requirements specified.
a7ead04a-5e2c-5935-9172-8844bba2f9c0 | note | Reference Documents - Beca Spec 002 – 7.11.2
1abbacd2-a0e4-59ca-b212-ee89c8953f2d | note | Inspection/Test Method - Verify
55eca4bf-e875-560f-b9f7-bd51a6f27140 | note | Record of conformity - This ITP Signed
8efc5107-d167-5eb4-bb1a-743e8e548db4 | note | HP
f37718ef-72d6-5ce3-acef-3e893adb4fe1 | note | Responsibility - Project / Site Engineer, Principal’s Representative
00e893b5-b03d-5bf0-82df-d73eb0ca623e | date | Date Completed:
c26b8cc6-3c39-45a3-b7f0-5e383ad951a5 | signoff | AUTHORITY HOLDPOINT
57b41481-d68c-4391-90b7-9f9d89a45349 | section | 3.0 - Construction
491114b2-bb94-4739-831b-3c181b620eea | checkpoint | 3.1 - Trial Application
c19b6e36-1556-5662-8e3b-f4c52c9e0755 | note | Frequency - Prior to commencing works
e66b1bdb-6f64-52fe-af14-cbfafc9854ba | note | Acceptance Criteria - A trial application, to be conducted as part of permanent works, shall be conducted on an area of the Works agreed and witnessed by the Principal’s Representative
af5b48aa-c2a6-5e1c-8f10-f3370cb0889d | note | Reference Documents - Beca Spec 002 – 7.5
7f1ef474-79ff-5de1-b406-54b608a4495f | note | Inspection/Test Method - Visual inspection
9c0b55f7-61c9-5684-bde1-8f885847c0f7 | note | Record of conformity - This ITP signed
b42bd78c-ad4e-57fe-8ea4-61f146d837fe | note | WP
b82a8cb5-2d38-5273-8ae1-403740c26d57 | note | Responsibility - Project / Site Engineer, Principal’s Representative
406d6ea4-31b7-58b1-a3f7-6c745a8da018 | date | Date Completed:
bdb6f786-9d14-4d15-990f-6b639b120d4c | checkpoint | 3.2 - Surface Preparation
773a9aa3-ff5c-5944-bccb-01be5c87e0da | note | Frequency - Prior to commencing works
598d64e6-ead0-515d-b29f-964c310c4c60 | note | Acceptance Criteria - Immediately before applying the prime coat, the full width of the surface to be primed shall be swept to removal all loose dirt and material. The prepared surface is to be inspected by the Principal’s Representative.
203147b0-7dc0-5aa9-9b11-f9be67189f19 | note | Reference Documents - Beca Spec 002 – 7.6
4588eeaa-da56-565d-8276-ecafa72e65b3 | note | Inspection/Test Method - Visual inspection
52f14954-865d-59b4-b737-81399518cca1 | note | Record of conformity - This ITP signed
b9599d19-5082-5bc3-9cc4-0386357d50a9 | note | HP
ad28aeba-8d64-5dfc-a5d3-fdc10776ea72 | note | Responsibility - Project / Site Engineer, Principal’s Representative
845b96ba-b45e-5e50-95c4-e86b955bf003 | date | Date Completed:
14b307ab-29c0-4f6d-affe-50c8e32766b7 | signoff | AUTHORITY HOLDPOINT
6b746c0c-f9f3-4314-b90d-936949285f61 | checkpoint | 3.3 - Application of Bituminous Material
5927ef10-05c0-5e30-b878-a0cf84ce60ba | note | Frequency - During works
6ef9b667-a035-5d62-a551-6efb39d2dd23 | note | Acceptance Criteria - The prime coat shall be applied at a uniform rate and shall be between 1.0 and 1.4 litres/m². The depth of penetration shall be a minimum of 6mm and maximum of 10mm
8552218b-5cb9-5e9c-8c60-c99ac0d16523 | note | Reference Documents - Beca Spec 002 - 7.7.1
dd2df51c-e5b4-5695-8529-0eba36c4ef7b | note | Inspection/Test Method - Visual inspection
f137d25f-23b3-5538-9e5c-8fd12bd00229 | note | Record of conformity - This ITP signed
89c050ed-eefb-5ca1-a945-d100eccc7d99 | note | WP
5ed4fc47-a56e-5a55-9e45-3c7ecd1836a7 | note | Responsibility - Project / Site Engineer, Principal’s Representative
4a9b897e-27c8-5c6b-a81e-22e0b85583ed | date | Date Completed:
8d4009bf-128b-4ba8-9c2f-f59a6b63c4f0 | checkpoint | 3.5 - Job Samples
a25b296e-7122-59c1-965b-5dbbd425f1f6 | note | Frequency - During works
e1247717-fdc6-5cd4-ab4b-c7284f49c6f4 | note | Acceptance Criteria - Samples of each bituminous material shall be obtained from the delivery vehicle at not less than one sample per 10,000 litres of bituminous material sprayed.
499e39c3-8cf3-507d-8f7e-86373ba32d2c | note | Reference Documents - Beca Spec 002 – 7.11.3
c4c8f6a5-b97f-5568-883f-d5a6f587b46d | note | Inspection/Test Method - Verify
593b9d22-2eed-5a0c-89f4-3d58ec10c487 | note | Record of conformity - This ITP signed
e2673f27-73ac-52c8-8656-0bb7484901ea | note | WP
3d3107ee-41da-5a2a-add6-b44331834c17 | note | Responsibility - Project / Site Engineer, Principal’s Representative
a61fc26e-0007-587a-a63b-9eeddb53199c | date | Date Completed:
3111ef1e-8067-4611-9b62-cc6907b81677 | checkpoint | 3.6 - Spray Rates
5293682c-172a-58fc-950d-21b77a8a012f | note | Frequency - During works
b650fea7-6531-52ad-98b5-0390b0fc3213 | note | Acceptance Criteria - The Contractor shall submit records of spray application rates at completion of each mobilisation
48c810e2-deeb-56db-8d38-8ac4d78c4fbd | note | Reference Documents - Beca Spec 002 - 7.11.4
9f9951cc-7314-586f-b814-06dbc24e42bc | note | Inspection/Test Method - Verify
e673b04d-668e-5ba2-8fa3-e193efd1cd4c | note | Record of conformity - This ITP Signed
e2bb34f8-7a03-5b63-b023-62fa95a3cd26 | note | HP
7f2eaaed-6852-58d3-809f-d4764c71b679 | note | Responsibility - Project / Site Engineer, Principal’s Representative
bc0e6561-5eeb-583d-9fbe-03ff94d22535 | date | Date Completed:
b07a4c7a-0883-4cd9-993a-7cc53f321ead | signoff | AUTHORITY HOLDPOINT
e7911909-0654-4de0-888c-21d32b274fb8 | checkpoint | Final Inspection
4c2faa46-c70c-5661-924e-86e232994310 | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality\System Procedures and verifies lot compliance with specifications.
45b29829-d6fe-58e8-8eec-d07a28ddadfb | textbox | Print Name:
500536a7-e1bf-50d2-8c1a-760159d5e869 | textbox | Position:
c33e2fde-3cdd-5305-8e64-d94760ac2606 | date | Work Completed On:
9f863073-35d4-5e36-8dc1-19fa91b6d652 | date | Date:
48e2b06e-08d3-437c-aae8-49c61c1e0e9e | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0023 - RBB Install - Rev 0 | itp | ITP023 - RBB Install
d6b5c7ae-8d09-47fb-a3b1-3e55cc75e2bf | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
186676e5-7449-43fc-a1f3-1a01a8078414 | checkpoint | 1.1 - Check for correct documentation
2c95854c-7da0-5c61-9835-cece79e27c3b | note | Frequency - Prior to commencing works
61543c2b-40ac-517a-8104-fde5a363d1a0 | note | Acceptance Criteria - Current revision drawing is being used including the Subcontractor’s copy.
6f3997bd-ffbd-5b78-ae4f-6d82339efa46 | note | ○ Current revision to be obtained via Aconex.
0cc38b36-4bc2-5fc4-908c-ee6a83dab520 | note | Reference Documents - Current Revisions in Aconex or ACC
15c33c0b-e1b8-532e-a9d4-79f89e788aea | note | Inspection/Test Method - Visual inspection
03bd8099-2eba-5dba-a19e-e6ed65036f92 | note | Record of conformity - This ITP signed
cd19e67e-cb71-5841-8f20-01ee56fb076b | note | HP*
56f2d637-2f15-59e6-950e-52c69bcdf343 | note | Responsibility - Project / Site Engineer
46e90f62-3664-521f-8aa4-66a9b2fa436d | date | Date Completed:
201b6ccc-8d3a-496f-881e-b6221146a2c6 | checkpoint | 1.2 - Implementation of all measures and controls
7f728bcf-3978-5ba5-86d6-b9956acdf930 | note | Frequency - Prior to commencing works
c123ac80-ac46-5d2e-8df4-0c827fd340d3 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
ad5ace02-6ea0-5bc6-b35b-0f876d1c3e6d | note | Reference Documents - PSP, EMP, TMP, SWMS, WMS
e1d8dc7c-b8f7-5a09-8b88-9b596a8136da | note | Inspection/Test Method - Visual Inspection
83e1c9d9-2673-56b9-aca7-c792d5081731 | note | Record of conformity - This ITP signed
ead37f11-4ab3-569c-956c-d4d80be278d2 | note | HP*
6a719f23-11cc-513e-b11b-d453eba39fc3 | note | Responsibility - Project / Site Engineer
29e4158d-3355-5a02-b84d-5b225d392793 | date | Date Completed:
41e2ff4d-b15b-4a60-955c-8c17150ab031 | checkpoint | 1.3 - Definition of the work area
041f6814-a957-5767-b30b-2c397636ca14 | note | Frequency - Prior to commencing works
ff013046-beb0-5682-a098-5262c867a6a8 | note | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of work clearly defined.
580612dc-259c-5832-a13f-8703d05822a2 | note | Reference Documents - Drawings
7a7682a9-60ed-5efb-a925-4971a8e3a68a | note | Inspection/Test Method - Visual Inspection
95b4c713-5890-5fc6-bf8c-938ea8696cf5 | note | Record of conformity - This ITP signed
1750b9fd-8ea6-5f1d-999c-36a434bb6b74 | note | HP*
4b695982-94f9-52a3-a7b1-63121010aed3 | note | Responsibility - Project / Site Engineer
8b7d0b79-8ba6-5f97-b2e4-4bb059c65907 | date | Date Completed:
0cfe9cd4-5e91-4417-a535-4a27e4bc5c8c | section | 2.0 - Materials
d160ed2e-6847-41fb-ba24-e6ed3f7bdbdc | checkpoint | 2.1 - Rubberised Bituminous Sealant
fbd11730-afb4-56a9-9d6f-f890317f7be9 | note | Frequency - Prior to commencing any activity
2c9803dc-4f5a-5f78-a092-e4afea3512b4 | note | Acceptance Criteria - RBB must be a proprietary polymer modified bitumen (PMB) crack and joint bandage product and have the following properties:
03eed60d-ce28-55ac-b813-837e24d89e14 | note | – Minimum softening point to be 95°C
e342c0c3-1015-596f-95d0-7cc86a0516a3 | note | – Penetration at 25°C between 20 and 50
8e51ecc6-b845-51df-bdf6-079955508c9b | note | – Flow at 60°C at 5 hours to be maximum 5mm
9ee93e50-6207-509a-9ae3-0b26209ca80e | note | – Viscosity at 180°C to be maximum 3Pa.s
abdb09e9-354f-50ac-843e-6c417397a30a | note | Reference Documents - Beca Spec 002 – 10.7
fb46036d-fe3d-5318-acf9-6209c2225260 | note | Inspection/Test Method - Verify
e92a81c8-f380-582a-b9f7-552758d21cb7 | note | Record of conformity - Manufacturer’s Datasheet
4e973bea-b492-5cc0-bd28-5664a2c1c28c | note | HP*
a549832f-ad4b-524b-bb0c-c6c777cae0da | note | Responsibility - Project / Site Engineer
02fa45ba-d4b0-5331-96d2-453816ef42c5 | date | Date Completed:
9c3c15e1-04bf-4aa9-82d6-1e10f5cb6aea | checkpoint | 2.2 - Material Sources – Conformance Test Certificates/Reports
4244069d-59ec-58bf-9493-92bed312287f | note | Frequency - Prior to commencing works
c4eaac12-e3c2-5a6b-a2d9-4ffb336f47ec | note | Acceptance Criteria - Test certificates and matching production batch numbers are to be provided for each product used
4a9bdc17-a242-5966-a84d-e1677290c17c | note | Reference Documents - Beca Spec 002 – 10.7
2c6477c0-f0e0-55b0-8fcd-1cdd1014623b | note | Inspection/Test Method - Test Certificates
ae515e79-805f-5df8-bb65-7d051c84c64a | note | Record of conformity - Aconex Reference
ffc645a4-c81d-564d-8708-87cbae1b8233 | note | HP*
8bbd01a0-2e65-5ddc-ac85-a8b586138f82 | note | Responsibility - Project / Site Engineer
8fc12915-5ac4-53d1-9737-26f7a72467c4 | date | Date Completed:
2b78505f-4709-4e31-8b3c-61a3c9ece50f | section | 3.0 - Sealing
e9ba9f88-6c0d-48c6-86ab-f3716397a7de | checkpoint | 3.1 - Applying Sealant
861841e9-49c8-58a0-8426-caedab89037e | note | Frequency - During joint sealing works
8620914e-564f-56e4-975d-dcc24212dd58 | note | Acceptance Criteria - Sealant bandage is to be between 50mm and 75mm wide or as per drawings.
dc9f1072-3067-5bf7-97e1-78546ae8e8e4 | note | Reference Documents - Beca Spec 002 – 10.7
021932c7-7087-59e2-829f-f2c2b0df5f26 | note | Inspection/Test Method - Visual Inspection
cb413dcc-fda2-5e9a-a417-f14e87aecc0a | note | Record of conformity - This ITP signed
ceeeb223-8dc3-5c7c-94df-f44fb1ff3af3 | note | IP
2fac2c4f-ad4c-5196-9678-0c4aced13b1a | note | Responsibility - Project / Site Engineer
ba64cb88-7b63-5a78-a6c0-2601761bb935 | date | Date Completed:
7b89067c-ada2-4eb4-b4c4-ec1368559b41 | checkpoint | 3.2 - Protection of Applied Sealant
16494742-a6f6-5687-86a1-e05a964bd9ac | note | Frequency - During joint sealing works
f22346f2-9dd3-5a42-a7c9-162a247afc16 | note | Acceptance Criteria - Installed sealant must be protected from damage by traffic (and possible pick up on construction vehicles and aircraft tyres) until it has cooled to ambient temperature.
6f57a268-4b60-5f3c-85a6-16360a2afe91 | note | Reference Documents - Beca Spec 002 – 10.7
95f97a53-6263-5acb-bbb9-bdc1f3d784e1 | note | Inspection/Test Method - Visual Inspection
1d978172-71fc-530a-b78d-141d26a22a51 | note | Record of conformity - This ITP signed
7e410a98-6a8c-539a-b8e8-97af0cb70c00 | note | IP
793967b4-3968-51ea-8551-d53d4399ce63 | note | Responsibility - Project / Site Engineer
c30eda83-441d-59e5-8150-a3e62c6ee6d6 | date | Date Completed:
7142072f-8e6a-45e0-b5f6-10766bcde79a | checkpoint | 3.3 - Cleaning up
7ea2d8cb-875c-52c9-a92a-7386fca8926a | note | Frequency - After sealing works
20e1a690-efd5-58f9-abfd-912b712fd967 | note | Acceptance Criteria - Any sealant split on surface of pavements must be cleaned off immediately.
9ee8fd9e-5e71-5539-b571-7870e15ef959 | note | Reference Documents - Beca Spec 002 – 10.7
e0beba91-6ab2-5ff7-af81-3a591484e883 | note | Inspection/Test Method - Visual Inspection
dbecbf8e-d8d6-561a-bdf1-5777e0dd6896 | note | Record of conformity - This ITP signed
f52db4fa-7f90-5943-882d-7583591fd0fa | note | IP
bd5be3ef-182a-5b88-bf86-4f0b5efede10 | note | Responsibility - Project / Site Engineer
8af468f6-b16c-5017-ad32-330faa3db0c4 | date | Date Completed:
ff4c9e47-c7bf-4391-ad81-c8151ab4336e | checkpoint | Final Inspection
fe3a4b26-40e0-5abc-b2f7-b9b43ef0bba3 | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
fe5a825e-c3aa-5431-b490-13d79dec5cc6 | textbox | Print Name:
53ce214a-06c1-5e68-ac23-9fb7d1fe59ca | textbox | Position:
649d83bc-792d-505e-9b40-61c34cb55df6 | date | Work Completed On:
85940907-b8d7-5644-9893-d51e93fdbd77 | date | Date:
2e52f8ff-f039-508a-a53c-edd8cbc34cf3 | checklist | Ω (Deprecated) FH-ZU2-QU-ITP0024 - Line Marking - Rev 0 | itp | ITP024 - Line Marking
5a37da6d-0098-5585-adcb-850f5634087d | section | 1.0 - Preliminary Activities
78f2eb97-4d27-5397-9616-d0974c63c400 | checkpoint | 1.1 - Check for correct documentation
3dd0ff50-fb8b-5323-a5f4-174235db3bb0 | note | Frequency - Prior to commencing works
be6ca003-eacb-5536-9502-4129ac55e0b6 | note | Acceptance Criteria - Current revision of drawings, technical specifications, permits as required for excavation and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
570d0344-ab6f-5cba-adbc-bde76755f574 | note | ○ Current revisions of these documents to be obtained via Aconex.
c431b101-0de6-59ab-8118-51c68a8a6dab | note | Reference Documents - Current revisions in Aconex
5575fbe7-6bd3-5b47-9484-d67ebca9a673 | note | Inspection/Test Method - Visual inspection
fb4ad021-737e-577d-93fd-1ad92991ec07 | note | Record of conformity - This ITP Signed
58ca559a-49a6-5f2f-821a-ca46bcc68042 | note | IP
d484f66d-bebf-5686-b013-3d3e948efaf8 | note | Responsibility - Project / Site Engineer
6ad6dba9-f8be-5a8b-bc3d-882f42f8e80b | date | Date Completed:
457fc29c-5478-51c3-a60f-061f5ba4ad0d | checkpoint | 1.2 - Implementation of all measures and controls
0a017651-706d-54c3-85fb-702e8e5c945c | note | Frequency - Prior to commencing works
0106cef8-fb07-52f8-9d0b-233e8ef0f3d4 | note | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS.
f58b93c3-403e-5d79-ab72-e34a033eac3c | note | Reference Documents - PSP, EMP, TMP, WMS, SWMS
1f09cf1c-9444-5f88-a031-ba84e76b04f2 | note | Inspection/Test Method - Visual Inspection
d7e6d134-341b-5d02-9a40-0380783982a8 | note | Record of conformity - This ITP Signed
68d00306-27e9-5052-b4d2-6a1210117b22 | note | IP
84d48667-eb48-5eb7-afae-2f88167e3235 | note | Responsibility - Project / Site Engineer
fcdc119e-9234-54a5-a446-d7e82e5bdb52 | date | Date Completed:
8e1d15a0-80f2-5559-9761-6b1391fc9e6a | checkpoint | 1.3 - Plant and Equipment
23478d3f-8c15-5af2-995f-bbc053c914e7 | note | Frequency - Prior to commencing works
69b71fac-fa43-5c98-ad82-6a2ed8531a3e | note | Acceptance Criteria - Plant and equipment used in the works are appropriate to achieve specification requirements.
c5ca853a-957f-5094-972c-3521e8655124 | note | Reference Documents - BECA 15.3
99119ef4-7428-51ff-ac9b-31cd7d180bfd | note | Inspection/Test Method - Verify
1244ceca-96fd-5036-9f91-a4b83546731a | note | Record of conformity - This ITP Signed
f873376a-fa8a-524e-aeac-b362e3eaf3ca | note | IP
6f99f2b5-daa8-5308-b16d-6c10228094b3 | note | Responsibility - Project / Site Engineer
57f8b51b-7585-5199-95a2-a1dda2a6ec41 | date | Date Completed:
3d6e7a74-8a4b-569d-a3c2-e0d24e5279ac | checkpoint | 1.4 - Materials
11e6049f-9282-599b-8fcb-dc11a80f43da | note | Frequency - Prior to commencing works
6b583343-7806-5826-822f-f886d472e47a | note | Acceptance Criteria - The paint to be used shall be a premixed synthetic latex-based paint (such as WATTYL AIRPAVE or approved equivalent).
23e4def6-2144-530f-9067-8eb87b76f67d | note | Reference Documents - BECA 15.4.1
849ce26d-f900-51e9-b9ab-21ff7a41d281 | note | Inspection/Test Method - Verify
1d78b532-1208-5f9e-b15d-a6fae4f54452 | note | Record of conformity - Material Reports / This ITP Signed
ecc46e2a-e3c4-5a42-bf21-ab6823f96a58 | note | HP
96744f4c-965e-5c80-be1f-96add9453d56 | note | Responsibility - Project Engineer, Principal’s Representative
05d53222-c990-50eb-9cc3-8770814cd045 | date | Date Completed:
0119ba62-9ab5-5c8c-bf06-711caae1fe15 | signoff | AUTHORITY HOLDPOINT
da39e7d4-ce7e-5bb2-9638-ef2f50abb8a7 | checkpoint | 1.5 - Material Handling
c3d6276f-066a-52a9-9000-ef5282e2e88c | note | Frequency - Prior / During works
2d82c0ea-8f85-595a-a7cf-90869432ba81 | note | Acceptance Criteria - The paint Is to be packaged in 20 litre containers that are of durable construction without sharp edges. Paint containers are to be clearly labelled “Airport Pavement Marking Paint” as well as being labelled with the following: Manufacturer’s name, Colour, Batch number and Date.
2c1660b3-f58e-5825-ae91-5655d2f8ce13 | note | Reference Documents - BECA 15.4.2
1dd3cc97-d546-56df-adb9-054971e0be0c | note | Inspection/Test Method - Visual Inspection
b8b1013b-2633-57f4-a0b9-1a8a5c0cb19b | note | Record of conformity - This ITP signed
8a6cf72d-6148-5f62-ac49-1cd72a02075b | note | IP
8fb203db-286c-5914-b0dd-97105b755bfb | note | Responsibility - Project / Site Engineer
3a10c983-588f-5609-afab-b5dbc4b19711 | date | Date Completed:
c871658f-3e9a-5e49-b084-2962c09d6aee | checkpoint | 1.6 - Survey and setting out
01f9edc2-85ae-5270-81d6-345693e57f30 | note | Frequency - Prior to commencing works
6a4e6821-b71c-532a-af20-36f243b84fcf | note | Acceptance Criteria - The Contractor shall carry out the setting out of the pavement Markings as shown on the drawings. This shall be approved by the Principal’s Representative.
54e07015-df2e-5be5-b2b2-49c296fb3488 | note | Reference Documents - BECA 15.7
15737500-c913-50a7-bd25-063724ab7b7a | note | Inspection/Test Method - Verify
9fd85844-0a9a-5631-909a-9c3d9dad2f4c | note | Record of conformity - This ITP Signed
40d1cdd5-d2ea-5735-99bb-a2562c034cf6 | note | HP
9aee3244-b56b-556c-bfa0-5c4043c5657e | note | Responsibility - Project Engineer Principal’s Representative
8c36297f-486c-568f-a61a-a65ff6307389 | date | Date Completed:
e0c31cab-119d-5382-b56f-d6078cebdc06 | signoff | AUTHORITY HOLDPOINT
648931ca-ea92-5007-b762-3e625bbef167 | section | 2.0 - Construction
681ade3f-e48c-5564-9edf-5b16cbc3d45b | checkpoint | 2.1 - Removal of Existing Line Marking
764ec3ec-870c-57a0-87f4-8159a07872d4 | note | Frequency - Each Lot
3ac85a29-e707-5e70-97ee-fd25e2b8d166 | note | Acceptance Criteria - Existing pavement markings, at the locations shown on the Drawings, shall be removed by water blasting or other approved means that is non-destructive to the existing pavement surface.
a20704dd-3752-517f-a098-c5e79b7192bb | note | Reference Documents - BECA 15.5
efedbbca-ee60-5ba5-8a07-b130fc8b4f3e | note | Inspection/Test Method - Verify
ebdb1d2a-b6d0-531f-b042-e2a69b4db626 | note | Record of conformity - This ITP Signed
68fa665a-82e1-547c-bad6-7356ac5d833c | note | HP
8d9993ac-df7b-5f07-8d20-5a34c339c90a | note | Responsibility - Project / Site Engineer Principal’s Representative
559431fd-bcaa-51ae-bf61-6f39dba60262 | date | Date Completed:
eef8f178-0072-5287-9af2-7a4ca27e92f2 | signoff | AUTHORITY HOLDPOINT
14088100-2192-5bdc-81da-ec742c09fb6c | checkpoint | 2.2 - Surface preparation
e2c8b966-0ac1-5f47-8638-ee0d2152fff2 | note | Frequency - Each Lot
76c75673-a826-597c-b900-f03b90f44781 | note | Acceptance Criteria - The surface of the asphalt or concrete pavement in the areas to be painted shall be thoroughly cleaned prior to the application of the pavement marking paint. This shall be approved by the Principal’s Representative.
0a20df0c-3926-58a9-bbf0-3ce181017df8 | note | Reference Documents - BECA 15.6
5bbade8c-02b7-54a8-b284-1888a7264a16 | note | Inspection/Test Method - Visual Inspection
57424184-ac24-531d-9aca-1d36f6c32426 | note | Record of conformity - This ITP Signed
864c3c6f-408b-570b-af65-2cee519aabcf | note | HP
b326933c-558c-5185-a248-36d2b855bb39 | note | Responsibility - Project / Site Engineer Principal’s Representative
0be80a0a-60a2-5ade-a6e7-333e0e25db80 | date | Date Completed:
53600c54-7994-55d7-94b2-5f0976e97edd | signoff | AUTHORITY HOLDPOINT
5ebec58b-474a-5be8-8f64-e19e13ed9304 | checkpoint | 2.3 - Weather Conditions
9549e51a-6f94-58bc-8d48-fca26969af2a | note | Frequency - Each Lot
6dafaa30-d289-5b1e-b8c8-3b0007c8de14 | note | Acceptance Criteria - Pavement marking shall not proceed during wet weather or when the pavement surface is wet or when rain is likely or during high winds.
ebc917bf-fd7c-5078-b024-249d2e48f67f | note | Reference Documents - BECA 15.10
6737025b-0d8b-5d4a-9a22-8435e396f8b5 | note | Inspection/Test Method - Verify & Visual Inspection
9664c81b-3037-50b0-89d2-58344186894b | note | Record of conformity - This ITP Signed
87604978-b18d-589d-aa84-162f4868fc54 | note | IP
e4a2e562-4cf0-5a52-997f-da44b4c5d8b7 | note | Responsibility - Project / Site Engineer
31a0d07e-546e-5c07-ac93-fa15e582e689 | date | Date Completed:
a5154039-7580-5563-baf9-1bf6f8ffe4d1 | checkpoint | 2.4 - Application
3d301684-6259-5233-b2eb-7321d10d1906 | note | Frequency - Each Lot
ab07e7f6-d46e-53a2-8beb-1c2407fc97fc | note | Acceptance Criteria - The paint must be applied in two even coats to provide the required minimum total dry film thickness as specified by the manufacturer. The second coat is to be applied no less than three days following the initial coat.
82c65602-9fdf-5025-9dc6-f31c48c4c3e9 | note | Reference Documents - BECA 15.8
7856548a-50a2-5b31-816a-2122d0e018dd | note | Inspection/Test Method - Visual Inspection
06cc89a2-f42b-53a9-8ba6-8b47cf98f081 | note | Record of conformity - This ITP Signed
d47c620d-2137-5eea-9e1f-7aa1c65c68d8 | note | IP
5fa78e4a-7ccc-5d95-a9ab-6a81411db053 | note | Responsibility - Project / Site Engineer
cfc11233-6da3-50cc-9239-dcc92dab8c34 | date | Date Completed:
e81d07e9-bb2e-5c81-bddd-4d004625d48d | checkpoint | 2.5 - Application Rate and Conformity of Application
563b61c1-ce07-5b57-b773-f41581ee0fac | note | Frequency - Each Lot
98200636-45d2-5279-b3ed-9c18ff03b166 | note | Acceptance Criteria - Daily records of paint usage and the area covered shall be maintained by the Contractor.
c1b68d07-31e8-5e09-9c3e-9d37dbf15bab | note | Reference Documents - BECA 15.12
7fec02aa-b67a-5afd-9382-76c469161716 | note | Inspection/Test Method - Daily Records
16591429-06b7-5f37-9377-a7cfe44792ea | note | Record of conformity - This ITP Signed
98ea938a-a873-5359-b179-b853ee519235 | note | IP
64bb29e1-5afd-5cc4-b6b8-4fb265e2f13c | note | Responsibility - Project / Site Engineer
d3b740af-f020-5400-a732-468d6ab5fb0b | date | Date Completed:
3da33369-6e9d-5056-b7b3-713e5e79cd00 | section | 3.0 - Post Construction
bbff472a-32f2-504e-b36c-c68825e037b4 | checkpoint | 3.1 - Records
162b4d84-3404-5e60-9bb5-b03d95ff3c65 | note | Frequency - Each Lot
2cdbf4f6-160a-5604-adea-5b385854df4c | note | Acceptance Criteria - Finished pavement markings shall conform to the following tolerances:
bbf7bbd5-8abb-5779-b60d-646b662381b9 | note | ○ Location of pavement markings ±10mm
f689dfa8-e020-5ef4-a77f-3247e0d5b38c | note | ○ Width of any line or line forming an alpha/numeric symbol ±5mm
eb6dca9a-7994-5705-a50c-2c2f9c6f092b | note | ○ Length of any line and the spacing of broken lines ±50mm
be1d940b-5121-5c10-9be7-cb9f8d85600c | note | ○ Dimensions of any alpha/numeric symbol ±10mm
cf5961b2-a636-54fc-a693-400e4009ff29 | note | Reference Documents - BECA 15.9
6b03534f-1808-5f6d-90be-e674587b5f75 | note | Inspection/Test Method - Verify
df3bfed5-d7f5-516f-9f0d-3ac8de9a4400 | note | Record of conformity - Survey
923afd04-5dea-5669-b301-2cae53158290 | note | SCP
c9b17de7-b8e0-56d3-8f36-4f87e091d88c | note | Responsibility - Project / Site Engineer
7ac1f5cd-621f-5399-a338-8e054ec6a8d4 | date | Date Completed:
e4df1e76-54d1-5b97-b96b-bf3da9d4c209 | checkpoint | Final Inspection
9f6a4cf4-dc9b-5660-b654-f7197f44fbde | note | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
4354d4b2-71d7-5b11-8246-5ec50a7b1b78 | textbox | Print Name:
fe9538f7-73ad-5156-a05e-cae731d3d5a6 | textbox | Position:
ef4e302c-689d-5b40-a0eb-3681aee031ea | date | Work Completed On:
d36e0338-74d7-585c-bf57-6c855923465a | date | Date: