## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP031 - ALER 3 Onsite Concrete | itp |  |  |  |  | FH-ZU2-QU-ITP031 - ALER 3 Onsite Concrete - Rev 0
section | 1.0 - Preliminaries
checkpoint | 1.1 - The current revision drawings are being used including subcontractors copy.
label | Frequency - Prior to Start
label | Acceptance Criteria - Current revision drawing is being used (including the subcontractors copy). Current revision to be obtained via Aconex or ACC
label | Reference Documents - Drawings and drawing registers
label | Inspection/Test Method - Verify
label | Record of conformity - Up to date drawing sets and this ITP signed
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to Start
label | Acceptance Criteria - All necessary measures and controls being implemented, that is CEMP, TMP, SWMS, & WP
label | Reference Documents - CEMP, TMP, SWMS, & WP
label | Inspection/Test Method - Verify
label | Record of conformity - Site and office Inspection
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 1.3 - Excavation Permit
label | Frequency - Prior to Start
label | Acceptance Criteria - Excavation Permit issued by APAM obtained prior to any excavation on site.
label | Reference Documents - APAM, Excavation Permit
label | Inspection/Test Method - Verify
label | Record of conformity - Proof of & permit ITP sign
label | HP*
label | Responsibility - FH Engineer
date | Date Completed:
section | 2.0 - Supply of Materials
checkpoint | 2.1 - Reinforcement
label | Frequency - Pre-commencement
label | Acceptance Criteria - HOLD POINT
label | ○ Test Certificates demonstrating compliance of the reinforcement with the requirements of AS 3600
label | Reference Documents - Drawings and Specification
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Concrete Mix Designs
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Mix design to be submitted to contract administrator for review and acceptance.
label | Reference Documents - Drawings ZULU-BECA-014-DWG-00201, ZULU-BECA-030-DWG-20001
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Review of Curing Regime
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | ○ Concrete curing regime to be reviewed and approved by the contract administrator prior to use
label | Reference Documents - ZULU-BECA-030-DWG-20001
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 - Construction\Erection of Formwork
checkpoint | 3.1 - Setout
label | Frequency - Each Lot
label | Acceptance Criteria - Setout completed and conformance with Beca IFC Drawings.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Survey Report
label | SCP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
checkpoint | 3.2 - Excavate
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Excavation depth shall be as per specified or as shown on Drawings to accommodate structures.
label | ○ Principals representative to be notified for at the completion of excavations for inspection prior to any blinding being poured.
label | Reference Documents - Specifications as per Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | WP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 3.3 - Confirm Ground
label | Frequency - Each lot
label | Acceptance Criteria - HOLD POINT
label | ○ Completion of excavation and inspection of subgrade materials.
label | ○ No soft spots, unsuitable material. Confirm ground bearing pressure
label | Reference Documents - Specifications as per Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - DCP Test Results (if required)
label | HP
label | Responsibility - FH Engineer
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Concrete Sub-Base
label | Frequency - Each Lot
label | Acceptance Criteria - Blinding layer is installed as per drawings
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual Inspecti on
label | Record of conformity - This ITP Signed
label | HP*
label | Responsibility - Site Engineer / Foreman
date | Date Completed:
checkpoint | 3.5 - Formwork
label | Frequency - Each Lot
label | Acceptance Criteria - Formwork / Reverse Shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
label | Reference Documents - Specifications as per Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
checkpoint | 3.6 - Penetrations/Cast in items
label | Frequency - Each Lot
label | Acceptance Criteria - Penetrations/cast in items are present in the formwork.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - FH Engineer Surveyor
date | Date Completed:
section | 4.0 - Reinforcement
checkpoint | 4.1 - Reinforcement installation
label | Frequency - Prior to concrete pour
label | Acceptance Criteria - Pre-Pour Checklist Completed:
label | ○ Position and spacing check and recorded.
label | ○ Cover checked and recorded.
label | ○ Reinforcing supports checked and recorded.
label | ○ Laps at required length.
label | ○ Penetrations/cast in items
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Pre-pour inspection List CLA31A
label | IP, HP*
label | Responsibility - FH Engineer
date | Date Completed:
section | 5.0 - Pre-pour Planning and Inspections and Placement (1st Pour)
checkpoint | 5.1 - Pre-pour Inspection
label | Frequency - Prior to concrete pour
label | Acceptance Criteria - HOLD POINT
label | ○ Superintendent or Engineer to conduct pre-pour inspection prior to concrete pour
label | ○ Principals representative to inspect formwork and steel fixing
label | Reference Documents - Specifications and Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Pre-pour inspection List CLA31A
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Pour in-situ
label | Frequency - Each Lot
label | Acceptance Criteria - Concrete shall be placed within 90mins from batching.
label | ○ All concrete supplied for concrete structures shall be subject to project control testing in accordance with AS 1379.
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.3 - Concrete Testing – Compressive Tests
label | Frequency - Each Lot
label | Acceptance Criteria - Composite samples to be taken in accordance with AS 1012.1.
label | ○ 2 – 7 Day cylinder and 2 – 28 day cylinders to be taken.
label | ○ Frequency of testing shall be one sample taken either every 50m3 or once per day, whichever yields a higher frequency.
label | Reference Documents - Drawing 00201 Note 51. AS 1012.1, AS 1012.9
label | Inspection/Test Method - Verify
label | Record of conformity - Concrete Testers Sheet/Results
label | TP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.4 - Concrete Slump
label | Frequency - Each Truck
label | Acceptance Criteria - Slump test is required for each load per day
label | Reference Documents - Drawing 00201 Note 51.
label | Inspection/Test Method - Verify
label | Record of conformity - Concrete Testers Sheet/Results
label | TP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 5.5 - Finishing & Curing
label | Frequency - Each Lot
label | Acceptance Criteria - Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces.
label | ○ Concrete shall be moist cured or coated by an approved curing compound for a period not less than seven days unless approved by the Superintendent.
label | Reference Documents - Specifications and drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This Signed ITP
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
section | 6.0 - Post Pour Details and Inspections
checkpoint | 6.1 - Removal of Formwork
label | Frequency - Each Lot
label | Acceptance Criteria - Forms shall remain and be maintained firmly in place until the concrete has attained the necessary strength to support its own weight.
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - FH Engineer
date | Date Completed:
checkpoint | 6.2 - Review of Test Results
label | Frequency - Each Lot
label | Acceptance Criteria - Review of 7 day and 28 day test certificates
label | Reference Documents - Drawing 00201 Note 52.
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - FH Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | On behalf of Fulton Hogan it is hereby certified that the Works represented by the items of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: