## Table 1
BESS Alinta Wagerup Peaking Power Station Field Inspection Checklist – Concrete slabs Document Number: RR-SEPD-BESS-FIC-002
Document Information
| Checklist title |  |  | Concrete slabs
| Checklist No |  |  | RR-SEPD-BESS-FIC-002
Lot Description
| Revision no. |  |  | 0
Revision Date (DD/MM/YYYY)
| Description of Changes |  |  | First Issue
Document Review
Prepared by:
| Responsibility |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
| Drafted by (Engineer) |  | Juan Orozco |  |  |  |  | 2024-07-10
| Reviewed by (Supervisor) |  | Jake Scott |  |  |  |  | 2024-07-10
| Approved by (Manager) |  | Artur Krupinski |  |  |  |  | 2024-08-10
Part 1 – Preliminaries (photos where applicable)
| Inspection/Test item |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
[8 empty] | ROBAR | SEPD
| 1.1 | Review of approved construction drawings and specifications |  |  | All drawings and specifications approved and up to date | WBS-SS-CI-SPC-007
| 1.2 | Verification of permits |  |  | All relevant permits (GDA/GDP) in place | GDA/GDP
| 1.3 | Site access and safety preparation |  |  | Site access cleared and made safe | WBS-SS-CI-SPC-007
| 1.4 | Safety inductions and toolbox talks |  |  | All personnel inducted; safety briefings completed | Induction record
Document No: RR-SEPD-BESS-FIC-002 ¦ Revision: 00
Pg.1
| 1.5 | Environmental controls in place |  |  | Dust, noise, and sediment barriers installed and functioning | SEPD environmental requirements
Part 2 – Survey (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 2.1 | Set-out of slab location |  |  | Slab set-out conforms to approved design coordinates | Site Layout Drawings, Survey Plan
| 2.2 | Level and alignment check |  |  | Levels and alignment of formwork and slab position verified | WBS-SS-CI-SPC-0007, Survey Report
| 2.3 | As-built survey after formwork and reinforcement |  |  | Survey to confirm reinforcement cover and formwork position | As-Built Drawings, Survey Report
Part 3 – Pre-pour inspection (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 3.1 | Review of approved concrete mix design |  |  | Mix design approved P3220100 | AS 1379 WBS-SS-CI-SPC-0007
| 3.2 | Formwork installation |  |  | Formwork aligned, clean, and secure; dimensions correct | AS 3610 WBS-SS-CI-SPC-0007
| 3.3 | Reinforcement placement |  |  | Reinforcement size, placement, spacing and cover as per drawings | AS 4671 WBS-SS-CI-SPC-0007
| 3.4 | Reinforcement ties |  |  | Reinforcement securely tied in place, no loose bars | AS 4671
| 3.5 | Installation of dowels |  |  | Correct placement of all embedded items, dowels aligned | WBS-SS-CI-SPC-0007
| 3.6 | Waterproofing membrane |  |  | Membrane installed per design; overlaps secured | WBS-SS-CI-SPC-0007
| 3.7 | Crack control joints |  |  | Joints placed and cut as per drawings and specifications | AS 3600 WBS-SS-CI-SPC-0007
| 3.8 | Construction joints |  |  | Joints placed and prepared as per drawings and specifications | AS 3600 WBS-SS-CI-SPC-0007
| 3.9 | Site safety inspection prior to pour |  |  | Site clear, access routes checked, and emergency plans in place | Safety Plan WBS-SS-CI-SPC-0007
Part 4 – Concrete pouring and compaction (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 4.1 | Concrete delivery |  |  | Delivery in line with approved mix design | AS 1379 Delivery dockets
| 4.2 | Slump test |  |  | Slump within specified range (e.g., 100mm +/- 20mm) | AS 1012 Slump Test Results
| 4.3 | Concrete placement |  |  | Concrete placed within formwork without segregation or delays | WBS-SS-CI-SPC-0007
| 4.4 | Compaction of concrete |  |  | Concrete compacted using vibrators, no visible voids or honeycombing | AS 3600 WBS-SS-CI-SPC-0007
| 4.5 | Cylinder sampling for compressive strength |  |  | Cylinder samples taken for 7, 14, 28-day tests | AS 1012 Sample Register
Document No: RR-SEPD-BESS-FIC-002 ¦ Revision: 00
Pg.2
| 4.6 | Concrete temperature monitoring (if required) |  |  | Temperature recorded during pouring | WBS-SS-CI-SPC-0007 Pour record
Part 5 – Post-pour inspection (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 5.1 | Surface finish |  |  | Class 5 | AS 3610 WBS-SS-CI-SPC-0007
| 5.2 | Curing method |  |  | Curing compound or wet curing applied as per requirements | AS 3799 WBS-SS-CI-SPC-0007
| 5.3 | Formwork stripping |  |  | Formwork removed after concrete reaches required strength | WBS-SS-CI-SPC-0007
| 5.4 | Compressive strength testing |  |  | Compressive strength results meet >32 MPa at 28 days | AS 1012 Test Results
| 5.5 | Inspection of surface cracks and defects |  |  | No major cracks or surface defects observed | WBS-SS-CI-SPC-0007
Part 5 – Final survey and as-built verification (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 5.2 | As-built survey verification |  |  | As-built levels and layout match design | As-Built Drawings, Survey Report
| 5.4 | Final inspection sign-off |  |  | Final approval of the slab surface, dimensions, and finish | FIC sign-off
Document sign-off
Final sign-off
| Company |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
ROBAR
SEPD
Document No: RR-SEPD-BESS-FIC-002 ¦ Revision: 00
Pg.3