## Checklist Templates
Id | Type | Name | Values | Prompting Name
b8a9f919-9b7e-4441-b9f2-6d4f78511368 | checklist | Asbestos Removal Works |  | Asbestos Removal Works
e44730e9-8d98-4d80-b858-c7d0a991379d | checkpoint | Air Monitoring Results
4c6cbb1a-bbc6-4c73-ba0e-c030b7f649f4 | checkpoint | Attach Photos
41fa11e9-2261-4ff7-be8f-d445a327cc9a | checkpoint | Attach Clearance Certificate
c0565b94-c207-4824-9453-2b2bdb7d894a | checklist | Block A - Seismic Bracing QA Required |  | Block A - Seismic Bracing QA Required
98fc351c-1d72-451c-8ef2-2334522bcfb3 | section | Report dated 4/7/23
48a11a89-b1e1-4770-8f92-4f36a0370b0c | checkpoint | Item 7 - Photo required of control joint between bulkhead and full height wall
47bc5567-a3e2-4ea0-8083-d2339c5c82d8 | section | Report dated 4/9/23
56eb3877-63a4-4321-a3d2-02a8ea319ec4 | checkpoint | Item 13 - No photos provided for fixed ceiling hangers at seismic joint
92c07780-8868-4149-afb7-955ed1d4fa7f | checkpoint | Item 17 - Ensure mechanical brace indicated below is installed within 600mm of corner.
2d6263b0-bf31-49cc-ab44-cebc4a3aee52 | checkpoint | Item 18 - Mechanical duct dropper has no clearance with above cable tray. Fix cable tray to bottom flange of steel beam with EA bracket on either side of cable tray.
e355d2ac-c09b-48f1-ab2e-009d68f1a10c | checkpoint | Item 19 - Ensure GIB Negative detail is provided underneath structural elements for all walls with deflection track.
22695f43-d000-5c3b-bfa0-c7366c2a8a49 | note | No photos provided showing negative detail in full height walls (at DHT Level).
2acf0eb6-c56a-4e41-9059-8a18456ee954 | checkpoint | Item 20 - Install additional lateral brace (transverse) to highlighted ducts on following page. Additional brace is due to flexible connections to units.
7f41bedd-a21a-4f7e-8b27-efa5c668965d | checkpoint | Item 21 - Some braces fixed to underside of purlin with timber block and one - two screws. Not okay. Must be installed to bridging or direct to web of purlin with CPC 80.
14254c24-7d8a-4367-b3f7-108ad2d9d6fb | checkpoint | Item 22 - plasterboard ceiling above reception braced incorrectly. Braced with GRIPLOK braces. Not okay. Braces required to furring channel as per design. Strengthen as per attached detail.
05aebd9d-6b8a-4933-ac05-f137e567f48d | section | Report dated 4/9/23: Timber Bulkheads above reception require strengthening:
bb3508b8-d956-4a83-b844-1f7bbed16b17 | checkpoint | Item 14 - Bridging members required for timber braces as per KCL Details. Can use CPC 80 brackets instead of EA on detail.
e902bed9-5d66-5cc8-9696-b97cea749de5 | note | Bridging for braces for timber bulkheads not installed as per design. Remediate as per design.
73a1f7ba-0221-42bc-8c4c-5d5c5c96fe4f | checkpoint | Item 15 - Add additional 90x45TS to make 90x90TS bridge above droppers with braces on them.
57b365b0-ecf5-59e7-b1ae-a4b77f564bb5 | note | - Minimum 2x screws required per connection required for timber to timber connections. - Braces cannot fix to open face of purlins. Must go to back side of purlins. Timber bridging not strengthened at brace locations as required in last site report. Timber to be added.
6a602165-57f4-4979-baaa-f91dea336881 | checkpoint | Item 16 - Move / extend brace arm to achieve required clearances for timber brace to dropper connection.
a6d217da-f0fe-5fe2-b043-7f268572a897 | note | Timber braces not moved / extended to achieve required clearances for timber brace to dropper connection.
f60d406e-5f7e-4b31-8013-b06ff7bafe04 | checklist | Compliance Documentation - Russley School |  | Compliance Documentation - Russley School
af4b3726-966d-4051-9121-0a44f1c18c29 | checkpoint | Structural PS4
8d4b3211-dde7-4956-b52e-1417c56b836c | checkpoint | Geotechnical PS4
19d6935b-25cf-4655-9b50-3841515306a1 | checkpoint | Hydraulic PS4
d067bb6f-9456-481c-8a5f-e813ad2a2a15 | checkpoint | Mechanical PS4
869c93bf-98a8-4f65-99f1-a23467c3fcbb | checkpoint | Fire PS4
8eff2514-080a-4266-807a-4d8c034a6212 | checkpoint | Civil PS4
16c06e63-8d8b-4cbe-9684-e5b181c629e1 | checkpoint | Seismic PS4
1ed60a44-0f36-4776-b704-1f51c778f538 | checkpoint | Building Location Certificate
d55ffdbb-6129-43b3-884c-eee833f30e4b | checkpoint | Certificate of Title
00a7aac0-baf7-4ef2-a7ac-41e142a7cf03 | checkpoint | CPU Application Form
3d6339dc-a68d-45f9-bc5a-47e07524f713 | checkpoint | CoC Application Form
296df35b-91e3-4407-a6c1-16e113963cca | checkpoint | CPU Certificate
acb68339-fe78-416a-9e44-0d3ec1db36dc | checkpoint | CoC Certificate
b24e461a-f950-553f-aa85-81d08e6f7933 | checklist | Concrete Pour Checklist (Self Perform) |  | Concrete Pour Checklist (Self Perform)
437c17a3-85aa-5abb-aa70-e192f061714e | section | Pour Details
1870e61d-7e27-417f-a394-0386a875323c | checkpoint | Pour Details
bfe43aae-b877-5eee-a40e-c8f28079b1d4 | textbox | Area to be poured:
9342ebeb-75f3-52f4-b700-812d434e522c | textbox | Date of pour:
137b4e15-56dc-57b4-a928-033b272c175e | checkpoint | Latest drawings available, checked and referenced
6295d1e2-8ec5-52af-92c8-9f10c3b37124 | section | Formwork and Embedded Items
31cad3d5-1c41-5266-b969-3f685710670d | checkpoint | Formwork - location, height, falls and dimensions checked and accurate
55668503-73c3-5ce7-a6e1-32a827076d63 | checkpoint | Service penetrations formed correctly and locations checked/correct
f78d33cd-2e25-59dc-9178-262857563c85 | checkpoint | All surfaces correctly prepared (e.g. joints to existing concrete, release agent to formwork etc)
66d8c5d9-4a1b-5603-8dd3-5c43c2d7afb6 | checkpoint | Any control joints/ stop ends installed accurately and correctly braced
9f8df55d-6f53-5da7-bda2-b378a4669d72 | section | reinforcement
2472b193-2a75-5339-8069-257bf3f8ef4a | checkpoint | Trades QA received, attached, reviewed and approved
70db0c9f-5cf9-5025-8639-ac9e5496fdff | signoff | Raise Remedial / Request trades QA / Sign Off
d60d8c9d-1110-5bf1-ac9f-e2a57a0fcfbf | checkpoint | Size and type correct to specification
552d4d55-5b66-58d2-9dc4-f28279042880 | checkpoint | reinforcement spacing and location correct
b7df81d8-620b-5cba-8f1b-50e6248e0be9 | checkpoint | Specified covers checked/correct
812b6f4e-a8d4-5ab7-8925-024fe9cb3acf | checkpoint | Splice laps checked/correct
d9257527-facc-5a71-bf85-1df5d463cf23 | checkpoint | All couplers installed correctly (if reid bar couplers have been used, has epconC8 epoxy been used as specified)
9364afed-553b-5487-82e7-b2cdb942e50d | checkpoint | Any starter bars are installed correctly (location, size and spacing )
538cc68d-0d73-57bb-9608-2d6897423abb | checkpoint | Any additional items installed/ completed (trimmer bars etc) and excess reinforcement removed
8caa6802-6912-593e-a333-2826c0914282 | checkpoint | Welding certificates sited and attached
f1895b07-825e-508c-be95-c7074ddff417 | checkpoint | Mill certificate reviewed, attached and approved
51d910a3-59d1-5523-8490-ad5abaaf51b4 | checkpoint | reinforcement installed correctly to specification and ready for concrete to be placed
3e4ee940-3962-539f-b494-aa31054d6e67 | section | Pre-Pour Completion (Approval to pour)
ad00d49a-55a3-5ddc-8502-ee97b2cf8199 | checkpoint | Any waterproofing elements have been correctly installed and checked
ff45da24-f9b6-5b4c-805d-c54843392343 | checkpoint | Any relevant service requirements completed (locations checked and accurate)
e15b117c-d2a9-546a-bb82-eb587a9edb15 | checkpoint | Engineer inspection completed - any observations / remedial work documented and closed out
8551c254-8fcd-57c1-8036-dca6c9a3ba7e | checkpoint | All relevant inspections completed and attached
a0c78d52-6bd1-59b3-b437-ad06236c71eb | checkpoint | Main contractor inspection completed - Approval given to pour concrete
cc0cc6fb-1566-56b6-899a-4439eaf5cc25 | section | Concrete Supplier Specifics
ff0daeab-c2ad-47f1-b443-762ac82e1c1a | checkpoint | Concrete Supplier Specifics
08de9ec0-2944-57b8-9e18-550950e2ee33 | textbox | Supplier Name:
153aaeb2-f6dd-585c-b655-1b3d2eb22478 | textbox | Specified concrete strength:
104c2f02-1473-5f08-8e6e-198a5127e0ff | textbox | Concrete strength ordered:
010844b5-e6a1-5225-9cf6-877326ea0d7a | textbox | Concrete quantity ordered:
c2a0c45a-a14b-51c0-889b-20dd9a758bb5 | checkpoint | Test blocks booked
19d4d747-6bd1-5ca9-a47a-3d8d02ea3079 | checkpoint | All concrete dockets photographed/ attached
e96e58af-2414-5567-8192-f270dbb3a19a | checkpoint | Concrete strength test reports attached and required concrete strength achieved
cb588cf4-14bd-5a90-a2b6-f1805be97460 | section | Concrete Distribution
3c3449d9-ab97-5140-8553-926446511dc7 | checkpoint | General distribution photos, documents and observations attached
1c8b2c8d-add6-5046-adbf-071bd50e981c | checkpoint | All concrete distributed correctly (area left clean and tidy)
a28c464e-acb8-5c38-b58d-703b020faaf1 | section | Placement Method
28e50c19-7d55-517a-9865-60fb77594fe1 | checkpoint | Placement methodology confirmed and necessary plant and equipment on site
20eb1aa2-0543-59f3-b4e5-1f60712cd7d0 | checkpoint | Heights and falls checked/confirmed before placement
1ba50dd5-75b2-5eb9-b537-3367140d1297 | button | Is the cover correct to specification | Yes, No
f72af891-01a1-5dd7-a643-b7a8cc5f0aa5 | checkpoint | Heights and falls checked/ confirmed after placement
8c5a4c09-2cb8-5981-a3c3-e53f1fa16e55 | checkpoint | Any curing compound applied correctly
4c52fe01-af86-5919-a8b0-6cf4ce645d12 | checkpoint | Concrete placement completed - specified level of finish achieved
d21b14a7-739f-588d-8c47-71bb08be490c | checkpoint | Area left clean and tidy
773f530a-df5a-5e65-848f-0f09e77959db | section | Post Pour Checks/Sign Off
d0deee38-dd1a-50ea-aea9-e824231147d0 | checkpoint | Any remedial work completed
405c0c3a-7a1b-534e-85f6-c310b8a9d9e5 | checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
43b36c59-535f-49f5-ae2d-b6b7cfa8d09e | checklist | Excavation Works |  | Excavation Works
26c0f2a9-6873-4bb7-9f08-3315e9621407 | checkpoint | Foundation Beams
a2bb2980-6e28-4c29-a937-2d46f8ad8670 | checkpoint | Sub Grade Inspection
6d6e107e-b5d9-482a-95ff-b48a68963fd3 | checkpoint | Backfill Layers
31463602-4ef3-4cee-9ae1-2d89976a99d4 | checkpoint | NDM Testing
ddbcd545-a794-50d4-9e82-cfe0d448a719 | checklist | Final Sign Off |  | Final Sign Off
0d821de5-3d8d-5e89-a698-c53321ae4885 | checkpoint | Doors Installed including drop down seals if applicable
f6dc7d8b-2f67-54d4-a8f5-1c570b7f87fe | checkpoint | Hardware as per approved schedule
4b50bddb-cae1-5b9c-abf3-b6ccc0a96df5 | checkpoint | Architraves and skirtings installed
b4888850-c034-5a5c-97a0-26de8b411283 | checkpoint | Electrical Power/Lighting second fix installed
f234ed4d-c909-5f0b-9844-f987ee3a20df | checkpoint | Sprinkler/Alarm second fix installed
5d12ee1b-536d-50ce-a53a-2ee3e88d7986 | checkpoint | Security second fix installed
253e68aa-867a-51a0-83c4-ed81b1f69e84 | checkpoint | Data second fix installed
6ae8cf9d-5255-509a-a6b2-56557403a07c | checkpoint | HVAC second fix installed
dfda991b-3351-5969-a7fb-21ff43be7895 | checkpoint | Floor finishes installed as per architectural plan
3f9f9f52-5e6d-558d-9ea8-5eeab17cf76e | checkpoint | Paint correct colour
7999fac9-a55f-551e-8397-6c32f5a7dc8e | checkpoint | Door signage installed
244633a5-65b5-51f4-931c-ca701e4147ad | checkpoint | Manifestations on glazing
67433f06-71c7-59a4-a088-d9d5f1e2c621 | checkpoint | Joinery installed correctly
ecb2393b-d0ab-4536-928f-c47fa54f521a | checklist | Roofing & Spouting |  | Roofing & Spouting
a9367bad-a908-4517-8921-06b82c35f381 | section | Pre Roof
7c7cc3de-0214-4bf5-8944-60868809edec | checkpoint | Roofing Type
24edb369-3b79-402e-9b35-8c30e117f840 | checkpoint | Confirm Roofing Colour
cd5c7e53-8f1e-46b6-a10a-44db05677d7d | checkpoint | Confirm Sample Provided
6a8c1d15-780a-409e-8181-408cb3891c0d | checkpoint | Confirm alignment of structure
a9b8034d-cb2f-4c0d-acd4-4c5b33e9b095 | checkpoint | Confirm batten / purlin spacing
55de2e4e-d54e-45c5-9fd9-a9fd4f0f3340 | checkpoint | Confirm building paper / netting required
114b3942-d4c1-4b5a-8c86-4858739fbec0 | checkpoint | Confirm insulation
558e84ab-bee9-478f-8c7f-f584737bf624 | checkpoint | Framing / Substructure
a0994dbc-b812-4089-afc5-3fe4888b55e7 | checkpoint | Confirm Council Pre-Roof Inspection Required?
d2c93eb2-c900-4fb1-b7f9-ff02f76c482f | signoff | HOLD POINT
356e1ef9-fd3f-4a05-b5cd-6cb83248d30c | section | Roof Installation
ecdc60ef-38b4-4c7b-b56a-b4566f54350c | checkpoint | Safety Mesh / Safety Nets
acf1da60-7d0b-4fea-bd60-57881091a1df | checkpoint | Confirm Fixing types
ba34bc0b-c15a-4308-8e30-a44c53a68d0a | checkpoint | Confirm Expansion joints, laps
58a5d9f7-23f3-4f48-b5a6-287ba86b0243 | checkpoint | Confirm Alignment of ridges, hips valley, falls
d64ce778-a47b-4266-9604-93d7755e8718 | checkpoint | Confirm compliance with Weathering details – E2
fa9677ca-9171-4216-a93b-694517d02b74 | checkpoint | Confirm Air passages
d72df3d3-5d30-43cc-bc14-bb0401f8fb37 | checkpoint | Skylights, correct position, sealed, flashed
fe632bfb-cc00-4b99-8684-b14a3ee114ec | checkpoint | Ridge Flashings
60a86eca-cb4c-4218-97db-fbf7842661f5 | checkpoint | Apron Flashings
e2545636-0a3f-448c-a0c2-ca2a2addb79e | checkpoint | Barge Flashings including correct laps
79ce42f0-16cb-44e7-8062-039f9b64986a | checkpoint | Penetrations sealed and complete
8886d70f-adc7-46b6-b016-99bad72a7286 | checkpoint | Gutters
b7a7ddb6-f747-4edb-8269-1bc4c0cda1cf | checkpoint | Fascia lines straight & true
6f842ad0-d151-446a-8d44-9bc2ba71fff9 | checkpoint | Brackets even spacing
7cecedd4-0d60-41c8-a603-4feb0ceffb2d | checkpoint | Brackets correct fall
9cc448d0-29ea-4e13-b4fc-b02eb828991f | checkpoint | Correct downpipe position
ec8057b5-75bd-4d62-8e00-b6da5cd64a6a | checkpoint | Spout expansion joins @ 15m
8eb71f95-4499-4dd9-a0b1-362bce106d2a | checkpoint | Spouting straightness
263884c4-8741-48b1-957f-01e92f4d4c96 | checkpoint | Snowstraps
6756ccfe-0e33-41bf-b711-a25658193fd6 | checkpoint | Rainwater Heads
c6c4b62f-8dfc-4ba9-ae55-8aa6f414c556 | checkpoint | Fall Arrest System
f7b589dd-d180-4f4c-b8a5-6cdda40a890a | checkpoint | Roof Access Platforms / Monkey Toe
27886045-275d-45d7-8181-f1de34e1c1a2 | checkpoint | Roof Ladder Brackets
1db3ba99-5bda-4695-bbdf-5d17ebe5d11c | checkpoint | Consultant Inspections - Structural
e24cf6c2-a760-4318-80ef-c4448dc40248 | checkpoint | Consultant Inspections - Architectural
50d4afbd-145f-4318-b830-155dcfa9f672 | checkpoint | Trades QA received, attached, reviewed and approved
065ad6d5-8016-444b-a6c0-91fdd2be2421 | checkpoint | Roof Clean + Roof Works Complete
6c45a7f4-6b3d-49d7-a07c-ba330b2d56b6 | checkpoint | SIGN OFF
7c86331b-59ae-4834-9014-524d598371ac | signoff | SIGNOFF
3e49197d-687a-4e47-9e50-23e4be408f12 | checklist | Timber Framing |  | Timber Framing
922a5bb2-c188-4503-b2d4-3b6452870bd2 | checkpoint | Confirm Wall Type Plan (Drawing Numbers and Reference)
86f185d0-4b45-5ecd-894a-0ac51b94a394 | textbox
9308ce1b-9513-40fb-854d-075adaa7b120 | checkpoint | Confirm Wall Type Schedule (Drawing Numbers and Reference)
e1b218e8-572b-59a6-a9c6-293b595ca232 | textbox
eb4b52c0-8c2d-4167-9f97-cf673f148502 | checkpoint | Confirm Timber Treatment Type
18606b01-ffac-40f9-aea5-8c9d0f2e9f4e | checkpoint | Confirm Below Checks Complete
d83677b5-7570-52d5-857b-4ee4c6d79886 | button | Damp Proof Course Installed | YES, NO, NA
d40e1fd9-ba29-5887-ae29-398033acb13b | button | Confirm Set Out of all openings | YES, NO, NA
091b4083-cd2c-51af-9cd0-217bebe1c59c | button | Confirm Stud Centres | YES, NO, NA
e02fa32f-2a9a-59a1-b795-a5a204ce521c | button | Confirm Dwang Centres | YES, NO, NA
e90d5a6d-734b-58a9-8eb5-8179c98dc348 | button | Confirm Lintels | YES, NO, NA
4884a9b7-828f-454a-ba2b-750f5e166c12 | checkpoint | Dimensions / locations checked and accurate
ee48547a-edde-4552-bc51-07198daa87f8 | checkpoint | All frames are square
be2abd56-0ee9-4014-905a-949840596176 | checkpoint | Frames are straight and level
f28c64c7-49c6-4bcb-87eb-031e851ef2ba | checkpoint | Fixings are correct
6c49dfef-4d92-4a34-b022-e7e39ce9564a | checkpoint | Any bracing requirements installed
2c42b8a1-8d4e-4a30-b94b-46f83ebee899 | checkpoint | Any additional photos, comments and observations
f1bf8638-c04c-49f3-8c17-f79d33f7e79f | checkpoint | Trades QA received, attached, reviewed and approved
02d355e8-7677-4b24-8fa7-f3329ebdc19b | checkpoint | Raise Remedial / Request trades QA / Sign Off
134f4fad-b8ac-4e08-9214-73098164fcfe | checkpoint | All framing completed correctly within tolerance in respective area
dae93589-4599-56fb-b8c5-1ff16f3b3678 | checklist | Underslab Services Checklist (Audit) |  | Underslab Services Checklist (Audit)
a2a248ec-b0bf-501d-9cf9-2076d1f8c33b | checkpoint | Electrical services/ conduits installed, fixed in correct location, backfilled and correct as per design
9dcd9292-fb26-5127-8c71-23a8ab75b7d2 | signoff | Raise Remedial / Request trades QA / Sign Off
7caa46f7-253c-5cae-a0f6-4f02ff8b401c | checkpoint | Hydraulic services installed, fixed in correct location, backfilled and correct as per design
b5a682dd-1283-530b-8bf1-deac49046a86 | tickbox | Storm Water
1f7ddc55-2b40-5ae3-92af-f4616ed67bd2 | tickbox | Sewer
59f5c4f7-f042-5441-aad7-5908288298da | tickbox | Water Supply
62e21613-9781-569b-89e2-3ed1640b5c7a | signoff | Raise Remedial / Request trades QA / Sign Off
e1a16d83-b15a-5047-8dfa-fc41870ce3f9 | checkpoint | Gas installed, fixed in correct location, backfilled and correct as per design
1fca7fd9-193d-5caa-b68e-26abd8ae99d4 | signoff | Raise Remedial / Request trades QA / Sign Off
2428ad3b-37d1-5d82-989e-565e9f382fa8 | checkpoint | Telecommunication/Fibre installed, fixed in correct location, backfilled and correct as per design
00c88ec9-47c9-5314-863c-a40a07658868 | signoff | Raise Remedial / Request trades QA / Sign Off
9f59dd52-cf16-544d-923b-67efb5daa5cf | checkpoint | Any other relevant services installed, fixed in correct location, backfilled and correct as per design
85d45bbb-489e-5e66-b562-6b10e372a935 | signoff | Raise Remedial / Request trades QA / Sign Off
eaa9d388-ff58-5994-9ae0-550db5ab233b | checkpoint | Any additional observations / attachments
cb6b1fac-e4a5-5eff-9ac4-c7ee34614d30 | checkpoint | Any relevant inspections carried out and attached - observations documented and closed out
2db07358-5d51-5848-99ed-e6ff0439328b | checkpoint | All subfloor services correctly installed to respective area