## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | 2a6c2a8f-c62e-49d0-993f-5cfb89d77095 |  | checklist | Paint ITP |  |  |  |  | Yes | Paint ITP | 0ea8d9f6-4dea-49b9-be6e-86d1e831b611
checkpoint-group | 88943f59-4889-41fb-861e-d0035c03956f |  | section | Spray out internal
checkpoint-status | efa86a45-d5b9-45f5-b295-0fb4fa974cf0 |  | checkpoint | All plastering sanded and internal junctions free from dust prior to sealer undercoat
checkpoint-status | 209920a8-ba82-4a23-a2e7-dfc22c09c79d |  | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion of spray out.
checkpoint-status | a74242c1-9064-4da1-8431-a4877b6f4e95 |  | checkpoint | All nail holes, joints and gaps are filled prior to painting.
checkpoint-status | 6c34d677-7bc0-4325-90d5-b7a3883d2a50 |  | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
checkpoint-status | de4d89d2-3053-4376-ba0b-44771d327f44 |  | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
checkpoint-status | f3caa5cc-6124-4ede-904b-43ddd2d87017 |  | checkpoint | All ceilings are lightly sanded in between all coats and are back rolled and layed off in reasonable fine stipple finish.
checkpoint-status | b8300d28-6117-4ee1-b21f-59d9238c7438 |  | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
checkpoint-status | a82abec7-ade5-4958-ad85-94b968fb325d |  | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
checkpoint-status | 06595880-ea5a-4d50-ad8e-7f5d1aac74e2 |  | checkpoint | Clean up is completed ONLY in the supplied wash out area.
checkpoint-status | a2dbc1d5-b112-4cf7-9a52-1938473a2e3d |  | checkpoint | All rubbish is to be placed in the bins provided and the area is to be left clean and tidy and void of rubbish and excess materials.
checkpoint-status | f5b9b4d1-f6a5-49b4-9c63-e5131be206e0 |  | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
checkpoint-status | bb7c6657-bd93-471d-ba7b-bd564f55d6f2 |  | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
checkpoint-group | 72f69e43-a01e-4204-be78-9a0c6c073a63 |  | section | First Coat & Final Coat
checkpoint-status | 665d6390-232f-4118-a3c4-5af5d479fe25 |  | checkpoint | Full protection to joinery, window frames etc prior to painting. Any overspray is cleaned off prior to completion.
checkpoint-status | 1fbe6384-cd29-424b-ae73-fd321781ac4d |  | checkpoint | All nail holes, joints and gaps are filled prior to painting.
checkpoint-status | 14fb0010-ba39-4f7f-976e-5484523542f4 |  | checkpoint | All edges to internal / external doors are sealed and painted as per manufacturers specification.
checkpoint-status | deaf4d8b-8d5b-443d-b18d-dec0569d0673 |  | checkpoint | All hinges, door furniture, latches and striker plates if removed are to be retained and re-installed prior to completion.
checkpoint-status | 06345fa7-1ddd-44c5-9727-c5c52de86792 |  | checkpoint | All walls are lightly sanded between coats.
checkpoint-status | cd1795d4-0f85-4785-bb99-5538f091ae9a |  | checkpoint | All wall coasts are back rolled and layed off in a reasonable fine stipple finish.
checkpoint-status | 0c7d8060-1715-43b3-9288-1d2e5a1fd78e |  | checkpoint | All paint is NOT site tinted or any other liquid added or altered without written approval.
checkpoint-status | ce5efa3d-41eb-458c-873b-1343c139323d |  | checkpoint | All cutting work is consistent is consistent and complete in a tradesman like manor.
checkpoint-status | c439dff3-9ec1-4cc4-89a7-9c5ae6d06e66 |  | checkpoint | Clean up is completed ONLY in the supplied wash out bay.
checkpoint-status | ec188ff6-06c9-4be3-bbfc-854c6b01df44 |  | checkpoint | All rubbish to be placed in bins provided and the area is to be left clean and tidy and void of rubbish and excess material.
checkpoint-status | 8a4e00b6-115b-4367-b07a-d68219ef5243 |  | checkpoint | Ensure no damage is done to other trades work (if so, you Must Report to the Supervisor and Wadsworth Project Manager immediately).
checkpoint-status | 192f82fa-d621-46df-bf91-e25e028b96f4 |  | checkpoint | All completed works are consistent with the scope of works supplied by CBGU JV, the supplied paint specification, and approved samples.
checklist-sectioned | 60941a89-af19-49e6-8d08-983a2fcb252f |  | checklist | Ceiling ITP |  |  |  |  | Yes | Ceiling ITP | 564a6db8-cafc-44a0-9138-7b614c90ae66
checkpoint-group | df21acb4-7ac5-4f1f-8858-d4db775ccaeb |  | section | Set out
checkpoint-status | ec8df6fb-c03c-461d-a492-719cfbac4602 |  | checkpoint | Reflected ceiling plans current revisions checked and ceiling set out completed as per the current plans
checkpoint-group | 31c3a236-605e-4cc3-9e6d-4d725fb1980f |  | section | Construction Generally
checkpoint-status | 9e057e2a-c0b6-4516-a675-5ebad6a02b92 |  | checkpoint | Install & fix to prevent looseness or rattling of ceiling components
checkpoint-status | 827de70f-711c-448d-91f6-33e3d6b6a94b |  | checkpoint | Install the ceiling to allow for differential movement at abutting surfaces
checkpoint-group | af220dc3-de12-40c4-8326-d2f53041c0fe |  | section | Suspension system
checkpoint-status | acd97354-4cfb-4f96-a247-b622c8d82549 |  | checkpoint | Provide suspension system and workmanship as per supplier installation guides.
checkpoint-status | 768509fb-78d0-4972-9420-d6a419064b18 |  | checkpoint | Provide additional back support or suspension members to prevent distortion, overloading or excessive vertical deflection.
checkpoint-status | 4e7ba411-d00a-4b97-8af4-ea8b35110ae5 |  | checkpoint | Ensure that the failure of any one suspension point does not cause a progressive failure of the ceiling.
checkpoint-status | 8a223bbc-a527-4a5d-a551-4eb47eaf77c1 |  | checkpoint | Where applicable, provide height adjustment with a length adjustment device at each suspension point.
checkpoint-status | fe5ff95f-8bfb-4cbb-bc5e-d3ecf89ff170 |  | checkpoint | Services: Do not fix to the installed services. Where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.
checkpoint-status | f62b6504-b592-4b84-ac0d-6b80ea4c89b5 |  | checkpoint | Uplift: Suspension system and framing to resist uplift.
checkpoint-status | abfa066a-8d7b-426b-b2b4-dfbe660a8628 |  | checkpoint | Tolerances: Flatness, twist, winding and bow: 1.5mm deviation from a 1.5m straightedge places in any position
checkpoint-group | e678b142-ee42-4314-ad52-137645fe8963 |  | section | Hold Point
checkpoint-status | cf5e8cde-4b70-4f7f-97b4-75a150d112f1 |  | checkpoint | Suspension system completed – Ready for installation of ceiling tiles, lining and panels.
checkpoint-status | 5bf9d431-1723-4d16-8dc9-2c724edc6fcc |  | checkpoint | Confirm all service trades are complete & ready for closing in of ceilings.
checkpoint-group | 19022f8c-c8aa-4401-8040-6293e27cd329 |  | section | Ceiling Lining
checkpoint-status | 963a2d89-16ad-413f-a235-d8d94e9fc2aa |  | checkpoint | Provide board lining to a finish and workmanship as per supplier installation guides.
checkpoint-status | f8bab96a-40ba-4673-ab6a-772ebd543a7c |  | checkpoint | Fit accurately and neatly, without distortion and free from air leakage and staining.
checkpoint-status | 927ce9be-f4d9-421f-aeaa-a9a61b162958 |  | checkpoint | Set out patterned or heavily textured materials with a consistent direction of pattern or texture.
checkpoint-status | 6f870619-6eff-4e76-bdc8-4ca8f0f68d5e |  | checkpoint | Cut ceiling unit edges: conceal, or finish to match prefinished edges.
checkpoint-status | 6653c94a-ba99-477e-bb81-135683f26973 |  | checkpoint | Multiple sheet layers to fire rated and acoustic rated elements: Fill & flush up all joints on each layer and caulk up perimeters and penetrations before commencing succeeding layers. Stagger all sheet joints by minimum 200mm.
checkpoint-status | 96ad51c0-661e-4dc0-9f9b-25c553bedd2d |  | checkpoint | Board joints support: Provide framing parallel to the joint on each side. Do not fix the lining to abutting building surfaces
checkpoint-status | f1a5c31f-ed9f-4f79-9dab-08dc398f772b |  | checkpoint | Flush joints: Provide recessed edge sheets and finish flush using perforated paper reinforcing tape. Locate & position joints to intersect light fixtures, vents or air diffusers.
checkpoint-status | e6e953ea-3ae7-4e52-85a3-77e2a16e4326 |  | checkpoint | Tolerances: Suspension system bearing surface for flush lined ceiling to AS/NZS 2589
checkpoint-status | 385a687a-58ec-4953-9f4a-ff54cfaa4e70 |  | checkpoint | Levelness: Max tolerance of ±5mm relative to the documented height datum for the ceiling in each room or space.
checkpoint-status | f43f3b23-413a-4e94-b0a4-7480f5518c83 |  | checkpoint | Trims & accessories: Provide trims at junctions with other building elements and surfaces, including walls, beams and penetrations.
checkpoint-group | fc60b50f-9047-4062-94ee-15d4b85f3921 |  | section | Control joints
checkpoint-status | 7d3c4f46-58c8-4762-8419-a128541f1a72 |  | checkpoint | Align ceiling control joints with the structural control joints. Do not bridge structural control joints.
checkpoint-status | 6de76021-c98d-414a-a0cb-c25f67109790 |  | checkpoint | Provide purpose made PVC control joint beads where documented.
label | f0c27c05-52b8-517a-9c73-709e1e317e71 |  | note | Provide framing parallel to the joint on each side.
label | e222f189-5973-5f18-b52b-88d5711f115e |  | note | Plasterboard lining: 12m centres
label | 4368e638-4bf3-536b-aa77-94d5b545b559 |  | note | Fibre cement lining: 7.2m centres
checkpoint-group | ef0adfc2-c028-4fe7-822a-5a169d64906d |  | section | Bulkheads
checkpoint-status | a6f5e34c-d3d4-478f-9d94-9a9037e75b83 |  | checkpoint | Integrate bulkheads with the ceiling structure and brace to prevent lateral movement. Where ceiling is terminated at the bulkhead, provide for seismic requirements
checkpoint-group | da0256f3-cbe4-4d13-9295-3cd32b35cf7a |  | section | Tolerances
checkpoint-status | 1d622821-75bf-48db-8099-b921f31e63e3 |  | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge
checkpoint-group | 39515853-1ef6-456c-9453-59453db9229b |  | section | Acoustic installation
checkpoint-status | dde6be54-4b18-4264-8352-6524debaa001 |  | checkpoint | Where documented, place acoustic batts on top of ceilings system and butt to each other and to partitions.
checkpoint-status | 9f05ccaa-4eb5-4334-ba5d-7c7654634d19 |  | checkpoint | Tightly butt and trim neatly around services items and other items.
checkpoint-group | 2ae6b4da-8aa2-408d-bddb-b1631ac6f68e |  | section | Smoke baffles and acoustic baffles
checkpoint-status | 2bca070a-7f39-4228-bc4c-f757e5a675c7 |  | checkpoint | Provide approved smoke and acoustic baffles where required
checkpoint-group | 8cb5cbed-c345-4a0d-9cd0-f2953aafcfa0 |  | section | Additional checks for fire-protective board lining
checkpoint-status | 2ebd199c-6674-47c1-994f-201cb45fe579 |  | checkpoint | Check the fire resistance levels on RCP
checkpoint-status | 55a4ce48-a2b9-4e3b-b4ef-01a0dbc280be |  | checkpoint | Fixings: Direct to concrete elements and to purpose made steel framing
checkpoint-status | f6a3ab9f-0a6b-4147-b72f-62c2d7593769 |  | checkpoint | Penetrations: Seal penetrations in the board lining to maintain the integrity of the required fire resistance level including suspended ceiling hangers and suspension systems for services.
checkpoint-status | 30f159b1-6ad7-436e-aff8-c15282b883c2 |  | checkpoint | Board perimeter: Provide fire sealant and trims at junctions with other building elements and surfaces, including walls, beams and penetrations to maintain the required fire resistance levels.
checkpoint-group | 39155ce0-8d4a-4812-8403-f500f7b23321 |  | section | Access panels
checkpoint-status | 481dedf6-70a8-4ad3-ac49-a784a4e9f7a6 |  | checkpoint | Match the access panels to the ceiling in appearance and performance
checkpoint-status | eb441c87-2bb1-427e-ac29-52210f5099fa |  | checkpoint | Provide access panels supported and anchored to permit ready removal and refixing
checkpoint-status | 9b713267-0424-4f1f-a465-ce993f0aae1c |  | checkpoint | Provide fire rated and acoustic rated panels where documented or where required to maintain the designated rating of the ceiling element
checklist-sectioned | 848e56ee-ada8-47fc-91a8-0617df358e66 |  | checklist | Doors & Frames ITP |  |  |  |  | Yes | Doors & Frames ITP | 5f087745-b5c2-4776-bf1e-328690e3427f
checkpoint-group | 86bed9cf-9f51-4de8-8312-5a8703516545 |  | section | Take delivery
checkpoint-status | 865d4e21-8804-45c7-afe5-7b1831e50f63 |  | checkpoint | Frames as per design documents
checkpoint-group | ecf6d02a-86e4-4722-86ec-214d2541d222 |  | section | Setout
checkpoint-status | e55f14eb-0bea-4691-88ee-ac90d3c61699 |  | checkpoint | Ensure Frames are set out as per Setout Plans.
checkpoint-status | e78e87b4-603a-4d66-8758-f13de2569eed |  | checkpoint | Set out is to be read in conjunction with Door Schedule.
checkpoint-group | 61fe1cba-f20b-4962-b4fe-8f4b3b4cf31b |  | section | Execution
checkpoint-status | 59b4f18d-9f45-4079-8deb-17e834f41004 |  | checkpoint | Frames are filled in accordance with acoustic or fire requirements where applicable
checkpoint-status | 5b170df2-0a5d-4a79-94c0-732b38b4a58a |  | checkpoint | Frames are plumbed, levelled, straight and within acceptable tolerances
checkpoint-status | 3c4e0140-b001-4882-b13c-a8f3941a88a7 |  | checkpoint | Frames are adequately fixed or anchored to the building structure.
checkpoint-status | ce43b928-af78-47e4-8527-4cf41a10d78e |  | checkpoint | Frames are installed so that they do not carry any building loads
checkpoint-status | 0565947d-833b-41ab-b8c9-bd890fa9edd3 |  | checkpoint | Fire door frame note: Fixings to substrate to be in accordance with manufacturers instruction. Steel stud frame typically, 10 gauge steel screws at max 300mm centres and no more than 100mm from each end.
checklist-sectioned | 62b2cb19-6ba7-4d01-bcde-11769109993b |  | checklist | Underslab Insulation ITP |  |  |  |  | Yes | Underslab Insulation ITP | b4882792-5e7a-4bb5-998e-f7f925899cc5
checkpoint-group | d9c7f729-fe02-4e0a-94e2-6a742418c4e0 |  | section | Take delivery
checkpoint-status | 4ce07b67-b2db-422a-968d-97e6b8471ec2 |  | checkpoint | Insulation panels arrive as per Design Documents and defect free.
checkpoint-group | 7c6e30c1-bc28-4fdc-96cf-59543fa7e96e |  | section | Setout
checkpoint-status | 9d78fa72-c9f7-4156-b6ca-a8c3d1c88c69 |  | checkpoint | Ensure most up to date drawings are being utilised
checkpoint-group | 4df3161b-691b-491b-b519-5138d21aed7a |  | section | Execution
checkpoint-status | 18b5f090-b927-413a-ab59-dfa4eb87995d |  | checkpoint | Mechanically fix panels to Manufacturers Specifications
checkpoint-status | 9ad3eadc-7059-4e4d-8049-3bcafd323853 |  | checkpoint | Tape all joints and exposed edges with a minimum of 75mm wide silver tape
checklist-sectioned | dd109a6e-fa31-435e-8a6b-465a1e29bee4 |  | checklist | Partitions ITP |  |  |  |  | Yes | Partitions ITP | c70e4c50-b5be-4f98-9944-2ba9cadb2d7f
checkpoint-group | 36aac969-f31e-433b-a69c-3a5988236bc1 |  | section | Set out
checkpoint-status | 6d93512c-9528-45b1-b237-6519aa17711b |  | checkpoint | Partitions set out plans current revisions checked and wall set out completed as per the current plans
checkpoint-status | 1aa901e3-9f2c-464f-b036-6df7a7add872 |  | checkpoint | Minimum/critical dimensions (face to face) on drawings checked
checkpoint-group | 3c187d51-3817-4e00-8226-58a5f3131b8e |  | section | Stud Framing
checkpoint-status | 79b92609-84b6-43fc-8d26-aa402713cfb2 |  | checkpoint | Base & Head tracks fixed in accordance with steel stud partition design. Typically ≤600mm centres and 100mm from ends
checkpoint-status | 18614645-469a-413f-a01a-96dacd367188 |  | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
checkpoint-status | f7448dab-2cfc-4e09-ac69-cc0fee34cd7b |  | checkpoint | Stud spacings correct as per steel stud partition design. Noting max 450 centres for wet area sheeting.
checkpoint-status | c4598d48-3183-4a2f-9306-b0a446630af8 |  | checkpoint | Fixing to post tensioned concrete: Maximum embedment for fixings = 50mm
checkpoint-status | 90bb6b18-6a5b-4ae4-abf6-ef618f2a49e1 |  | checkpoint | Door frame openings as per Rondo design
checkpoint-status | c8af8519-a52c-4b41-8e2f-1c74ccd11bd8 |  | checkpoint | Full height partitions: Fix deflection head tracks to the floor slab soffit to allow a minimum deflection capacity of 20mm.
checkpoint-status | bd5638e1-2d56-4b31-815c-2bdaf43f21dc |  | checkpoint | Rotate intermediate studs into tracks for friction fixing
checkpoint-status | 60881634-ded1-4ace-beae-655ffa42894b |  | checkpoint | Structural floor control joints: Disconnect partitions over joints with detached double studs and ensure bottom tracks, bracing and top tracks are not fastened across joints
checkpoint-status | 5ecb68a6-2fa8-4d9c-89f1-9eed7698249d |  | checkpoint | Stud service holes: Splice additional stiffening to studs if site cut service holes exceed 1/3 the width of the member
checkpoint-status | 35b939cf-071c-4de1-b0b1-d1a83fc89f12 |  | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details
checkpoint-status | e1ee475e-7302-4649-9549-c0977c4187de |  | checkpoint | Noggings: Fix noggings as per steel stud design.
checkpoint-status | 07491fd7-4319-4243-b233-f6b051901844 |  | checkpoint | Door frames: Installed
checkpoint-group | 234d558f-9ac7-49fb-aa0b-a5dd7012af3b |  | section | Bulk Insulation
checkpoint-status | d5cffe78-324f-4ac6-8144-3ce0d3952dd7 |  | checkpoint | Install acoustic and thermal insulation.
checkpoint-group | d5e1bc9b-7f54-4a3f-a0e4-667c0418a6f1 |  | section | Hold Point
checkpoint-status | 785f630d-8d6d-4087-9729-6b8d0ca85e21 |  | checkpoint | Framing system completed – Ready for installation of sheets.
checklist-sectioned | f34a734e-9c7d-4042-9766-4df1ba13023a |  | checklist | Speed Panel ITP |  |  |  |  | Yes | Speed Panel ITP | d15fcef9-b7f0-42d4-ae0b-457156f5e67c
checkpoint-group | e43cca28-eaf8-44c4-aa85-1d8ca68271e1 |  | section | Prior to Commencement – The following documentation are completed and approved
checkpoint-status | 0abc53a9-5bde-4b13-b1ee-f8cc27b109c4 |  | checkpoint | Samples and prototypes submitted and approved (Fire sealants approved)
checkpoint-group | acd075d7-2d23-4c4b-8727-35f013577bcd |  | section | Set out
checkpoint-status | 0eaa03b3-8617-4edc-afbc-57babeb60129 |  | checkpoint | Speedpanel walls set out plans current revisions checked and wall set out completed as per the current plans
checkpoint-group | 75732784-3316-45e3-bb57-b7655259d8b2 |  | section | Framing & Speed Panel
checkpoint-status | 565af6c2-b7f9-491d-9bf3-ae1d63687721 |  | checkpoint | Powder coated speedpanel used where required
checkpoint-status | cec877ec-ecb0-4f63-a04a-1d9cc7cc1d30 |  | checkpoint | Fix tracks to floor & soffit per manual
checkpoint-status | e7fd97c8-09cd-42f5-ba78-84b224538eb1 |  | checkpoint | Provide fire, smoke and acoustic sealing where indicated on the drawings/details.
checkpoint-status | 0239bc34-eabb-4dc4-8116-f819860dd415 |  | checkpoint | Ensure that the configuration is as per the Speedpanel site specific detailing.
checkpoint-status | dae7090d-f643-4d62-8a75-e18940f5a012 |  | checkpoint | Ensure that all caulking is as per the Speedpanel site specific detail.
checkpoint-status | 40cd4a5b-ee47-4c34-8b41-2ae7efd17f88 |  | checkpoint | Ensure openings are as per the specified jamb & door sizing.
checkpoint-status | 3fb8d2bf-4883-4aba-8b80-6ae4d6d54ce7 |  | checkpoint | Door frames: Installed
checkpoint-group | 88344d9e-3dce-46ec-a6a5-bac899cd67f5 |  | section | Tolerances
checkpoint-status | 05fa2806-8406-4da1-93c1-21b1ee7f4797 |  | checkpoint | Flatness, twist, winding and bow: Maximum 1.5mm deviation from a 1.5m straightedge.
checkpoint-group | 5cd69a85-6c29-4b59-8e4a-947240feaaee |  | section | Penetrations/Access panels
checkpoint-status | 02329a5d-530c-4c81-b310-5d7ac7904856 |  | checkpoint | Installed as per Speedpanel design & install specification.
checkpoint-status | eeebfb90-4ccd-4111-90eb-4f5f05f9c448 |  | checkpoint | Correct FRL achieved.