## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
0d888666-84ac-507b-aa55-2eee1cf531e3 | checklist | AHU Install |  | AHU Install
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
93486dd3-e6a8-5917-9116-ff96e4b4d024 | checkpoint | AHU is correct for the system/building and position shown on drawings
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
d21146b7-36cb-59f9-b918-3e55a0bf13ce | checkpoint | AHU filters fitted and manometers connected
678fe04b-13d8-5146-bc8d-1d0469f95dbe | checkpoint | Is AHU installed level & plumb
11426ec1-04a7-590c-8171-5e3db96c3023 | checkpoint | Are seismic restraints installed
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
21619dc4-15d6-5923-a69f-0fd160e7b55a | checkpoint | Have subcontractors completed all work.
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
2bee4728-0aa4-5c40-929f-62bab4d436f2 | checklist | Air Curtain Checklist |  | Air Curtain Checklist
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
f183293e-6cf8-5a3f-a353-e8436348f42f | checkpoint | Air Curtain is correct for the system and position shown on drawings
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
c5e108b8-0034-5f97-9229-1c3a4fc3ea43 | checkpoint | Filters installed, size recorded
6b511ad9-a438-55bc-873c-cf6b9308170d | checkpoint | Is Air Curtain installed level & plumb
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
e621c66f-4062-5af6-b250-4d583d940065 | checkpoint | Electrically connected and fan going the correct way
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
97296055-1a8d-53d8-8483-25c890476077 | checklist | Attenuator QA Checklist |  | Attenuator QA Checklist
5c10c537-8060-5adb-b266-186a504c3db7 | checkpoint | Is the location drawings approved for construction
bdc57ca8-e6c3-5bef-b306-1646b7657bf1 | checkpoint | Attenuator is correct for the system/building
916703d2-0786-5c82-a483-3c5bbcc98a5b | checkpoint | Check casing, report any damage
848d8c9e-1ce5-57cf-810c-7a0b760d3690 | checkpoint | Orientation and connections correct, flow arrow correct
09920e86-173c-5738-a7af-b0c02117c633 | checkpoint | Attenuator is installed to manufacturers recommendations
fc0ad490-bb48-58ff-bb1e-0d962bc0d4d1 | checkpoint | Verify & record on drawings As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
4bbce625-4cf3-5574-b1eb-e25c2786113d | checklist | Chiller QA Checklist |  | Chiller QA Checklist
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
a1edb09b-9de3-50ee-bc15-545ba27e89d7 | checkpoint | Chiller is correct for the system/building
47c24851-a44e-53e8-b84c-8550f049f680 | checkpoint | Check for damage and report observations
4df259d6-2390-59a4-9bdb-e919a31621a1 | checkpoint | Check antivibration mounts
e3755413-d300-58f3-8862-097dca856014 | checkpoint | Chiller installed to manufacturers recommendations, check all connections are correct
62f48b2e-37fe-57f1-b563-dab77bb23598 | checkpoint | Is chiller installed level & plumb
11426ec1-04a7-590c-8171-5e3db96c3023 | checkpoint | Are seismic restraints installed
6e434366-2ba5-516b-9178-a611d5063ec1 | checkpoint | Sub-contractor work is complete
b857dc11-a196-594e-80c4-5d8d09022844 | checkpoint | Check chemical dosing of system
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
19c34633-c7e3-4886-8ba2-096c793279ef | checklist | Ductwork Checklist |  | Ductwork
25d5c34a-7e5f-4101-b67c-24aa3b30acf3 | section | Details
35f0799e-20ec-455a-9ddd-df1823667520 | checkpoint | Ductwork insulation complete
d42f9215-de69-4d2b-9290-a40e17b9009f | checkpoint | Ductwork pressure testing completed and passed
914bf567-49c3-4c07-82cc-b99a01d9fe9a | checkpoint | Labelling completed
3c24cd0c-e95b-44b1-824d-a09066f42a52 | checkpoint | Access requirements to any in ceiling components available
bb811fbb-b8a3-5e98-a999-cc5da3046f81 | checklist | DX AC Unit Install |  | DX AC Unit Install
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
5d0331b4-1e7b-57f1-bee6-a3e467419c71 | checkpoint | Is site safe for work start, report discrepancies (floor, walls etc)
b9f07dea-0bbe-500f-bab5-862a368f7e76 | checkpoint | AC Unit is correct for the system and position shown on drawings
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
0ab1ed76-354a-5ec4-81e0-a6bcbadcd6a6 | checkpoint | All pipework (Pair coil & Condensate drain) is correct and ready for installation
15c7b2c2-9bec-52e0-869e-c28fc2cb7399 | checkpoint | Is AC Unit installed level & plumb
d184bfd4-4a63-54e0-b537-dfc7a2990da2 | checkpoint | Fill drain tray to test condensate drain
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
29dbfe95-561b-5a38-928e-419f4551b91a | checkpoint | Verify & record on drawing As-Built dimensions (if differ or required)
321cb4e4-7bbd-5160-91ff-3ecd0ebbb885 | checkpoint | Check Electrical Supply to Indoor & Outdoor Units
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
30ea0a9a-2e2e-4d28-b79b-c62df43e9d95 | checklist | E4M Checklist |  | E4M
e3844992-febe-48b4-a189-c68187862a20 | section | Details
54575ed8-2932-4b43-9b3b-d6c2de374a7d | checkpoint | Electrical for Mechanical cabling complete
5da470ea-0a3d-52af-9b92-3916725424d0 | checklist | Fan Install QA Checklist |  | Fan Install QA Checklist
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
d3739250-6d7a-5fa6-a01e-4a201218a7bb | checkpoint | Fan is correct for the system/building
1dad82c4-1f6a-5d42-81d3-e5ee9ded3c29 | checkpoint | Check casing, fan blades, motor & cowl for damage, report observations
8ec3f017-cb26-5351-8763-1fd2c8567dcd | checkpoint | Anti vibration mounts are fitted
bff2dc0d-f785-54ba-b5a1-50de08609d9e | checkpoint | Fan is installed to manufacturers recommendations
ac1364cb-a398-5767-b63d-382fadfaba94 | checkpoint | Check brackets and seismic restraint if necessary
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
ecc1c53b-cca9-516c-a907-3381bc2f7ae4 | checklist | FCU Template |  | FCU Install QA Checklist
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
47f369d0-3539-540c-a65c-1cf588fe6d6f | checkpoint | FCU is correct for the system and position shown on drawings
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
c5e108b8-0034-5f97-9229-1c3a4fc3ea43 | checkpoint | Filters installed, size recorded
3bc39a8f-33f5-57d4-9488-29dfac0341be | checkpoint | Is FCU installed level & plumb
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
712cd2cb-e393-50e3-b793-727f09c0f1b6 | checklist | Filters Template |  | Filters Template
c243cb05-7d92-5c34-a6c1-985e2c875b1a | checkpoint | Locate and verify the AHU
3ddf148d-8b16-56c3-b282-ee2eda869f29 | checkpoint | Identify correct filter is being installed
4c666a7f-30d6-5495-926d-38412da95d61 | checkpoint | Has the Air Filter been installed in the correct position
604a3ac0-d3c2-54cf-b3ed-cbcc5d5c2b52 | checkpoint | Verify the last time Filter was changed and note current date on sign off sheet
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
407321f7-e8c3-548e-b56d-c7c1ed20e226 | checklist | Fire Damper |  | Fire Damper
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
ac0b292f-acdb-5fee-bfb9-05fc909e9968 | checkpoint | Installation of duct completed as drawn
a09e0335-e81c-5a14-9458-10df3b4f7b4a | checkpoint | Is the Fire damper accessible
d0260af5-b941-51bc-a8ad-6277db46cc35 | checkpoint | Testing of Fire dampers
8535249f-a39c-5add-b803-502ceb18b472 | checkpoint | Fire damper labeled
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
cada9929-e27f-5caa-8339-4b6ac709ddbb | checklist | Flexi duct QA Checklist |  | Flexi duct QA Checklist
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
08eeabf2-12c0-593c-9923-a37907b88956 | checkpoint | Duct delivered is correct for the system/building
c5c04667-87e8-52ef-b99d-efa79a863800 | checkpoint | Measure & mark off duct run dimensions on site
0196ab38-4847-56af-940d-dd32e405d718 | checkpoint | Install duct
0c1156a6-8911-5346-b572-9dbe84f19cb8 | checkpoint | Has duct been installed to the drawing
6434ad23-791e-571a-a8dd-76d116bbeb5d | checkpoint | Has duct been installed to correct levels & falls
6fa861be-62e1-5980-b748-f2b625de39db | checkpoint | Is flexible duct supported at appropriate centres
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
810c4b37-dd93-5c88-a445-ec7cd5ef4e63 | checklist | Grilles & Diffusers QA Checklist |  | Grilles & Diffusers QA Checklist
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
695f24b0-57bd-5290-88d4-8600f3eeafc7 | checkpoint | Grilles delivered are correct for the system/building
d932e7f3-afcc-5d79-940c-7f8cbf739413 | checkpoint | Check grilles & Diffusers for damage, report observations
c5c04667-87e8-52ef-b99d-efa79a863800 | checkpoint | Measure & mark off duct run dimensions on site
b027ac71-f635-5f7b-9e33-627fdc50f772 | checkpoint | Install diffusers & grilles
cc2105a4-86f5-58ea-bca2-a7b2185d337e | checkpoint | Has diffuser been installed to level & plumb
1c9cc190-5bc9-568e-80b7-da7a6a98f5e9 | checkpoint | Are fixings visible
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
c8ecfd48-074d-52eb-9467-4ca4a367a17b | checklist | Heat Exchanger QA Checklist |  | Heat Exchanger QA Checklist
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
6c94ddd1-79c8-55c3-ba46-304c8e2c9cc0 | checkpoint | Heat exchanger is correct for the system/building
aef8d228-9c10-597b-9b6f-92b26efca804 | checkpoint | Check casing, plates for damage, report observations
9a9c712a-2294-5723-88ac-e39f8482de6b | checkpoint | Pipe work connection adequate
c40ba1e6-e8ae-5101-b792-b0578d7513b6 | checkpoint | Heat exchanger is installed to manufacturers recommendations
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
f48ea813-2bf9-5288-b8c8-f7ecee3b64e4 | checklist | Heat Pump Install Template |  | Heat Pump Install Template
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
8cccb747-bfba-5eda-9647-b5e386e887d4 | checkpoint | Heat Pumps is correct for the system/building
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
259c46cf-ddb5-5b1a-9ae3-b19740e19f3b | checkpoint | Measure & mark location dimensions on site
fddc0cfa-c56e-53a9-8000-74d61f2f431e | checkpoint | Is Heat Pumps installed level & plumb
11426ec1-04a7-590c-8171-5e3db96c3023 | checkpoint | Are seismic restraints installed
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
5edee250-cae1-5062-9895-cec65bf996e7 | checklist | Heating Coils Template |  | Heating Coils Template
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
09efdbb5-3103-5728-bd41-56b3813ffba8 | checkpoint | Heating Coil is correct for the system and position shown on drawings
bbf0c66a-0ab4-56ae-a6dd-f6a070356c56 | checkpoint | Is Heating Coil installed level & plumb
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
29dbfe95-561b-5a38-928e-419f4551b91a | checkpoint | Verify & record on drawing As-Built dimensions (if differ or required)
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
3cbc5b11-e1a8-53b6-8f11-e222f2a4f215 | checklist | HTM 02 01 B15 |  | HTM 02 01 B15
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
6839f22e-1f80-5cca-a3bd-dbecc92094c7 | note | This is to certify that medical gas systems have been tested in accordance with paragraphs 15.163–15.167 and the results are as follows (insert values for gases – tick for vacuum):
c7c3f514-c434-5d0b-8e1a-265724b9f30c | checkpoint | Gas and Source (pass when complete)
f658641f-05ab-59cf-a369-3ec031e71320 | dropdown | Oxygen from liquid or cylinders. | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
c769ba31-a59e-59c1-a85d-8f8b2ef80eb2 | dropdown | Oxygen from concentrator | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
cc293031-aa9a-5bff-b131-85b14f67ae3f | dropdown | Nitrous Oxide | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
5e6fe6c5-2617-521e-a224-b2c21a6a9ae9 | dropdown | Nitrous Oxide/Oxygen mixture | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
e3e10035-7869-5ef9-82e8-ad11bc62abda | dropdown | Medical, Surgical, and dental air. | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
4638f26a-99ee-5ee6-b732-40e35c1e1467 | dropdown | Synthetic Air | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
4e553c3f-9b8c-5f60-900a-3f2564c549e0 | dropdown | Vacuum | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
b3a26ae8-14dc-56cb-8ad9-f46fb840c7d7 | dropdown | Nitrogen Sheild Gas | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
49e4dc97-ad06-523d-b190-ff7e434d0b04 | dropdown | Helium/Oxygen Mixture - test 1 | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
acfa0052-12f0-53a8-9d9f-711036d59c79 | dropdown | Helium/Oxygen Mixture - test 2 | Paramagnetic Oxygen Analyser Reading, Thermal Conductivity/infra-red instrument reading, Carbon Dioxide detector tube indication if TC meter used, Vacuum Probe
d9988858-89d2-59f3-8fb5-352baeb934c4 | signoff | Signoff if required
81589a7c-c04a-57e9-9d09-b5bccce4ec20 | checklist | HTM 02 01 B15 |  | HTM 02 01 B15
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
ce2549cb-0775-5124-97aa-b1dd6d5c591d | note | This is to certify that medical gas systems have been tested in accordance with paragraphs 15.163–15.167 and the results are as follows (insert values for gases – tick for vacuum):
366daeb9-9217-5e34-879e-f186f34d9ced | checkpoint | Paramagnetic Oxygen Analyser Reading
ee3cdbdf-291b-5d62-bae6-c0a74cc6642c | textbox | Oxygen from liquid or cylinders.
ab99c44c-6efe-54b3-8de3-716cdfc11f8b | textbox | Oxygen from concentrator
ec1472cd-fa9c-5fef-868e-77b372ae109c | textbox | Nitrous Oxide
6fd84b50-ac62-53ee-a8c7-eb42fb73c5e4 | textbox | Nitrous Oxide/Oxygen mixture
c825e2d6-74f5-57ac-b749-201648672ccb | textbox | Medical, Surgical, and dental air.
fc788ab0-164b-5e6d-9486-4b0a9fa0a196 | textbox | Synthetic Air
3498d2ba-1951-56fc-8cfa-e6b363c75962 | textbox | Vacuum
7fb796f5-e386-50e9-aca2-8c6811045361 | textbox | Nitrogen Sheild Gas
4a761093-db45-5d1e-a6e1-a486b9a067cc | textbox | Helium/Oxygen Mixture - Test 1
2c349e4c-6f0b-5152-84fe-327d88bbaa67 | textbox | Helium/Oxygen Mixture - Test 2
3eb3e240-447b-5043-8716-d804e0690038 | checkpoint | Thermal Conductivity/infra-red instrument reading
c907a87c-7999-5c95-98b9-383639957034 | textbox | Nitrous Oxide
57effeec-a897-5179-beeb-e0d5544630ca | textbox | Nitrous Oxide/Oxygen mixture
dfe4388b-7e89-5ab4-8535-02ed7fc3a457 | textbox | Nitrogen Sheild Gas
595c8550-befc-5ac1-838b-095206e0de9e | checkpoint | Carbon Dioxide detector tube indication if TC meter used
ec909d7e-bbcb-545d-9924-78e7334bd20d | textbox | Nitrous Oxide/Oxygen mixture
a6a71e93-30d1-53c1-9a80-bfd78eb88f09 | checkpoint | Vacuum Probe
f9ecaa44-2a5a-59fe-903d-018a14d65685 | textbox | Vacuum
def621c4-6024-5d4e-94b1-26ec0f8cc620 | checklist | HTM 02-01 - B9a - Vacuum Plant |  | HTM 02-01 - B9a - Vacuum Plant
92b8af04-b1a3-5f3d-bd83-a900c869a541 | checkpoint | Attach form (Confirm drawings are verified)
bcef0f89-d37f-5f04-9b3b-5d2cc802508a | note | The following Sources of Supply have been tested in accordance with Paragraph 15.85 and as found to comply with the following specifications.
8d93b25f-7cfa-5ea9-8ece-100b2d75bccc | signoff | Signoff if required
826016fa-2138-57c7-bdc6-4452eefe7b3e | checklist | HTM 02-01 - B9A sources of supply - Duplex Pressure reducing panel |  | HTM 02-01 - B9A sources of supply - Duplex Pressure reducing panel
92b8af04-b1a3-5f3d-bd83-a900c869a541 | checkpoint | Attach form (Confirm drawings are verified)
f3f3904d-78e3-571e-94dc-e1b15304e8c9 | note | The following Sources of Supply have been tested in accordance with Paragraph 15.85 and as found to comply with the following specifications.
8d93b25f-7cfa-5ea9-8ece-100b2d75bccc | signoff | Signoff if required
7bf8b529-beb8-538a-8d06-73326b732fb4 | checklist | HTM 02-01 - B9A Sources of Supply - Medical Gases Manifold |  | HTM 02-01 - B9A Sources of Supply - Medical Gases Manifold
92b8af04-b1a3-5f3d-bd83-a900c869a541 | checkpoint | Attach form (Confirm drawings are verified)
7b8214fd-ee01-58c4-a501-6e00a82d1b56 | note | The following Sources of Supply have been tested in accordance with Paragraph 15.85 and as found to comply with the following specifications.
8d93b25f-7cfa-5ea9-8ece-100b2d75bccc | signoff | Signoff if required
0fb3cc93-8276-596e-928d-fea55d0dc674 | checklist | HTM 02-01 - B16a - AGSS |  | HTM 02-01 - B16a - AGSS
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
0ae87381-0e48-55d3-b368-c40acbd905fd | note | This is to certify that the following system has been tested in accordance with paragraphs 15.169-15.178 and the results are as follows:
e8c84160-a1a2-5285-9d55-c042243328c9 | textbox | System
3976c378-272d-53aa-b872-45652298508c | textbox | Pump Type
022a4934-7001-529d-a44c-09c465bec5a3 | textbox | Terminal Units Total
cca11ce2-803a-51f6-be98-e09301239ce9 | textbox | Terminal Units Active
c3f5b672-f9fe-5d3f-a103-4186169c1f80 | button | Remote Starts | Yes, No
f80960fa-20d3-5d48-a9e6-4d259db31b9c | button | Remote Starts tested for Start/Stop | Yes, No
98cbb50e-eff4-5e78-9dd8-929ab9612778 | button | Tested for fault Indications | Yes, No
1f5edfb9-b467-5332-891d-bf0cea0c96a1 | signoff | Signoff if required
e7c00c70-7805-5ffb-bbc4-d1d7f45038f9 | checkpoint | Terminal testing (AGSS)
112154f2-40d6-5a9c-8fa1-27aeb005680d | checkpoint | Static Pressure
a1b53db8-fb75-5ddc-b444-6ca877684252 | checkpoint | Normal Pressure Kpa
83d8681f-b27f-5b0d-a029-3373e0631710 | checkpoint | Flow rate Kpa
c04d79c9-e248-5714-9e87-32d0fe80a52d | signoff | Signoff if required
ad33f8ce-1817-5a65-ae37-97832ac85332 | checklist | HTM 02-01 - B16a - AGSS |  | HTM 02-01 - B16a - AGSS
71236b3d-40e1-5085-99a1-dbc8ba7ee5a4 | checkpoint | Pass when complete
528c86c5-c674-5f9c-9d42-9350c6a12c1c | note | This is to certify that the following system has been tested in accordance with paragraphs 15.169-15.178 and the results are as follows:
a7ba5860-a0b9-5ab3-bef5-041d50d522db | textbox | System
27fa61e1-e7d0-5654-b83f-b3313d3b5eab | textbox | Pump Type
f4460438-04c5-5ce4-a053-24d8db5ed2e7 | textbox | Terminal Units Total
27326751-7078-5c70-92f8-8305f8885f9d | textbox | Terminal Units Active
32754069-6a89-54f3-a3cc-dbe7d030e29a | button | Remote Starts | Yes, No
b28cd6aa-df38-5ba3-b738-0ebc42337b24 | button | Remote Starts tested for Start/Stop | Yes, No
ebc9654c-71cc-51e3-abcd-a8a08b4d6537 | button | Tested for fault Indications | Yes, No
d1e15f62-a297-553c-a9fb-51b162ec64c4 | signoff | Signoff if required
d70a55f4-1254-55da-ac4c-ef722486abed | checklist | HTM 02-01 - Functional Test of NIST connectors |  | HTM 02-01 - Functional Test of NIST connectors
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
8e8c07ad-32ce-522c-9327-3fa2e518cd12 | note | The following Functional tests NIST connectors has been tested in accordance with the contract specification and paragraphs 15.80–15.81
38ba8365-864a-5d23-a497-a50f57c4328a | textbox | System:
eac0025e-8d40-55b2-b850-5abd91b4bb3f | textbox | NIST Gas
b12a53ce-f839-5a63-9987-6f70620e8e23 | checkpoint | Gas specificity
e298545b-9cbb-543a-88fe-13c3211b15eb | button | Self sealing | Adequate, Inadequate
af7f103b-b94a-5501-a6ab-6a512ed7ce20 | signoff | Signoff if required
0af2ef1a-f542-585f-bc3e-bf3b062c192a | checklist | HTM 02-01 B7a Functional Test of Terminal Units |  | HTM 02-01 B7a Functional Test of Terminal Units
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
0996db50-50c2-51db-bd80-6caaf6624ea3 | note | The following Functional tests of Terminal Units has been tested in accordance with the contract specification and paragraphs 15.77–15.78
d0dbf3a5-e9e9-5848-94a5-24d63164af93 | textbox | System:
1f51f1de-563c-5c84-9216-7e6def27d769 | textbox | Specified Flow L/min
e8e505b5-d6d1-5b0e-a3b0-5999cff24220 | textbox | Specified Pressure Drop kPa
63463572-2af8-582e-9bcb-16401c0555b8 | checkpoint | Specified Flow Achieved
8dd1b641-ca9a-594b-a9cc-20d3f68a6f54 | checkpoint | Specified Pressure Drop Achieved
824e26e4-880b-59d0-b75c-379b5557bf77 | checkpoint | Mechanical Function
ae4ce16d-dceb-5a55-8f7e-7da8b404a69f | checkpoint | Gas Specificity
8a3537c2-c106-5d62-8ccb-85e73a9d4bff | signoff | Signoff if required
4c255ac3-558d-536f-b3f7-4b4f96e024da | checklist | HTM 02-01 B8 Design Flow Performance Test |  | HTM 02-01 B8 Design Flow Performance Test
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
f102e9ae-db59-506e-af1a-40ea01953d2d | note | The following Design Flow performance test has been tested in accordance with paragraphs 15.83–15.84
bcf02e58-aeba-5289-891e-616a1e2c9576 | textbox | System gas
1af94bca-d4d5-5e8f-a118-f849b02d198f | textbox | System Design Flow L/min
1b48ab0a-f016-5bc8-80d6-60cbead0955b | textbox | Total number of terminal units in system at test flow(s) of:
974e9130-a7fe-5ff6-83b4-ea4b099810c0 | checkpoint | Single Point Test Flows
86ec9929-c3c5-5403-9009-b5632e20aa45 | note | 40 L/min
72535864-29d6-596e-abc6-5fd7a0374476 | note | 80 L/min
589b4c4c-f099-5fc2-9e06-ea6b8cb48e7d | note | 100 L/mi
f92cbfc7-9536-5c9c-975c-e3ed9a7b77c7 | note | 275 L/min
34ef539b-9533-5946-ac23-b633baa43b89 | note | 350 L/mi
b25356eb-4719-5f03-83af-800940759d68 | textbox | Total Flow L/Min
bf829da3-a95a-5ed4-889f-a7c932c0575e | signoff | Signoff if required
c94f98a5-1291-5852-91a5-50dcfdf73885 | checklist | HTM 02-01 B9 Functional Tests of Supply Systems |  | HTM 02-01 B9 Functional Tests of Supply Systems
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
df544a99-96b6-5350-85bf-574055234a52 | note | This is to certify that the following sources of supply have been tested in accordance with paragraph 15.85 and the attached sheets and found to comply with the specification.
28c0ee9d-1f7c-562c-81b6-796cd17d5572 | textbox | Source of Supply
1f5edfb9-b467-5332-891d-bf0cea0c96a1 | signoff | Signoff if required
7ac8b952-1a17-5c3f-9c96-46b3d39d5a81 | checklist | HTM 02-01 B13 - Purging and Filling |  | HTM 02-01 B13 - Purging and Filling
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
dece2014-0175-5eec-ad80-6fbf03111adb | note | This is to certify that medical gas systems have been purged and filled with medical air/O2 free nitrogen/the working gases (delete as appropriate) in accordance with paragraphs 15.93–15.99 and/or 15.100–15.101 as follows:
1c894e1a-fb41-5eb4-a7c7-6fd98efdd30b | checkpoint | Action
756fd208-a04b-5cdc-937e-3c6f02384197 | dropdown | Action | O2, CO2, MA, SA, VAC, DCA, DVAC, CA, AGS
1d3da8eb-ee8e-5929-94b0-4ce3ad66028b | button | Special Connectors/cylinders removed from site | Yes, No
66070d4b-e151-5d59-a26d-cae07c468121 | button | Filling | Yes, No
e9517919-a294-56bc-aa60-9482197c30fe | button | Purging all terminal units | Yes, No
70e666d3-3853-5409-a61f-f322921430c8 | button | Venting | Yes, No
9788a807-bf2d-5e86-b7b3-a653ab675512 | button | Tick if particulate tests have been performed and specifications met | Yes, No
87c75d12-a820-5755-97ed-58a89e55f6bc | button | Tick if odour tests have been performed and specifications met | Yes, No
1b092f38-539b-58c6-b9c6-11576da33738 | signoff | Signoff if required
87bde179-81a7-584b-a2ea-d559202741c9 | checklist | HTM 02-01 B14 - Quality Specifications |  | HTM 02-01 B14 - Quality Specifications
92b8af04-b1a3-5f3d-bd83-a900c869a541 | checkpoint | Attach form (Confirm drawings are verified)
3835e1d6-d5d5-598b-8834-5562fb96d505 | note | Quality specifications for medical gas pipeline tests (working gases). This is to certify that medical gas systems have been tested in accordance with paragraphs 15.109–15.162 as follows:
8d93b25f-7cfa-5ea9-8ece-100b2d75bccc | signoff | Signoff if required
5b6f3234-62ec-51bd-a854-1949cfbd49c2 | checklist | HTM02 -01 B1 Carcus Test |  | HTM02 - 01 B1 Carcus Test
0ccb0251-c457-54ad-8955-ea29a15197fa | section | Carcus test
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
90924a08-45b3-5d3f-a307-561683883c27 | textbox | File number:
15944a73-43af-53b0-8988-346445c853d4 | note | The following Pipeline Carcass Systems has been tested in accordance with Paragraph 15.47-15.51 and was found to comply with the following specifications:
2a7d18df-8039-5596-be7e-52aab52499b0 | note | During a test period of 2 hours, the maximum pressure loss should be ≤ 0.2 kPa for 400 kPa systems, ≤0.5kPa for 700 kPa systems, ≤ 0.2 kPa for vacuum & AGSS (plastic or copper).
eea6b9d2-5f73-5603-b8e5-35e7079bdb8f | note | Systems should be tested at a working pressure of;
022de1c2-49b5-50ad-adc3-571a74153407 | note | For compressed medical gas systems - 10.0 bar (1,000 kPa);
2205baec-d649-507c-bbde-fbfc05394bc6 | note | For medical compressed air systems for surgical use - 18.0 bar (1,800 kPa);
bcbe2933-d8c6-5e0b-9512-634ef16a6178 | note | For vacuum & AGSS systems constructed in copper 5.0 bar (500 kPa);
b1be53b9-b83d-59a0-b0f0-45de85dfb3a9 | note | For vacuum & AGSS systems constructed in plastic 1 bar (100 kPa).
b182bff2-80ef-54ee-8a6d-65283709ad0e | checkpoint | Gas Tested (Pass or Fail at end of test)
fe9b69c1-320e-5429-92de-c949913d4255 | textbox | Test Pressure (kPa)
77b226fc-6279-5916-b277-5ecd1ad9a4e9 | textbox | End Pressure (kPa)
3fd1ee19-858a-596a-9c49-ea5bad89ecd7 | textbox | Pressure Change (kPa)
2abfdf95-c839-543b-afc3-5cd3dd8ac748 | textbox | Time started
9f614df7-b21f-5aa4-b247-6dc415f2a687 | textbox | Time ended
6df24dc8-de6f-587c-b3a8-b1dc944fb595 | textbox | Final temp
58118ab2-85ae-535b-a9e4-9dcec812c38c | checkpoint | Were any links made - make a note in the comments
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
0d37c673-6eb7-5acc-b128-5061fed06fed | section | Pipework 1st Fix QA Checks
29997670-6da3-551c-9143-6fc2f749b737 | checkpoint | Copper to AS/NZS 1571 Table B
e764dedd-2605-561b-acdf-0db8af96313d | checkpoint | Silfos 15%
a20dfc55-c782-5c1d-b152-7d58501cf971 | checkpoint | Support Hanging, Spacing & Seismic Restraints
22fbf3f2-3499-533d-a5f5-f1cd5fff3712 | checkpoint | Inspection & Sectioning of Joints as Per HTM 13.36 – 13.38
868a5728-94e9-598d-b0cd-14722b5d137e | checkpoint | Fire Rating / Penetration
bf1b38bc-567e-513c-a5f0-c0997df97404 | checkpoint | Electrical Bonding & Earthing
fe8e6fce-800e-57e7-b15e-90092613dd5c | checkpoint | Labelling & Direction Arrows
b4978e45-9324-5e07-8fc4-7bcabf7fa219 | checkpoint | As-Builts Marked Up
844f27e7-3adc-418d-bcf1-d3dddcccf0ec | checkpoint | Photos taken
c7e81991-ea2d-502d-ac9f-0f9b08041ae0 | signoff | Signoff by Main Contractor or Engineer, if required
897e935b-3f39-534f-aa63-15b26b1f468a | checklist | HTM02-01 B2 Contractors Cross Connection |  | HTM02-01 B2 Contractors Cross Connection
32677eee-dc25-5b82-8605-d4f230728d71 | checkpoint | B2 Leakage Test Complete
45ec97f8-76e2-528e-93df-755a535f27b0 | textbox | Test by
45cc2a08-1c43-5d5a-a5bc-fc7bcee3e78c | textbox | Test date
a55e1eb2-cd66-5afe-82ba-58afc43987f7 | textbox | Revision
321fe3aa-9fec-5cc8-b442-5b412b710a3e | checkpoint | This is to certify that a Cross-Connection test in accordance with HTM 02-01, paragraphs 15.52–15.55
7f6f775d-2a66-579d-b6ee-d8ec60512194 | tickbox | Cross Connections between these systems were found If yes, detail findings above
87774d50-17ff-5c9d-8499-2dea4e4e6f9a | textbox | Status
bfb31c8c-8fd4-52ed-bb7f-0d5f23f99ee1 | checkpoint | Sign Off Complete
9542c3ad-4cea-59e4-982b-c6456386c81a | checkpoint | Signed off By Witness
695db8f0-7ce6-51dc-b913-7a803a3b82dd | textbox | Witness Name
d5278973-939b-5dc4-bcdc-5253ce649b52 | checkpoint | Signed off by Consultant
870a3361-718b-5095-a054-371ff0cd62e8 | textbox | Consultant Name
3ea573dc-fa6a-5b74-b126-30e829ff99e1 | checklist | HTM02-01 B3_4 Leakage Test |  | HTM02-01 B3_4 Leakage Test
7c89f8ed-688d-5ebd-b0b1-7072b71b714a | section | Leakage test
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
096b8eb3-e52a-5dc0-bdfc-ba9d5d92615a | textbox | File number:
625fdc4b-b427-5bea-9fd7-dad1e7e96f33 | note | During a test period of 2 hours, the maximum pressure loss should be ≤ 0.2 kPa for 400 kPa systems,
25998f97-a9c6-54a7-8180-e76ccd8b8715 | note | ≤0.5kPa for 700 kPa systems, 1 kPa after 1 hour for vacuum with source of supply isolated.
265dccc6-a769-5214-912a-b54ac342927f | note | Systems should be tested at a working pressure of;
ed67d623-3b26-519f-b44e-961138d83338 | note | For compressed medical gas systems - pipeline distribution pressure;
e258cfd5-284d-5084-92dc-9bd5d6ad028c | note | For medical compressed air systems for surgical use - pipeline distribution pressure;
377d483a-0441-5f4b-b2a9-6fe8d444321f | note | For vacuum systems - pipeline distribution pressure.
02755d53-61fb-5c5d-9d0a-fa3b309aae7b | checkpoint | A certified gauge was used
6fef5664-e5dc-51db-ba5c-ca891d629980 | textbox | Number
f820b66a-2e5f-5808-b22e-c707f3e7b7ca | textbox | Date last tested
b182bff2-80ef-54ee-8a6d-65283709ad0e | checkpoint | Gas Tested (Pass or Fail at end of test)
6c7f8b2d-4c27-5740-9b00-cdcc4f41c94a | textbox | Test Pressure (kPa)
90e09003-cfde-58db-9725-f11555a7b448 | textbox | End Pressure (kPa)
bba9436b-bf5a-580c-857d-18bc8f7168a9 | textbox | Pressure Change (kPa)
f40781e7-03c3-5dbc-8390-b33ea4895b5a | textbox | Time started
d025dd4b-af87-5cf3-86a9-218fe97f7289 | textbox | Time ended
2906fd63-c542-5d93-bc63-256514c98591 | textbox | Initial temp
3f8b43ad-1daf-51fa-b628-e3bfb91fa9c3 | textbox | Final temp
58118ab2-85ae-535b-a9e4-9dcec812c38c | checkpoint | Were any links made - make a note in the comments
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
e2d371ed-522c-56ff-acce-948eaa14a41d | section | Pipework 2nd Fix QA Checks
29997670-6da3-551c-9143-6fc2f749b737 | checkpoint | Copper to AS/NZS 1571 Table B
e764dedd-2605-561b-acdf-0db8af96313d | checkpoint | Silfos 15%
76e86b3c-6b5b-5345-99b7-41639e290332 | checkpoint | Terminal Outlets 2nd Fix Fitted
954a9028-26e7-58c4-b3e0-81247b5aec27 | checkpoint | Alarm Pressure Sensors Fitted
7d78cb2f-9aff-5a54-9e77-7f5c422176e5 | checkpoint | Flexible Hose Fitted
aede1b54-9183-507b-8666-164869ae3180 | checkpoint | Safety Valves Fitted
e6daa453-3282-55e9-bfda-cec7ff0c5457 | checkpoint | Pressure Gauges Fitted
93365303-7506-5882-850c-c7eb92778839 | checkpoint | Labelling of AVSU’s & LVA’s
b4978e45-9324-5e07-8fc4-7bcabf7fa219 | checkpoint | As-Builts Marked Up
399048d3-aa31-4783-8ae9-19af5ef54d4e | checkpoint | Photos taken
3b786cbf-a0e9-50e5-831a-4018a64dfce7 | signoff | Signoff by Main Contractor or Engineer, if required
458352f6-4a06-57b6-b6cc-4bdb1ccd48de | checklist | HTM02-01 B5a Area Valve Service Unit - Closure and Zoning test |  | HTM02-01 B5a Area Valve Service Unit - Closure and Zoning test
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
8e3b2c8b-6282-5d07-99a1-8809ff442db3 | note | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
952084f7-6dee-50bd-9659-59232b16ee54 | textbox | AVSU Number
4af329fb-99b9-55ea-a9b6-b2588acfd375 | textbox | Test Pressure (kPa)
bd267e30-7187-5342-bf6e-1a6d04f640cc | textbox | Downstream/Upstream pressure change after 15 min (kPa)
662d552f-d36a-5ce0-a66a-d250c59e93c1 | textbox | Terminal Units controlled (total no)
a56abc2e-bed0-58e1-a3d0-54c663910385 | textbox | Terminal Unit Labelling
187ecfff-87cc-59e3-aa07-a303b75d3754 | checkpoint | Attach Photo of AVSU Pre-Line
c783be76-4e77-50be-9a51-fa20cf3a92ea | signoff | Signoff if required
473b4f14-98bd-5a66-82ab-15957276d037 | checklist | HTM02-01 B5b Line Valve Service Unit - Closure and Zoning test |  | HTM02-01 B5b Line Valve Service Unit - Closure and Zoning test
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
82d7d8c4-61f4-5d7e-96ac-b8131673a272 | note | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
c58f24e8-752b-5ed6-941d-1765e75c806d | textbox | LVA Number
f1a0e7cc-1c07-5f0c-89c1-0b6b9715af92 | textbox | Test Pressure (kPa)
8ea99915-532c-5322-94e5-c2af303a9968 | textbox | Downstream/Upstream pressure change after 15 min (kPa)
d20f7d74-6b25-571a-973b-fe03b312b5bd | textbox | Terminal Units controlled (total no)
3e92be45-ed23-537d-972c-cb8b3187c06e | textbox | Terminal Unit Labelling
7ddadc45-a665-5486-881d-dd10ff2e2b65 | checkpoint | Attach Photo of LVA Pre-Line
63273c4c-d105-5373-9fed-03aa6e45a451 | signoff | Signoff if required
3793cc6f-2f98-5d2d-877b-268246942094 | checklist | Humidifier Install Template |  | Humidifier Install Template
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
093dc87d-af2e-585b-a40f-7c2385abe2ba | checkpoint | Humidifier is correct for the system/building
5b1f87ee-46b1-51d6-9cfd-5e902a8f1422 | checkpoint | Check casing, fans, coils & duct for damage, report observations
259c46cf-ddb5-5b1a-9ae3-b19740e19f3b | checkpoint | Measure & mark location dimensions on site
2e3f5ba8-d14d-57f3-a530-2489ebb7355b | checkpoint | Is Humidifier installed level & plumb
11426ec1-04a7-590c-8171-5e3db96c3023 | checkpoint | Are seismic restraints installed
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
daa7bc5e-70d1-50c3-90ef-60db4c6884f3 | checklist | Installation Fusiotherm Pipework |  | Installation Fusiotherm Pipework
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
723d4f39-74f2-5546-be7e-6951b9ee759c | checkpoint | Measure & mark off circuit dimensions on site
89960329-3320-573c-8ef1-94f1b2712c2e | checkpoint | Carry out Fusiotherm checks to manufacturers recommendations
2f824016-359e-583f-99c7-308509f02e79 | checkpoint | Has pipe been installed to the drawing
04b9e33f-5278-5057-9332-291c8fc178c8 | checkpoint | Check pipe is installed to correct levels and falls
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
fba8d2f4-7c46-4053-8eba-55c96c907caf | checklist | Medical Gas Pipework Checklist |  | Medical Gas Pipework
a28f5b7f-0e54-4f4a-b2f3-4d2610e489f1 | section | Details
88810ef1-667d-410c-bf0c-3e7da6c22548 | checkpoint | Medical pipework installed
79b1583f-ad2d-42bf-98ca-41e3ee9bb368 | checkpoint | Medical pipework pressure testing completed and passed
f2910bf4-65ee-4fc7-b105-6a754cedc4c3 | checklist | Pipework Checklist |  | Pipework
38b074b0-9f45-4be4-8e0a-9920d776689e | section | Details
34fcdc96-1b3a-4544-9b30-a7ceae966be8 | checkpoint | Pipework insulated
d3897aeb-1268-4fac-95f4-c05b5aca1880 | checkpoint | Labelling completed
7ef6e5fc-624c-461e-9a29-42d5a98f74e7 | checklist | Pipework Pressure Testing |  | Pipework Pressure Testing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e11acb10-3b9e-489d-a33c-1ff486511a05 | checkpoint | Test results attached
19a0a826-b017-58db-bdb7-684f7fd3532c | checklist | Pre Pour Checklist |  | Pre Pour Checklist
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0bc49903-1835-503e-a5a4-0b98643c6474 | checkpoint | Is the drawing approved for construction and latest version
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
8fdb48c4-5ea8-5eba-b115-58f4601dba26 | checkpoint | Check all sleeves are in position
c13e26ac-fe19-534a-9024-61261544398a | checkpoint | Check all penetrations are marked out correctly on site
c636e444-efcc-56d0-bc42-f8a44349e387 | checkpoint | Photos taken of all penetration sites
cb3d9865-13ea-5e3a-80bf-ba174ce0f60c | checkpoint | Information passed to main contractor
93c04eb1-2f27-5bd9-b020-19846a980b5c | section | DBC Building Services Signoff
5d3077ae-da33-4077-b94b-250502cc03ae | checkpoint | DBC Building Services Signoff
366ccc4a-b894-50f5-94f8-cfbff49e6e9d | textbox | Completed By
591e378c-e51b-5879-97b6-fc51772fb366 | textbox | Approved
b7860b11-8fe7-559b-8cc0-20fc4734f12d | date | Date
3970c54b-0e2b-59b6-b11c-5d91b4135c9a | signoff | Signed
135232f9-3e65-5f6c-8f3f-a310163d5dfe | section | Main Contractor Signoff
cdfb4a94-165c-4625-8013-2fd549e756ab | checkpoint | Main Contractor Signoff
698c6165-b9c0-52ef-a188-29a3a817f2b5 | date | Date
e57fef1a-69a6-5430-af70-1f12f986b04c | signoff | Signed
57c972a2-7df4-54dc-9c9e-af9d4c291ec1 | section | Consultant Signoff
f5268e3d-d9bd-4aaf-8a66-a29771ddec88 | checkpoint | Consultant Signoff
188328ca-0491-5267-9aee-42209dec18a5 | date | Date
598f1a7a-1d47-5480-9da6-a9baa7defe71 | signoff | Signed
39410079-f435-4e41-8e59-1a73535593ab | checklist | Prelining |  | Prelining
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
31341237-d0a2-4ae6-b856-5632b3fb4be3 | checkpoint | Flushboxes or fixings in place
6767d7dc-cd13-52dc-9b37-8e6f29ee0186 | note | Correct location
9f3730be-087a-4800-b057-8fa02311aa0f | checkpoint | Cables installed correctly
130a4855-6460-59de-87ae-20e9f8f989cf | tickbox | Correct cable (or a draw wire for future)
a062fcc3-f271-5683-a9f9-ea66c4fcfd68 | tickbox | Correct support
dba0ffdb-47f8-552c-8263-411053b4bd77 | tickbox | Correct segregation
8dc67f21-dfec-5c7e-b3cb-1a2a2a554c9d | tickbox | Correct protection - if required
31077dab-c715-4614-8b7d-79889ae0f96b | checkpoint | Labelling
52ad47b3-166e-5997-9844-9605fd78bc26 | checklist | Pump Install QA |  | Pump Install QA
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
b74b34bb-337e-5593-85a3-ab91dc4aa89b | checkpoint | Is site safe for work start, report discrepancies
2343b5c8-b8a0-51e8-8fcf-4d369018b36a | checkpoint | Confirm the correct pump model is installed and labelled
ff86b113-d3e0-59c8-bb5c-6ce23a3e653a | checkpoint | Is the Pump installed the correct way around (arrow)
e3f46c06-a1e1-5870-af5c-8df412008069 | checkpoint | Has the Pump be mounted correct and fixed down
2c3f5509-ef4f-5697-a7de-92df5c5553e2 | checkpoint | Is the pump accessible and have free area around it
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
74afcc31-aec5-5119-a854-ebcde5ed3fa8 | checklist | PVC Pipework Install |  | PVC Pipework Install
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
e5cd8a17-923a-52b5-9347-8bc4a2fff3e3 | checkpoint | Measure & mark off dimensions on site
6fc7f4e5-eb60-51c1-9910-163c9d52e66c | checkpoint | Brackets installed and spaced correctly
4d28d451-084f-562b-8903-0b8e765af35c | checkpoint | Has pipe work been installed to the drawing
b6c74d61-0294-500f-9035-7877d963ee62 | checkpoint | Check pipe work is installed to correct levels and falls
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
ea360d85-3494-593c-8e6e-86c68691e6c2 | checklist | PVC Pipework Underground |  | PVC Pipework Underground
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
723d4f39-74f2-5546-be7e-6951b9ee759c | checkpoint | Measure & mark off circuit dimensions on site
1ab85254-cc57-555a-b702-9060d159caba | checkpoint | Has underground PVC mains pipe work been joined in accordance with the specification
4d28d451-084f-562b-8903-0b8e765af35c | checkpoint | Has pipe work been installed to the drawing
b6c74d61-0294-500f-9035-7877d963ee62 | checkpoint | Check pipe work is installed to correct levels and falls
76a2ffad-d76f-51e1-a5f1-089a821de7f7 | checkpoint | Pressure Test Pipe.
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
92df5ea3-33f8-44cf-a18e-423fb45dea86 | checklist | QA - Ductwork |  | QA - Ductwork
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f286cadd-ec6c-4765-bc17-785ccc93bce0 | checkpoint | Ductwork pressure testing passed
89f56003-4e2b-5756-90cd-2b326ffc4f13 | checklist | Radiant Heater Template |  | Radiant Heater Template
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
c7922c60-2e41-56c9-88e3-20f7a5be31bd | checkpoint | Radiant Heater is correct for the system and position shown on drawings
adb54595-c4b8-5380-9c19-31e22aae3bda | checkpoint | Is Radiant Heater installed level & plumb
5f6f1f94-d3eb-5f84-9a13-1cb171c1501f | checkpoint | Are supports and fixings installed adequately
29dbfe95-561b-5a38-928e-419f4551b91a | checkpoint | Verify & record on drawing As-Built dimensions (if differ or required)
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
a6d2d098-50b7-5f24-afbd-1c93661c5ad1 | checklist | Seismic Bracketing |  | Seismic Bracketing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8ff6a11c-8bb2-5f3b-9fe0-6410069c2a7a | checkpoint | Location of Bracket checked on shop drawings
7718ac3e-0799-5a8f-91c7-d2fe39e508aa | checkpoint | Correct bracket type selected
1b8ea6ba-5d81-5225-9292-6d642ef4eb5e | checkpoint | Correct Anchor selected and checked
5f6b53b6-292c-596c-a224-e3d5d0a8d986 | checkpoint | Anchor Hole Size and Depth checked
0e72331c-e2d4-5302-ac9b-22a3c533057e | checkpoint | Correct torque set for anchor
66ec0be7-114b-56f8-b9f0-73d9d38ae9e1 | checkpoint | Final Photo of bracket
94df928e-9c94-51e7-a20c-3acf0e308e91 | checklist | Smoke Damper QA Checklist |  | Smoke Damper QA Checklist
c7ccb539-3d2b-565b-872c-2e399600c3c9 | checkpoint | Is the location drawing approved for construction
ac0b292f-acdb-5fee-bfb9-05fc909e9968 | checkpoint | Installation of duct completed as drawn
db6c5f0a-b0b4-57e6-b237-1984563e02d0 | checkpoint | Is the Smoke damper motor shaft accessible
9ebab58a-deb3-53c4-9d92-60f939f15c5d | checkpoint | Smoke dampers open & close manually (mark duct)
d5e1f3d1-b34d-51d6-b982-2ae2e1d1fc93 | checkpoint | Smoke damper labelled
484e0585-569a-57ba-acaa-547731a10b02 | checkpoint | Photos Taken
8db8cc0f-8bd6-5fbc-b51c-e76d2a38b6e1 | signoff | Signoff by Main Contractor or Engineer, if required
667ad78c-bf76-5b18-8601-7227658a5b12/2 | checklist | Steel Duct Install |  | Steel Duct Install QA with Grille
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
08eeabf2-12c0-593c-9923-a37907b88956 | checkpoint | Duct delivered is correct for the system/building
c5c04667-87e8-52ef-b99d-efa79a863800 | checkpoint | Measure & mark off duct run dimensions on site
0196ab38-4847-56af-940d-dd32e405d718 | checkpoint | Install duct
0c1156a6-8911-5346-b572-9dbe84f19cb8 | checkpoint | Has duct been installed to the drawing
6434ad23-791e-571a-a8dd-76d116bbeb5d | checkpoint | Has duct been installed to correct levels & falls
d9c351f9-af9c-5a3e-a277-5415e40c0104 | checkpoint | Is rigid duct supported at appropriate centres
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
c307339e-cb8b-530b-b1e4-8aa79adead95 | checklist | Steel Duct Install QA |  | Steel Duct Install QA
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
08eeabf2-12c0-593c-9923-a37907b88956 | checkpoint | Duct delivered is correct for the system/building
c5c04667-87e8-52ef-b99d-efa79a863800 | checkpoint | Measure & mark off duct run dimensions on site
0196ab38-4847-56af-940d-dd32e405d718 | checkpoint | Install duct
0c1156a6-8911-5346-b572-9dbe84f19cb8 | checkpoint | Has duct been installed to the drawing
6434ad23-791e-571a-a8dd-76d116bbeb5d | checkpoint | Has duct been installed to correct levels & falls
d9c351f9-af9c-5a3e-a277-5415e40c0104 | checkpoint | Is rigid duct supported at appropriate centres
6fa861be-62e1-5980-b748-f2b625de39db | checkpoint | Is flexible duct supported at appropriate centres
77e0c941-f467-5ed1-bec5-6d961289d04e | checkpoint | Verify & record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
8f3b268a-b264-4f6e-93a9-0d7aa33c0d39 | checklist | Steel Duct Install QA with Grille - 2nd fix |  | Steel Duct Install QA with Grille - 2nd fix
1510e383-db87-4e59-8f0d-68b6de4ffc70 | section | Details
6fa861be-62e1-5980-b748-f2b625de39db | checkpoint | Is flexible duct supported at appropriate centres
7c53effa-a56f-538c-9580-3d4efff51e0f | checkpoint | Grille box installed to drawing
f88e2a41-56e7-5cf4-b1ff-613fb89e5eb8 | checkpoint | Grille box level and connected to ducting
30a823c5-633d-5d81-8919-c41b19a3abf3/2 | checklist | Steel Pipe QA Checklist |  | Steel Pipe QA
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1051d027-92f4-532a-833e-f0cdf9842b3f | checkpoint | Is the drawing approved for construction
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
723d4f39-74f2-5546-be7e-6951b9ee759c | checkpoint | Measure & mark off circuit dimensions on site
be55c655-333c-537f-a766-cc23da6ccc06 | checkpoint | Has steel pipe been tested as per Specification (photographs of test valves been recorded?)
2f824016-359e-583f-99c7-308509f02e79 | checkpoint | Has pipe been installed to the drawing
5f3eed23-fb35-5960-b913-30ebd340b093 | checkpoint | Verify and record on drawing As-Built dimensions
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
4af6e23d-c3c3-552a-b347-35353015b516 | checklist | SYS - HTM 02-01 B13 - Purging and Filling |  | HTM 02-01 B13 - Purging and Filling
8561923d-89d5-5fd4-a3ee-8523d8a9440b | checkpoint | Confirm drawings are verified
c3cd8a23-4aaf-5179-9b87-6e11a1ecbe64 | note | This is to certify that medical gas systems have been purged and filled with medical air/O2 free nitrogen/the working gases (delete as appropriate) in accordance with paragraphs 15.93–15.99 and/or 15.100–15.101 as follows:
1c894e1a-fb41-5eb4-a7c7-6fd98efdd30b | checkpoint | Action
dacc5e52-e21b-572c-bb15-bac4f39c2c9c | dropdown | Action | O2, CO2, MA, SA, VAC, DCA, DVAC, CA, AGS
fe0f3f21-b130-5521-937a-017d169f8eb2 | button | Special Connectors/cylinders removed from site | Yes, No
a5caf0c7-8b33-56eb-ad09-b428d6d98d63 | button | Filling | Yes, No
52555208-8ee2-5cd3-9107-c256451c779d | button | Purging all terminal units | Yes, No
839691a0-bcee-59a8-b76f-94f7f76ae3cd | button | Venting | Yes, No
26759293-164c-5497-ace0-7504fd3ad27c | button | Tick if particulate tests have been performed and specifications met | Yes, No
b27e8041-87c0-5fca-9dce-2d5e3624621d | button | Tick if odour tests have been performed and specifications met | Yes, No
1b092f38-539b-58c6-b9c6-11576da33738 | signoff | Signoff if required
a1068ec8-90b0-529c-a7b8-cf7d8e60e5e0 | checklist | SYS - HTM 02-01 B14 - Quality Specifications |  | HTM 02-01 B14 - Quality Specifications
92b8af04-b1a3-5f3d-bd83-a900c869a541 | checkpoint | Attach form (Confirm drawings are verified)
204b74c9-81da-5bf3-ad5a-efbe7fc71d84 | note | Quality specifications for medical gas pipeline tests (working gases). This is to certify that medical gas systems have been tested in accordance with paragraphs 15.109–15.162 as follows:
8d93b25f-7cfa-5ea9-8ece-100b2d75bccc | signoff | Signoff if required
2bcb9d1d-9bf6-5bf9-9b8b-f5d1511ab744 | checklist | SYS - HTM02 -01 B1 carcus test |  | HTM02 -01 B1 carcus test
0ccb0251-c457-54ad-8955-ea29a15197fa | section | Carcus test
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint-no-value | Details
c08de09a-228a-5e6c-a135-2652854b308c | textbox | File number:
4afff069-032a-5b64-aa93-a04bca8aae62 | note | The following Pipeline Carcass Systems has been tested in accordance with Paragraph 15.47-15.51 and was found to comply with the following specifications:
21055f79-c815-57a6-9a84-7ea02ba68b47 | note | During a test period of 2 hours, the maximum pressure loss should be ≤ 0.2 kPa for 400 kPa systems, ≤0.5kPa for 700 kPa systems, ≤ 0.2 kPa for vacuum & AGSS (plastic or copper).
967bb2fc-0ac7-563c-b89f-65631fac4c9c | note | Systems should be tested at a working pressure of;
97241116-6f55-5cf0-a577-03e59a2ad35c | note | For compressed medical gas systems - 10.0 bar (1,000 kPa);
a629dcf9-3dfd-5b63-83aa-916826182d83 | note | For medical compressed air systems for surgical use - 18.0 bar (1,800 kPa);
ae82ea43-e235-5b9d-843e-e7ce6adef9fc | note | For vacuum & AGSS systems constructed in copper 5.0 bar (500 kPa);
6083d95a-98d5-5f70-8c6b-790d21754e3c | note | For vacuum & AGSS systems constructed in plastic 1 bar (100 kPa).
b182bff2-80ef-54ee-8a6d-65283709ad0e | checkpoint | Gas Tested (Pass or Fail at end of test)
6cde75d2-8b32-5fe3-badd-7e1d3c6c0b0a | textbox | Test Pressure (kPa)
1f06acc8-e9c1-5037-a024-864706393c26 | textbox | End Pressure (kPa)
c9e1f142-cd19-53da-adbb-ab355004b578 | textbox | Pressure Change (kPa)
bbe5c8cf-5e08-5822-9a5c-467befa4226a | textbox | Time started
5828e4b2-3867-5c56-9a9c-b5b1bce21914 | textbox | Time ended
fa239a99-e942-5eb2-9143-05effabe6c32 | textbox | Final temp
58118ab2-85ae-535b-a9e4-9dcec812c38c | checkpoint | Were any links made - make a note in the comments
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
0d37c673-6eb7-5acc-b128-5061fed06fed | section | Pipework 1st Fix QA Checks
29997670-6da3-551c-9143-6fc2f749b737 | checkpoint | Copper to AS/NZS 1571 Table B
e764dedd-2605-561b-acdf-0db8af96313d | checkpoint | Silfos 15%
a20dfc55-c782-5c1d-b152-7d58501cf971 | checkpoint | Support Hanging, Spacing & Seismic Restraints
22fbf3f2-3499-533d-a5f5-f1cd5fff3712 | checkpoint | Inspection & Sectioning of Joints as Per HTM 13.36 – 13.38
868a5728-94e9-598d-b0cd-14722b5d137e | checkpoint | Fire Rating / Penetration
bf1b38bc-567e-513c-a5f0-c0997df97404 | checkpoint | Electrical Bonding & Earthing
fe8e6fce-800e-57e7-b15e-90092613dd5c | checkpoint | Labelling & Direction Arrows
b4978e45-9324-5e07-8fc4-7bcabf7fa219 | checkpoint | As-Builts Marked Up
ef029a75-4692-43b9-a0cd-433e832e4415 | checkpoint | Photos taken
c4044cfc-93e9-5d8b-bcbe-fad02e3faca0 | signoff | Signoff by Main Contractor or Engineer, if required
9bf174f3-a7cb-5241-971c-8e34d59ccb8a | checklist | SYS - HTM02-01 B3_4 Leakage Test |  | HTM02-01 B3_4 Leakage Test
7c89f8ed-688d-5ebd-b0b1-7072b71b714a | section | Leakage test
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint | Details
c01b47f0-a567-55d6-a6e7-8d0bfe3779ae | textbox | File number:
9bd1bbd9-6456-5795-90fd-e6f43bad9c9b | note | During a test period of 2 hours, the maximum pressure loss should be ≤ 0.2 kPa for 400 kPa systems,
415d1519-c4e7-58ef-b957-6af84c7f9e56 | note | ≤0.5kPa for 700 kPa systems, 1 kPa after 1 hour for vacuum with source of supply isolated.
3f82271a-e585-58d7-90e5-80669a941155 | note | Systems should be tested at a working pressure of;
cc1cc973-ba34-59fc-a954-c083db3fbc19 | note | For compressed medical gas systems - pipeline distribution pressure;
ff035d39-d2c8-5fe3-a46a-a8ec0e391b4a | note | For medical compressed air systems for surgical use - pipeline distribution pressure;
2285200e-4d6e-54bb-81ac-10da2d6fcdce | note | For vacuum systems - pipeline distribution pressure.
02755d53-61fb-5c5d-9d0a-fa3b309aae7b | checkpoint | A certified gauge was used
9cc7ca05-02d3-5b3c-beeb-5aa783b62d8a | textbox | Number
102f1beb-62bd-5780-a82a-24de7b7ec3f1 | textbox | Date last tested
b182bff2-80ef-54ee-8a6d-65283709ad0e | checkpoint | Gas Tested (Pass or Fail at end of test)
b6f205f6-631d-515f-81ae-a01a1197efd9 | textbox | Test Pressure (kPa)
261b84d7-1d57-53f6-8252-2c74fe64326b | textbox | End Pressure (kPa)
d9a8a367-5215-5bfd-b651-a2488d1a3d0f | textbox | Pressure Change (kPa)
533c1a44-6d88-5e36-adfa-5f94a0ade340 | textbox | Time started
805c47bb-c95d-52c7-8e36-8e7d0b463253 | textbox | Time ended
c196e0cf-2600-5485-953b-22ed0ec54a27 | textbox | Initial temp
32964ae7-7956-5624-8508-5d5b17b51801 | textbox | Final temp
58118ab2-85ae-535b-a9e4-9dcec812c38c | checkpoint | Were any links made - make a note in the comments
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required
e2d371ed-522c-56ff-acce-948eaa14a41d | section | Pipework 2nd Fix QA Checks
29997670-6da3-551c-9143-6fc2f749b737 | checkpoint | Copper to AS/NZS 1571 Table B
e764dedd-2605-561b-acdf-0db8af96313d | checkpoint | Silfos 15%
76e86b3c-6b5b-5345-99b7-41639e290332 | checkpoint | Terminal Outlets 2nd Fix Fitted
954a9028-26e7-58c4-b3e0-81247b5aec27 | checkpoint | Alarm Pressure Sensors Fitted
7d78cb2f-9aff-5a54-9e77-7f5c422176e5 | checkpoint | Flexible Hose Fitted
aede1b54-9183-507b-8666-164869ae3180 | checkpoint | Safety Valves Fitted
e6daa453-3282-55e9-bfda-cec7ff0c5457 | checkpoint | Pressure Gauges Fitted
8edd0d6f-32d9-531c-a9a0-992cebd30fa9 | checkpoint | Labelling of AVSU’s &amp; LVA’s
b4978e45-9324-5e07-8fc4-7bcabf7fa219 | checkpoint | As-Builts Marked Up
403b116e-0ccc-46ac-806d-a0cdb8fa19a5 | checkpoint | Photos taken
473eea6d-e6a2-500c-b952-e0a38b36f27e | signoff | Signoff by Main Contractor or Engineer, if required
778c85c4-fd68-5432-b2fa-b36ec233c22c | checklist | SYS - Pre Pour Checklist level 2 |  | Pre Pour Checklist level 2
0bc49903-1835-503e-a5a4-0b98643c6474 | checkpoint | Is the drawing approved for construction and latest version
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
8fdb48c4-5ea8-5eba-b115-58f4601dba26 | checkpoint | Check all sleeves are in position
c13e26ac-fe19-534a-9024-61261544398a | checkpoint | Check all penetrations are marked out correctly on site
c636e444-efcc-56d0-bc42-f8a44349e387 | checkpoint | Photos taken of all penetration sites
cb3d9865-13ea-5e3a-80bf-ba174ce0f60c | checkpoint | Information passed to main contractor
9e262333-3d61-50b2-bc7b-f70b7c4f795c | signoff | Signoff by Main Contractor or Engineer, if required
baf71804-cb4d-569c-8ebc-f85f32d5d9d1 | checklist | SYS - Pre Pour Checklist level 4 |  | Pre Pour Checklist level 4
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
0bc49903-1835-503e-a5a4-0b98643c6474 | checkpoint | Is the drawing approved for construction and latest version
ea81b164-32e4-5f3c-8dde-770da1bd5a28 | checkpoint | Is site safe for work start
8fdb48c4-5ea8-5eba-b115-58f4601dba26 | checkpoint | Check all sleeves are in position
c13e26ac-fe19-534a-9024-61261544398a | checkpoint | Check all penetrations are marked out correctly on site
c636e444-efcc-56d0-bc42-f8a44349e387 | checkpoint | Photos taken of all penetration sites
cb3d9865-13ea-5e3a-80bf-ba174ce0f60c | checkpoint | Information passed to main contractor
93c04eb1-2f27-5bd9-b020-19846a980b5c | section | DBC Building Services Signoff
b7f845f3-9865-4de9-9e80-10a17b013445 | checkpoint-no-value | DBC Building Services Signoff
fd51d479-0976-59d0-988e-7919ad794ddf | textbox | Completed By
5a526067-1c68-5294-ac83-c39ec48f580b | textbox | Approved
225d924f-5b35-5631-b7c2-9273c052facf | date | Date
24430d8a-a1e5-5d4b-b8a6-eef4bdc218fa | signoff | Signed
135232f9-3e65-5f6c-8f3f-a310163d5dfe | section | Main Contractor Signoff
6c8cfe08-edf0-413b-81d5-67fa4e00299c | checkpoint-no-value | Main Contractor Signoff
ba1ce88a-25a7-5e0a-968a-1331d06576d8 | date | Date
51b5524d-a378-5dd8-a899-301f0dd2583d | signoff | Signed
57c972a2-7df4-54dc-9c9e-af9d4c291ec1 | section | Consultant Signoff
f71b2af7-0d9b-4f48-bd9c-65abea46e08f | checkpoint-no-value | Consultant Signoff
c1723c3d-7713-53a6-86aa-0b021371f022 | date | Date
345397b8-927a-5708-83d2-18159dda8fbe | signoff | Signed
63f9d15a-5aca-54c8-9aae-9ad2940e560e | checklist | VAV QA Checklist |  | VAV QA Checklist
9e5832be-83bd-514a-b501-b2957899ad7b | checkpoint | Is the VAV Box model correct and labelled (correct size?)
ca4af1f4-fdcb-5807-ba8d-053d77dbd92a | checkpoint | Is the VAV box installed the correct way around
35769d52-3b4b-518a-b29b-518404b126f9 | checkpoint | Has it been mounted and seismically supported correct
7e54183f-31a3-51f6-8172-f47f78dd5bc0 | checkpoint | Is the controller and Valves (water) accessible from below
d50521f3-1b8a-5fca-9e18-9f40eda9f98c | checkpoint | Photos taken
929e4df1-5584-5893-b2fb-a6e86590e5fe | signoff | Signoff by Main Contractor or Engineer, if required