## ITP RMU2 Drainage
RMU2 DRAINAGE ITP
Location
| Drainage Location | Location of Installed drainage | Textbox
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
Holdpoint United Civil
| Site Preparation | Visual inspection of cleared and levelled area | P,F,Attachment
Site free from debris, vegetation, and unevenness
| Survey and Marking | Verification of layout and drain alignment & grades | P,F,Attachment
Alignment with approved IFC drawings
Local site datum found, marked & protected
Wastewater Construction & Installation
| Material Approval | Review and approval of pipes, culverts, and other materials to comply with IFC drawings and specifications
Wastewater pipework shall be DN100 PN12 PVC-U, all fittings shall be rated & compatible with the pipe
Wastewater tank shall be a Promax Enduro 5000L Septic Tank
|  | Material test certificates and or delivery dockets attached | Holdpoint United Civil & CHINT, P,F,Attachment
| Excavation | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework to comply with IFC Drawings
|  | Depth, dimensions, and cleanliness checked and maintained | P,F,Attachment
| Soil Stability | Inspection of trench stability and shoring/battering/benching is installed where necessary | P,F,Attachment
Stable and safe for pipe and tank laying
| Pipe Installation | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
Pipes to have 75mm of Gap7 bedding and top cover
|  | Wastewater pipe grade installed to | textbox
|  | ITC Completed for pipe installation | Holdpoint United Civil, P,F,Attachment
| Tank Installation | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
Tank to sit on 100mm of compacted gap20 then be backfilled with Pap7 to the pavement layers
|  | Tank half filled with water before backfilling | Holdpoint United Civil, P,F,Attachment
| Backfilling | Visual inspection of backfill material and compaction
Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
|  | ITC Completed for Compaction Testing | Holdpoint United Civil, P,F,Attachment
| Hydrostatic Test | Visual Inspection of hydrostatic leak test being performed
Hydrostatic pressure testing of pipes for leakage As per NZS4404 Appendix C
Leakage/make up water does not exceed 0.5L / Hr per metre length per metre diameter (0.5 * 5.5 * 0.1 = 0.275 L / Hr)
|  | Hydrostatic test holds and passes | Holdpoint United Civil & CHINT, P,F,Attachment
Subsoil Pipe Construction & Installation
| Material Approval | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings
Subsoil pipe shall be 110mm dia Novaflo subsoil drainage pipe with geotextile sock surrounding
|  | Material Test Certificates / Delivery Dockets attached | Holdpoint United Civil & CHINT, P,F,Attachment
| Excavation | Visual inspection and measurement of trench to comply with IFC Drawings
|  | Depth, dimensions, and cleanliness checked and maintained | P,F,Attachment
| Soil Stability | Inspection of trench stability and shoring/battering/benching is installed where necessary
|  | Stable and safe for pipe and tank laying | P,F,Attachment
| Pipe Placement | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
|  | Subsoil pipe to have a 1% grade to outlet | Holdpoint United Civil, P,F,Attachment
Stormwater Construction & Installation
| Material Approval | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings and Specifications
Pipework shall be DN90 SN4 PVC-U, all fittings shall be rated & compatible with the pipe
Stormwater Channel to be lined with Bidim A19 Filter Cloth
150x50 H4 Radiata Timber edging for the water tank surround
|  | Material test certificates and or delivery dockets attached | Holdpoint United Civil & CHINT, P,F,Attachment
| Excavation | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework
|  | Depth, dimensions, and cleanliness checked and maintained to comply with IFC Drawings | P,F,Attachment
| Soil Stability | Inspection of trench stability and shoring/battering/benching is installed where necessary
|  | Stable and safe for pipe and tank laying | P,F,Attachment
| Pipe Installation | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
Pipes to have 75mm of Gap7 bedding and top cover
|  | ITC Completed for Pipe Installation | Holdpoint United Civil, P,F,Attachment
| Tank Installation | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
Tank to sit on 150mm of compacted Gap40 and 100mm of compacted sand
|  | Compliance with approved IFC Drawings | Holdpoint United Civil, P,F,Attachment
Backfilling
Visual inspection of backfill material and compaction
Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
|  | ITC Completed for Compaction Testing | Holdpoint United Civil, P,F,Attachment
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive inspection of all elements relating to the RMU Drainage
Compliance with IFC drawings and specifications
|  | Verify all Drainage meets design and functional requirements | Holdpoint United Civil & CHINT, P,F,Attachment
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the RMU Drainage | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | Holdpoint United Civil & CHINT, P,F,Attachment
Complete and approved by client