## Master List Templates
Id | Type | Name | Values | Prompting Name
65334946-7ad1-40ae-94fa-2e6946071ac2 | checklist | Upload Attachments |  | Upload Attachments
6da6f498-e18e-4121-84fe-5cd5ddfb8d03 | section | Details
abd1894c-f4ca-4bd7-adb7-c536eb29dab6 | checkpoint-no-value | Upload Attachments

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
fe1bd0d3-9527-4a5d-903e-c0b192398112 | checklist | ITP - Drainage | itp | ITP - Drainage
c26f1bd0-1930-4796-84bf-1e5b80063381 | section | Location
c82a7f58-4b81-4455-bfe2-d73266a2bf67 | checkpoint-no-value | Drainage Location
fea24dea-1f52-51c6-b7ec-c42a6302b2d7 | textbox | Location of Installed drainage line
e0d1f0bc-5944-5d71-af4e-ca62fa030591 | textbox | Project drainage line reference (if applicable)
300f4514-48ec-4f56-8aa8-ca5a9638616a | section | Preconstruction
8409e24a-8897-4e4c-aa23-5d9fee7357c4 | checkpoint | Design Drawings
02dcefa5-5ce8-59c9-9bcc-92d5b476a2e7 | note | Issued for Construction Drawings available
11f9f648-c18a-4b7a-bbc8-04666e575329 | signoff | United Civil Hold Point
cc299b21-a832-4ca8-81a9-533785981f31 | checkpoint | Site Preparation
4a09b00f-3974-5740-9868-799c03ce7ba4 | note | Visual inspection of cleared and levelled area
bbb985f2-a089-5731-8dd8-76a07c5869e9 | note | Site free from debris, vegetation, and unevenness
1e081ace-a08f-4510-878a-98f7b95f4087 | checkpoint | Survey and Marking
87eccc8d-1ee4-5fc4-8f3d-f0803116521c | note | Verification of layout and drain alignment & grades
75f44d1e-8235-52f1-8d1a-a6481e7720d9 | note | Alignment with approved IFC drawings
9fb60223-f9e8-45e2-8434-e898d42a50dc | checkpoint | Material Approval
bb6ea80c-6f46-543a-8cb2-b114aed74139 | note | Review and approval of pipes, culverts, and other materials
10d975f8-03a5-586c-bd0f-065da03077d9 | note | Compliance with IFC drawings, specifications, KDC EES - S06 for accessways, and standards
66b310d0-d4e5-5632-a455-aba610ae7e66 | note | Material Test Certificates / Delivery Dockets attached
0329a0c5-e51e-4272-8d16-980e7e1d7b6a | signoff | United Civil Hold Point
0cf24214-8126-4e31-bb6c-1625d561fee8 | section | Construction - Excavation
011178e6-14bd-459e-ac8a-c13d6a61f614 | checkpoint | Excavation
e8e5837e-1dcc-5783-98f3-0bb95be2f4da | note | Visual inspection and measurement
cab8a44e-73da-54b6-b719-6c6d236aa5a2 | note | Depth, dimensions, and cleanliness
47ac976f-43a5-5a31-bc69-a0b6aaac5a6a | note | Compliance with design drawings
06ce6ecb-4394-4cf7-8237-f6aa97de3ddc | checkpoint | Soil Stability
23d24620-9022-52f9-b963-23eeba51577a | note | Inspection of trench stability and shoring where necessary
a2f11b00-f1e3-51dc-815f-97f66dc37a97 | note | Stable and safe for pipe laying
2745c1dc-453e-405f-bdf4-feebee584f94 | section | Construction - Installation
c74fff2e-c134-4395-a9a3-37bd53d298c2 | checkpoint | Pipe Placement
433d4825-90dc-50b0-b4b7-fb0383962858 | note | Visual Inspection of pipe placement, alignment, and bedding
b315b5eb-2fdd-54ee-8db9-a99e13c2c297 | note | Compliance with approved IFC Drawings
ed25c9a1-2d62-4138-a50a-69c86da02522 | checkpoint | Joint Sealing
5c13a856-599d-5798-be1e-87fb2d0af99d | note | Inspection of joint sealing materials and application
e49f1c3f-dd95-5241-ae99-1a78d5a98eae | note | No leakage; proper sealing per specifications
be00973d-b7f1-46ed-933b-4d12e0b9f835 | checkpoint | Backfilling
82b95dd9-2b37-51bb-9d5e-1d5700d7a526 | note | Inspection of backfill material and compaction
589aea76-2d64-54aa-b2bf-cfa53fdbdbb9 | note | Proper compaction as per specification
301a1a98-2a3f-5d71-8e94-7a7acf6d0e10 | note | ITC for compaction
749f476e-b31a-4f3d-9394-6cd230c6a199 | signoff | United Civil Hold Point
a8c9bd8d-517c-4403-b682-9333cdfc110c | section | Construction - Testing
c9c69a5c-311f-4981-ab92-6a412772d647 | checkpoint | Hydrostatic Test
b06f66d4-c14a-5d31-bc1c-5c530dc761fc | note | Pressure testing of pipes for leakage
1d5dd7dd-089f-58b5-aa1c-f3f498dc1f94 | note | Meets pressure standards for type of line being tested
ab7a5ae2-a11a-58f8-8554-bc96792696db | note | Test Report Completed
09f77e55-c152-4460-aeae-73579dedf99a | signoff | CHINT / United Civil Hold Point
87252f93-946d-42ad-b803-e167aeb988cc | checkpoint | Flow Test
374fc425-31e2-56d7-9ee4-8d2172182eca | note | Visual Inspection to verify water flow through drains
bc7953f1-a6a3-506f-aa32-e790ac9a7e28 | note | Smooth flow; no blockages
764f79cd-0f50-42b2-8d5b-e9622bbb713f | section | Post Construction and Handover
fdbeda9b-2428-4a57-9876-f59ed126781d | checkpoint | Final Walkthrough & Inspection
e62b0d29-3126-5256-b44e-c63efeb67fb3 | note | Comprehensive Visual Inspection of Stormwater and that it is ready for use
6e982035-3e05-50ea-9d30-f258afb646b3 | note | Comply with IFC Drawings / Specifications / KDC EES
bf157520-4f75-5dca-9ff0-32d517d98d10 | note | No misalignment, defects, or debris
0141d802-0986-4be2-8a53-90c1341733b0 | signoff | CHINT / United Civil Hold Point
a42f8a2d-7862-4ee4-84c4-a768e23b4492 | checkpoint | Non-Conformance-Reports
669bdfeb-11e0-5cb7-96ab-87a4aeaa90b4 | note | Each Non-Conformance Reported, Rectified & Closed Out
59242f9b-14f4-45e4-aa7b-eb970429b410 | checkpoint | Punch List
75c8c67b-2148-55ff-a823-77a3a691fbe0 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
7070abe9-5ad5-4b29-87f9-cc8a7a58a1df | checkpoint | Documentation
4e597be3-a8b7-5e30-8f97-afaa43d7f0da | note | On completion of the Mechanical works for this Block
e5419cd3-3e95-544d-af73-0b2339d110e4 | note | Submission of all test results, ITC's and any as-built drawings
5c481f09-c457-5a33-8103-1e625e474e0e | note | Complete and approved by client
9f70a944-0cd1-44cf-a3e4-20e189c758cc | signoff | CHINT / United Civil Hold Point
a1ffbecd-5483-4987-99f0-6db17b15bad9 | checklist | ITP - Internal Roads | itp | ITP - Internal Roads
abfc9555-4821-46f3-ac16-fb4d67f207db | section | Preconstruction
0776b846-c07f-4692-8b70-f16cd3d05627 | checkpoint | Design Drawings
2238628c-8cf2-553b-8f45-6e39f3de361b | note | Issued for Construction Drawings available
024abe8f-8342-4b72-8e84-430043e54510 | signoff | United Civil Hold Point
b6f13de5-cc0d-41d3-aa72-db20489a34f3 | checkpoint | Survey & Setout
0abc92ba-0810-5b3c-bd79-b1af67e034be | note | Verification of road alignment and layout
0fc00044-d1e4-52db-9586-91002bbf7b40 | note | Alignment with approved IFC Drawings
3912272a-594e-42e2-a15d-472e475aef35 | signoff | United Civil Hold Point
d2a617b8-c410-496a-b3f5-5a123b8ee170 | checkpoint | Site Clearing
2120c002-71b1-5a2e-b5c8-bf1d0669b819 | note | Visual inspection of cleared area
4a4b9df3-632c-5459-8f50-d92e79245ca0 | note | Free from vegetation, debris, and obstructions
b540acb9-1e62-47b8-beb7-b9934a8a7c87 | signoff | United Civil Hold Point
93276520-d40f-4b5e-900b-047ed05bd7d5 | section | Material Procurement
148d3182-847c-49c9-af39-5b54c73f578a | checkpoint | Material Approval
174e789f-e894-50f9-b290-fa881ae31d89 | note | Approval of road materials (e.g., aggregates, subbase, basecourses
754edef6-3360-518e-a601-829daff5ab40 | note | Compliance with KDC EES2011 specifications and standards and IFC Drawings
dcc2d280-7437-5097-85d5-43de06aad03f | note | Material Test Certificates - Gradings, CBR, Crushing Resistance
1dd95988-b5e0-4856-9ee8-f0abec7e4981 | signoff | CHINT / United Civil Hold Point
d1b99d41-c515-4673-8fd3-d7da726eb858 | section | Construction - Subgrade
93da8519-de31-477f-818c-907e840b6283 | checkpoint | Excavation/Grading
2f3c9e05-13cb-56ba-a524-999fdbc5cdbe | note | Inspect grading and levelling of subgrade
8cab52cd-6fde-5c1f-8784-88c7edddd5bc | note | Uniform surface with proper slope and drainage
5fcd1af1-9655-5871-b1df-d2332df22a8a | note | Visual Inspection and Measurements
b1e1f99a-073b-5eec-bdcd-f4af0d9363d2 | note | Every Internal Road
d5d9d7fe-78a1-4b0d-95ae-02dc593220f6 | signoff | United Civil Hold Point
e1341a0f-b5da-443f-9f16-debff9d10358 | checkpoint | Compaction
2c2f04cf-a4e3-5fa5-9e29-9af067e33e6c | note | Field density test
89e9803b-fd74-5e9c-b119-29ecc9f382c5 | note | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m
2c91c0d5-234c-5e0b-a6df-b83d96632778 | note | Scalar Penetrometer test check sheet
e1fec911-3f38-5bff-aec3-04160b8cf706 | note | For each section
d9afe38a-faa1-522f-aebd-a09367f6da71 | note | Hold Point for United Civil
c480b89c-e1d4-4b79-b339-77488bda7137 | signoff | United Civil Hold Point
7022365b-5974-4e77-88c5-3c1d400dc41f | section | Subgrade Improvements (Where Required)
58a0000b-dade-4f74-833f-e0c5ec1924f4 | checkpoint | Identify areas of Undercut
7593c718-dd98-5a1a-a276-a3146917fa88 | note | Identify areas of undercut and liaise with Client
17e8d11a-32e8-432b-b7c7-8bc6a6393ab9 | checkpoint | Excavate Undercut
5da30a04-3c77-5c98-ad2f-850fbf889e9b | note | Excavate a minimum of 200mm in depth full width of the road
a29cac63-962d-54cc-80f9-7bf930e9e6b5 | note | Any free water has a path off the road in a controlled manor
ceff2c65-988b-5770-b00c-72fbc463e9fe | note | Visual inspection of subgrade with Client
30fa97c4-319b-5862-b19a-7d48a499ffc4 | note | Undercut ITC completed
d3fd2b39-37c7-415c-85ef-2455f0e37a43 | checkpoint | Geotextile & Geogrid Installation
fc1e9c11-bf82-58a7-bf6c-b491d97be119 | note | Visual inspection of geotextile & Geogrids placement for each section
461ff8e7-c8f4-5412-a3cc-23d1b9b2341c | note | Correctly installed with proper overlap and anchorage
504d9c88-0c24-5919-9021-15890f3c9ccd | note | Product Data Sheets
ed8a9e06-170c-44ce-b71e-127831c545ad | checkpoint | Backfill Undercut
99ffefd8-bad9-558e-98c6-aad3062fbb63 | note | Visual inspection of backfilled material
f8620507-29bb-5ff3-b153-1363d322d11c | note | Compaction to be static compaction only
105f7cab-d663-53ff-b1d5-e5b14bd05c93 | note | Proof rolled with no obvious weaving or areas of instability
143968f7-775b-4f67-81dc-faba663e2893 | section | Construction - Base and Subbase
dd216a86-f22b-4873-91e8-0007d8676041 | checkpoint | Material Placement
defef8f3-d1cd-5959-9d49-4cb4f805a40c | note | Inspection of base and subbase layers
ae9c0bb9-9b60-5f6d-a0d2-1851520452f4 | note | Compliance with IFC Drawings and Product Data Sheets with Material Specifications
12468dcb-6ccb-5dad-8650-949821e220b2 | note | 100mm thickness of Gap40 and 50mm of Gap20
27e0e1f1-14ba-5389-8729-a28c2499d8b0 | note | ITC Completed for Internal Roads
9c5e0da1-1e55-47f8-bcab-ad7b4673c31b | checkpoint | Compaction
e9b41fe9-d11f-5de7-ad9a-228784fdea1b | note | Proof Roll
4aa5701e-2ef5-538f-bf83-00a9982ba838 | note | Visual Inspection of Compacted Base and Basecourse
89e5753b-e427-5fe5-b297-eb39f2fc3c5a | note | Each Road
4c4053ba-88b6-40c7-ab7e-961284b4a235 | signoff | United Civil Hold Point
b4e6ae2b-0065-4bd3-acf5-eb276050e093 | checkpoint | Level and Alignment
bde5091f-fcfc-5f23-b916-fdcd976764d6 | note | Visual Inspection of Alignment
3f0b7cb7-15e3-5795-8473-aed4d11c9aa6 | note | Compliance with design tolerances
2175eb03-8a36-51d9-bf42-4c0d301694c3 | note | Each Road
aeea9e42-b247-42d7-baa9-c3e3475f6bb2 | signoff | United Civil Hold Point
58fccf82-627c-45b0-aa15-c2690c41ed47 | section | Construction - Surface Layer
25c6ddd6-5172-431c-b00d-ca9015e06a70 | checkpoint | Aggregate Placement
6aec105c-9013-586a-ae86-53028e2ac8e6 | note | Inspect placement of aggregate layer
9e1d4dc4-3dec-50f2-b43f-b8eb7118b65a | note | Even distribution; meets design thickness of 50mm
2ee4b183-43cc-5975-bce3-2cb17514c7b2 | note | Every section
453c6bfa-3d4a-49e1-ad76-4b7ebef1e357 | checkpoint | Surface Compaction
aabb312f-dd1c-591e-a2df-f748d65e6316 | note | Proof Roll
fa242066-de5d-56ba-abbc-7aa606054710 | note | Visual Inspection of compacted surface layer
8ef3ac72-a5df-546f-8df0-e718366c816d | note | Each Road
6c13be30-0508-4e03-b92a-aedcbc49a11f | signoff | United Civil Hold Point
55071e8d-3eb9-4f5c-85fe-3ea0545b91b1 | checkpoint | Final Grading
d2248020-475b-5aff-b0d9-b1af034f62e3 | note | Visual Inspection of final grading and surface finish
c19a0554-41ab-547c-ad33-5f12a8adf3d2 | note | Smooth surface with proper slope for drainage
40f6ca79-b919-5ab8-ba77-e827c188c201 | note | Each Road
544f8d91-4a45-40a3-83f7-30fbdbc573a4 | signoff | United Civil Hold Point
fb4f2991-ead6-40d5-a4cf-6a62a0347e55 | section | Drainage
2b48e84d-2509-47ce-a6eb-8d4a4c0d0019 | checkpoint | Culverts and Drains
13c200ef-d50e-5d23-b7f2-5b74d0f90ae0 | note | Visual Inspection of installation of culverts and drainage channels
8a3cdedb-d4e9-505d-b989-81fea6cbe335 | note | Installed as per design; no blockages
9e6bad61-e694-5515-a19b-b90c1880900d | note | Water will flow without deviation
39003a07-0f48-59cf-b798-69d19b2fc210 | note | Reference Drainage ITP for Culverts
515aef71-d44d-4dc3-a3a3-e8ed81446ede | section | Post Construction and Handover
6368d12d-fff5-4de2-94f1-ebd0ee0e961d | checkpoint | Final Walkthrough & Inspection
1eac03a4-2c45-58b8-bebf-b8f8771718f4 | note | Comprehensive Visual Inspection of road construction & ensure roads are ready for use
a46d8159-1f74-58ec-8d2c-b4239fa4daba | note | Compliance with IFC drawings and specifications
e30b8f41-0fa2-58f9-a208-18c45d7c2926 | note | No defects
158441f5-cd44-43c2-b568-59ecb9eb47fc | signoff | CHINT / United Civil Hold Point
1023f131-e9f2-4af8-abe6-f66cdb935a47 | checkpoint | Non-Conformance-Reports
80496d78-6851-5494-a291-9914e58b22e0 | note | Each Non-Conformance Reported, Rectified & Closed Out
ba9533d3-86c7-449b-bb47-7f2b0b8fbcb2 | checkpoint | Punch List
7a342d89-983b-5472-9864-b00b2eda6010 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
fbff592b-230b-4e3c-be0b-c63cf7c252f9 | checkpoint | Documentation
7814b046-9a6a-522a-b694-5d8cda674e12 | note | On completion of the Internal Roads
c4b2fca8-684a-56be-bd39-c8b32170045f | note | Submission of all test results, ITC's and any as-built drawings
be5347e4-6e83-55db-8284-2567c995f49d | note | Drone Survey as-built for alignment and levels
3ce083c9-b2b9-483c-8c99-e8bf7b2617b4 | signoff | CHINT / United Civil Hold Point
d84173c5-21b0-4319-850a-3de723280854 | checklist | ITP - Inverter Foundations | itp | ITP - Inverter Foundations
cd3f2687-c440-402d-be29-9cb94f7ea436 | section | Preconstruction
d0e35911-877c-4c23-bc81-e4ab0c116a73 | checkpoint | Design Drawings
752fe0ba-6758-5ad7-879c-f090b86a0cfc | note | Issued for Construction Drawings available
26fe4fb9-3493-4b8e-8321-7a031dc55586 | signoff | United Civil Hold Point
134881fe-2994-40ff-9b44-70ae5f7c1ff1 | checkpoint | Survey & Setout
48934026-fd6e-5d93-9b4f-1fb54cb50923 | note | Visual Inspection of Inverter Foundation layout
58919954-6dcd-5c72-82f8-3b69b8745b10 | note | Alignment with approved drawings and site plan
eef92179-269a-42b6-b6e2-c7883bb9fc88 | signoff | United Civil Hold Point
e94e29ce-db08-4d9d-9d7d-d3249e76f17e | checkpoint | Site Clearing
89b21391-9ab5-57c7-9d70-6f6ed7462346 | note | Visual inspection of cleared area
99bad2ea-93c6-503a-ad31-c3bed656ee6a | note | Free from vegetation, debris, and obstructions
2b398180-937a-4cd0-9466-13dffc0777f7 | signoff | CHINT / United Civil Hold Point
cb98e4ed-fbf3-484b-9f71-11cb6d1f466b | section | Material Procurement
ac627828-823a-4e48-b9fc-03ee2a6d1540 | checkpoint | Review of Concrete, and Reinforcement steel
7be5fb85-e7ea-5d8f-a331-93766c6a279d | note | Compliance with IFC Drawings, Specifications and Standards
7fe1abae-c63b-5f74-89cb-95dcebca2b0f | note | All reinforcing bars shall be Grade 300E or 500E to AS/NZS 4671
34308fcc-5c28-593d-a0cf-0725be1b1ff7 | note | All concrete construction shall be in accordance with NZS3109 and IFC Drawings
cebc259c-71db-5a9f-914c-9f97417ef779 | note | Concrete shall be 40MPa Minimum Strength for precast elements or 30MPa for concrete poured insitu
5cb7c252-138b-5aa3-b126-1317931d4e0d | note | Material Test Certificates / Dockets supplied for each delivery/Pour
a791eb8e-6026-43b3-8290-7f41ce74bade | signoff | CHINT / United Civil Hold Point
d3aa878e-3d56-4910-bb35-727385d270f9 | section | Construction - Excavation
ea1a3a50-e6f0-4173-9422-da581ab169af | checkpoint | Excavation & Footing Construction
7602fcee-e56c-5fbc-9697-6d064190b6a0 | note | Visual Inspection of each footing location
d4a16d6b-209b-5535-ab5b-fd7935f0b71f | note | Check that depth & dimensions comply with IFC Drawings
0b9ae81a-4cd1-59d2-bac4-de51edca302b | note | Compacted hardfill pad under footing locations
fcb5a40c-8b8f-5ee1-87a9-717b216ee6bb | note | Results Recorded on Clegg Hammer Checksheet for compaction of each footing
11e95a57-9016-4174-8bcc-80aadc76dd5b | signoff | United Civil Hold Point
4a44a0a6-e99b-4174-9f08-23ed8c3aa6d3 | section | Construction - Concrete
4660680a-43ff-4856-86ba-b8bd56a509fb | checkpoint | Formwork Installation
5d461957-ccbc-5c17-baee-1d6d9a7559c1 | note | Visual inspection of formwork alignment and cleanliness
d5583a83-eaca-5c09-9c15-ae561d586923 | note | Compliance with IFC drawings; no gaps or damage
3c64d48a-bcea-5452-805a-6159fb2bab1f | note | Prepour Inspection completed for each pour
b980daa9-ee59-4eb4-9d9a-725decc80ffa | checkpoint | Reinforcement Installation
bff7b163-6acf-59ed-bce5-146bc5195139 | note | Visual Inspection of steel bar placement, cover, and tying
7db7c8d9-615f-504b-943f-5cdabb9ed3f4 | note | Compliance with bar bending schedule and specifications
525154c4-f998-524b-93be-72b40e4bb2a5 | note | Prepour Inspection / Inspection Report for each Pour
5cdef193-1bc2-4f07-90fe-b7cf69b6e00b | checkpoint | Embedments
dd591385-07c0-57ba-b54e-600fdfdea6c7 | note | Positioning of anchor bolts or inserts
16a7fb7a-aa13-5455-8095-e21710bf4d93 | note | As per approved IFC drawings
407064ad-5a3c-547e-b2b3-f8eebd611004 | note | Dimensional check
22cb0ec2-cb22-526e-975b-ffc4daf11bc9 | note | Prepour Inspection / Inspection Report
b0e8091c-bdb1-4010-9ee6-5f245063461d | checkpoint | Concrete Mixing
82177146-006d-5df4-a91f-8cc3025e501c | note | Verify Certified Batching Plant is used
d9f48488-8220-59c2-82a0-23109661363a | note | Concrete Mix Delivery Records
90f5027a-6ea8-5da0-acd4-0da25119576d | note | Prepour Inspection / Inspection Report for each Pour
2a94e774-eddf-4f37-83ab-d99916fd838f | checkpoint | Concrete Placement
15790235-56c2-5501-b83a-60de9c8af924 | note | Visual Inspection during pouring
a3f3fa93-f52e-5792-b5f5-e32315c321cb | note | Proper compaction of poured concrete, no segregation
844ec4c0-eec0-5619-b3de-4177110e5b0a | note | Each Pour
27e2532d-5643-4866-84e8-07dd87b2427b | checkpoint | Slump Test
7b036388-786b-5d5a-a91a-6d853e4a3be7 | note | Tests Taken in accordance with NZS3112.2
8093842c-991e-50bb-ba34-605e21aad6a8 | note | Slump Test Report
f6cc91e7-cd01-57ea-b54f-9cd805e8094c | note | Per Pour
2f280c82-78f9-4b17-8305-b7e8c2769396 | signoff | United Civil Hold Point
574ca381-0a84-4be0-9a6b-b8a71643204e | checkpoint | Concrete Strength
aa588c8e-ce2a-5a11-bcf9-679d59cf375e | note | Compression test on cylinders taken in accordance with NZS3112.2
17f887bc-3e1c-5e98-8996-130b17cbf062 | note | Meets required strength of 40MPa for precast element or 30MPa for concrete poured insitu
5a12dca7-fe69-5b47-b582-2b2563b07cd6 | note | Test Report
d0a25b7c-de58-4ae3-a600-f711937e89a9 | signoff | United Civil Hold Point
565142c5-cc5c-473b-8555-bdfe11d2b5fb | section | Post Construction
9b8f54af-6abb-4c1f-aa37-e04d9181a816 | checkpoint | Curing
7132febf-4e5a-55a4-b0ea-b8158562792d | note | Visual Inspection of curing of concrete
08fed105-2018-4304-805b-d2efbc4872df | checkpoint | Foundation Alignment
32095aee-468e-5b70-9184-17b52f9c76c8 | note | Check position and alignment of foundation
f2bedc2f-f5e1-5a50-a534-82d8de75aa50 | note | Dimensional checks & compliance with tolerance in drawings
21c2601d-3d4e-576c-9c00-383505c8ec0c | note | Larger Block dimensions should be 3338mm x 600mm x 770mm
e2f0ce4e-2634-5ba7-acdf-c0b2c4c49f25 | note | Small block dimensions should be 3338mm x 500mm x 725mm
175e39a4-d59a-4fa8-8626-4c96885ba60a | checkpoint | Surface Finish
6f7550b9-e1ff-53b7-9d46-cb9309c30e79 | note | Visual Inspection of surface for cracks, voids, and finish quality
0e79732d-697a-56f9-964d-f776c0530b75 | note | No visible defects or honeycombing
32f0db4c-221a-5bd1-baaf-0000bdc62831 | note | Every foundation
14728c59-0247-4c49-9d8b-4bf6d0815ed4 | section | Inverter Container Installation
ecb27e44-36bf-4186-ad98-8d389c35c95c | checkpoint | Anchor Bracket Installation
d7e454f7-60d6-506a-b89a-4dad787d2ee4 | note | Compliance with IFC Drawings, Specifications and Standards
1c65f327-6e1d-5a7a-8d78-248954adf6c2 | note | Material Test Certificates / Dockets supplied for steel and galvanising
dee699c4-fb20-5464-83fc-ed3abd9ec3b0 | note | Hold down bolts as per IFC Drawings and specifications
4ffed571-688b-5c3d-a356-622727685a28 | note | Epoxy to be as per IFC Drawings and specifications
1db7adfe-e027-52cb-9651-1e2febdff8b5 | note | Grout to be a minimum of 20mm thick under Anchor bracket plate
a84dd9dc-3cf5-4960-bcbe-bb65823a9962 | signoff | CHINT / United Civil Hold Point
f7557f18-62cd-4d2d-96d5-73969ca4ea0e | section | Post Construction and Handover
fe7034c8-ec42-43eb-a048-4d2bd9e18cd1 | checkpoint | Final Walkthrough & Inspection
2b922f96-2fd5-5b63-97d2-f02a8a862701 | note | Comprehensive inspection of all elements relating to the Inverter Foundations
7526a8bd-384e-5a73-8659-3cea3c40afd4 | note | Compliance with IFC drawings and specifications
74034241-f72d-569b-9efe-2708b468dc0e | note | Verify all Inverter Foundations meet design and functional requirements
df82b430-6537-53e0-9c98-1b60f28c6484 | note | Inverter Foundations ready for subsequent construction activities
3fa83fa4-7062-4eae-af00-f517cefebc4c | signoff | CHINT / United Civil Hold Point
476e73d6-a552-43cb-9b13-8ac37bad88da | checkpoint | Non-Conformance-Reports
58391f23-4839-51ef-a108-b9c12861bbe7 | note | Each Non-Conformance Reported, Rectified & Closed Out
bda39839-e5b2-42f8-8282-0b4d3632b451 | checkpoint | Punch List
74d5a0ed-2ab2-5638-b275-a90fa168bf2d | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor
5380513b-1284-402e-a654-3b6aaf93aa40 | checkpoint | Documentation
d7daa829-a1a5-56d5-9877-adc2c7f12721 | note | On completion of the Inverter Foundations
0f6ba1ea-312a-5cf6-b917-c08a47a80d52 | note | Submission of all test results, ITC's and any as-built drawings
6543104d-127e-5445-8422-83a5354c19f3 | note | Complete and approved by client
01941b37-1bde-4938-b1fe-c3bf21a6bc19 | signoff | CHINT / United Civil Hold Point
681eac53-c863-4037-b100-cc05a8b51ba5 | checklist | ITP - Laydowns | itp | ITP - Laydowns
ba5cf97b-09db-46c9-a908-940b44ba2f11 | section | Preconstruction
a940e2f6-7a75-460e-8ed5-fc8604befee2 | checkpoint | Design Drawings
9bfbd26a-d788-5e80-aea6-008b3266f68e | note | Issued for Construction Drawings available
e0df34b2-cbea-4b83-836d-18458998052c | signoff | United Civil Hold Point
2832fc8d-ec1f-4b6b-ba49-63a740a5c68a | checkpoint | Survey & Setout
4a4251b5-6e05-54f5-82c2-58a1135362c7 | note | Verification of road alignment and layout
caf462fd-d9a2-5201-a127-af27024487e5 | note | Alignment with approved IFC Drawings
5d53cac9-6879-4944-a666-67aa34c29fe7 | signoff | United Civil Hold Point
54ec5e4a-2cd9-43f0-92c7-38144d582785 | checkpoint | Site Clearing
079395b3-ee20-5fbb-8bf8-a890c58dc723 | note | Visual inspection of cleared area
acbf29b2-1547-52a3-8c0c-c09a52daa933 | note | Free from vegetation, debris, and obstructions
cce89b13-2477-4a9c-84da-07948115f86f | signoff | United Civil Hold Point
22c4f7c0-ecf8-4a61-a5e4-adbd3681530b | section | Material Procurement
8a8b9fb3-cf85-4d75-94d3-417e9d369d30 | checkpoint | Material Approval
f826cc1f-4e46-5ab8-8a09-0ee21aa1ca66 | note | Approval of road materials (e.g., aggregates, subbase, basecourses
79b96f08-3167-5dc7-894f-cfe21f874537 | note | Compliance with KDC EES2011 specifications and standards and IFC Drawings
8f01c985-450e-520c-8b3a-53bdfb562301 | note | Material Test Certificates - Gradings, CBR, Crushing Resistance
0b978d38-d8bd-490f-9706-fd2cb3cbe365 | signoff | CHINT / United Civil Hold Point
a8fb1cb4-bbc6-48e4-90c1-d034eef6f070 | section | Construction - Subgrade
57bc44a1-eaf3-40ba-ace7-e6c7f7bdd530 | checkpoint | Excavation/Grading
be68cb35-f164-5f39-8c69-087dce1674e1 | note | Inspect grading and levelling of subgrade
1cd9ccc3-4412-5f32-bfbb-84f70bd03a8b | note | Uniform surface with proper slope and drainage
e8d96996-69d6-5e54-854f-bf244b53bb48 | note | Visual Inspection and Measurements
3ad8dc38-ab5c-59f4-b84b-8e5bf89535ba | note | Every Internal Road
3ad1a8ad-77a9-4303-b829-f0e80b78541e | signoff | United Civil Hold Point
16eaa2d6-469b-4421-9cc6-bf0b5d0a9c34 | checkpoint | Compaction
e2682894-b734-54f8-bb62-250838caccd9 | note | Field density test
5ab292c0-438c-58d7-8f95-da91d86f62ca | note | Achieves required compaction (Scalar Penetrometer with min of 2 blows per 100mm) Tests every 100m
ed5c81f2-c794-569c-8a13-49ecc9d38ea7 | note | Scalar Penetrometer test check sheet
2c7411ae-f78c-57f7-92d2-26f28da300e0 | note | For each section
7aed4907-979e-49e6-9d57-d0aecf4b39ea | signoff | United Civil Hold Point
aeca93b5-5c58-4a64-99ea-62cdf1efc8a2 | section | Subgrade Improvements (Where Required)
c3fd6497-ca12-4f6e-b467-5ca4622f05e6 | checkpoint | Identify areas of Undercut
8e5a224b-953e-5557-bed7-da324aa78494 | note | Identify areas of undercut and liaise with Client
32407700-5097-435d-89ff-4e1389986bad | checkpoint | Excavate Undercut
a1994f7c-ecb3-5c07-866d-74a95d80ba45 | note | Excavate a minimum of 200mm in depth full width of the road
b019de98-0455-5dc1-bbb5-4f4b012bd381 | note | Any free water has a path off the road in a controlled manor
c0091483-b0a3-50b8-97cc-d540022d0fd1 | note | Visual inspection of subgrade with Client
b7804623-1b1f-5790-a945-5377019fe9b6 | note | Undercut ITC completed
7f10ae93-8bd2-402f-9482-cd635a4b6042 | checkpoint | Geotextile Installation
15a71406-33a1-5c22-acfa-c5a208784f3a | note | Visual inspection of geotextile placement for each section
1b09907f-375e-5755-94ad-39d85b53cbeb | note | Correctly installed with proper overlap and anchorage
b22a95a7-3b80-5be0-972c-01ec09445984 | note | Delivery Dockets
4cfdc63e-6313-470e-9607-8a622cef0870 | checkpoint | Backfill Undercut
3e78876a-520b-520d-a0c3-5a468dc357bf | note | Visual inspection of backfilled material
b2bfd069-0ef1-5ba1-b6b0-71af9e059a8b | note | Compaction to be static compaction only
97384a70-1952-54fb-8829-689ff8086459 | note | Proof rolled with no obvious weaving or areas of instability
25a48c49-65d6-4539-9274-45a30f1e2f27 | section | Construction - Base and Subbase
c69293d5-16b5-483e-8537-9ecc591d2258 | checkpoint | Material Placement
87993e91-54bb-58e3-a38d-e1b17384695e | note | Inspection of base and subbase layers
04e73905-2c27-504a-b4ec-c50367338fb3 | note | Compliance with IFC Drawings and Material Specifications
b4953d51-1ba3-5220-867a-021a5d337e65 | note | 100mm thickness of Gap40 and 50mm of Gap20
74b70a3c-4a36-4c8a-8bdd-5f74915a2d0d | checkpoint | Compaction
982fcaf4-ec99-5dc3-8716-f0d232d96e54 | note | Proof Roll
d1ec8c7b-e571-533a-9a4a-2a0e8fefa23a | note | Visual Inspection of Compacted Base and Basecourse
2c614dc7-0272-5d8e-9d10-9919c237d594 | note | Each Laydown
e1bfe800-0792-4e9e-b13b-c7845269e820 | signoff | United Civil Hold Point
2df93a48-58d0-487a-a496-1f563135399c | checkpoint | Level and Alignment
0fd7c24d-6f4f-5631-9041-463a8b2d3789 | note | Visual Inspection of Alignment
ca794cb3-58a5-52c7-9b75-b202d36d9dd5 | note | Compliance with design tolerances
db74f754-a884-57f2-81e7-158a89dbc28c | note | Each Laydown
2100772b-fb20-4399-ad0b-3ccea36b49a2 | signoff | United Civil Hold Point
ea31d84d-5417-41bc-9c3c-398ee56863ae | section | Construction - Surface Layer As Required
a144a0be-cf6a-4d5e-96ff-f41127e8e956 | checkpoint | Aggregate Placement
091b5675-b146-5bb3-a92c-572db289636d | note | Inspect placement of aggregate layer
25cd98f9-0b2e-5482-a709-288cebf70c90 | note | Even distribution; meets design thickness of 50mm
11006f77-82ca-51be-bab8-8f198bfd573e | note | Each Laydown
7076234e-a2c4-4c9c-8eac-8d9df0cf86c9 | checkpoint | Surface Compaction
07845a50-b67d-5435-9dcb-dc56a1155a41 | note | Proof Roll
77bf7cda-c137-557a-8037-ce585232b84b | note | Visual Inspection of compacted surface layer
36103f0a-5824-5a6d-910d-d0aea6f5af8e | note | Each Laydown
0b894adc-10f0-466a-8843-68bf3038ea0f | signoff | United Civil Hold Point
03da886e-d1ec-469d-84f8-0ed8c1268e2c | checkpoint | Final Grading
27b1f1ab-624e-576d-b4df-cffa2c625b8d | note | Visual Inspection of final grading and surface finish
5f990bd4-ccf5-5db9-990c-8e5ae27fde5b | note | Smooth surface with proper slope for drainage
8d60a8a0-a573-5d19-b1f0-008e5df926db | note | Each Laydown
4b32bf93-4fbf-453f-87a3-80f50c97a26a | signoff | United Civil Hold Point
80eb25a2-2f96-47f8-91ea-c6f939804f41 | section | Drainage - If Applicable
41fe9584-5cb7-4b79-9309-16f57427eb43 | checkpoint | Culverts and Drains
d13da9fc-bd63-5c1a-bd70-d93d5bd2b933 | note | Visual Inspection of installation of culverts and drainage channels
204707cf-36f0-5c68-b0c7-7a18c16c2412 | note | Installed as per design; no blockages
ff2b66c6-10e0-587c-91fe-6bab26a7bcab | note | Water will flow without deviation
1dc4ab8a-ad93-48ae-ab44-0b884b888bb7 | section | Post Construction and Handover
16217ce7-3c62-4dd1-b9a2-0424a91ff8e2 | checkpoint | Final Walkthrough & Inspection
352d3fd4-0318-5cb9-b013-502c65ade5bf | note | Comprehensive Visual Inspection of laydownsn & ensure laydowns are ready for use
176647ed-45c2-5f4b-a0cc-492df4fb88d0 | note | Compliance with IFC drawings and specifications
79b86a1b-96e6-5983-aac5-ea53a3aab398 | note | No defects
d304e028-0e03-4aaf-8e09-d4123682402f | signoff | CHINT / United Civil Hold Point
1fc48483-e371-4ec0-90ed-d80223510008 | checkpoint | Non-Conformance-Reports
98989017-ce48-5830-949e-d87ec00a19a6 | note | Each Non-Conformance Reported, Rectified & Closed Out
9705bcd5-6f69-466f-8776-e381197afd3c | checkpoint | Punch List
4d9aa531-384f-56ae-904f-0da745c719a5 | note | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely manor
5691c122-46f4-48df-85d0-2a826ade9f85 | checkpoint | Documentation
d91346bf-aad7-516a-804a-70d9437bd25d | note | On completion of the laydowns
786492a2-8704-597d-966f-68c3df604396 | note | Submission of all test results, ITC's and any as-built drawings
c21c3a04-826c-5094-95b3-ab9da2b8a605 | note | Drone Survey as-built for alignment and levels
a9454d01-5d84-4588-9980-8c723085d649 | signoff | CHINT / United Civil Hold Point
90cbf5b7-d277-4f4b-9faa-45df984e4a77 | checklist | ITP - Light Pole Foundations | itp | ITP - Light Pole Foundations
806018a6-f2cd-4f20-b9e3-02d77ff83c45 | section | Preconstruction
0ee23d5f-1444-46d4-8c06-4a814a3b3443 | checkpoint | Design Drawings
66db5928-911c-5c8e-aba1-631f0e7f502b | note | Issued for Construction Drawings available
d083f88c-5629-5d09-92f6-617b4865d49b | note | Drawing MSF-EN-ELE-DRG-070
7efc776c-a6b2-4720-a181-35dc74927a27 | signoff | United Civil Hold Point
8bc01336-a9af-474c-b949-b0dcf73ac162 | checkpoint | Survey & Setout
6766e542-2a5a-5e99-8162-c37815927ea8 | note | Visual Inspection of Light Pole Location setout
a6d64fcf-b37d-5c5e-868d-2c4dfaf43444 | note | Alignment with approved drawings and site plan
9025d4b3-a0d0-469f-be49-b04583e08404 | signoff | United Civil/CHINT Hold Point
e97fd8b1-dde0-4733-8501-928ad7d09420 | checkpoint | Calibration of Plant
0da20da5-b030-565f-9588-2dd123328c55 | note | All testing and measuring equipment calibration certificates valid
825066e9-cf8b-470b-bbbe-066ce24a11d6 | checkpoint | Site Clearing
c7d6b7f3-b752-5280-a02b-54a680d0abd2 | note | Visual inspection of cleared area
86a8c6d2-d1cf-5143-aa5d-92e61dbcf5a9 | note | Free from vegetation, debris, and obstructions
540fbb08-4de6-4d92-a68b-059cbd1c5a9b | section | Material Procurement
315b913c-61fd-4bbf-9577-28e968b9b22a | checkpoint | Review of Concrete, and Reinforcement steel
176e31fb-105c-5e8f-b437-8c4cde91177f | note | Compliance with IFC Drawings, Specifications and Standards
a264f3a7-2232-5b03-8cea-7404f159e981 | note | All reinforcing bars shall be Grade 500MPa to AS/NZS 4671
230edadf-e7ad-5c58-9b6a-f730a626dc1b | note | All concrete construction shall be in accordance with NZS3109 and IFC Drawings
c4cbaf59-f808-5ea9-8d19-8261e4829636 | note | Concrete strength shall be 25MPa
48b61cef-f99b-5f2b-891d-a9ca5646d16a | note | Embeded threaded rods, nuts and washers shall all be M16, grade 8.8
d7cd0ab2-1be6-5604-88bd-c77a175f258f | note | Delivery Dockets supplied for each delivery/Pour
d54a2b2f-96ef-403b-90a0-e6d7bec3eb3e | signoff | United Civil/CHINT Hold Point
6c9fb1f6-374d-410c-9f62-e1c6a797db59 | section | Construction - Excavation
9824b7f3-0582-49e4-bc67-ce491a78dc0d | checkpoint | Excavation & Footing Construction
538c4da4-9d75-5e98-8b08-1c63dbff4bab | note | Visual Inspection of each footing location
057b156d-f1ab-5ba7-b44f-ac935113513f | note | Check that depth & dimensions comply with IFC Drawings
f6cd1063-2ccb-5f92-9996-a5910616c0e8 | note | Bottom of foundation pad must be at least 350mm below ground level
90964c9e-00f5-5432-a781-57ceacb52601 | note | Compacted hardfill pad 200mm thick of Gap40 under footing locations
fb2fd412-debb-57ad-9b2f-910cb9d975e8 | note | Test acceptance to be a clegg test recorded to min of 24.
efb5cf26-d116-4488-b9cd-a826ad641cda | signoff | United Civil Hold Point
03a533af-94cb-4257-99a4-7465d39ec550 | section | Construction - Concrete
7156fec8-cfd9-4973-8590-48334e50b4d2 | checkpoint | Formwork & Reinforcing Installation
7628125e-d178-5c26-907a-1f8d13ee01cf | note | Visual inspection of formwork and steel bar placement, cover and tying, alignment and cleanliness
69d15d14-07cd-5acf-8349-5b15dc8a9be2 | note | 75mm Cover is maintained to ground and all formwork
d3900731-0c08-5818-b845-de37e93401c7 | note | Compliance with IFC drawings; no gaps or damage and formwork set for finished level to be minimum of 20mm above finished ground level
794ca97b-58c7-5250-a118-78fe736f40f5 | note | Prepour Inspection completed for each pour
d955e090-6610-491f-8311-ea8ff8fca94f | signoff | United Civil/CHINT Hold Point
303ab262-fea1-4f76-ab14-fb24238891fa | checkpoint | Embedments
693f5e37-00cf-5209-8f37-d3a93fb453e8 | note | Visual inspection of all embedded items before and following pouring
27b422c7-186f-520f-b106-894b74207963 | note | Positioning of anchor bolts or inserts is as per approved IFC Drawings
c48660fb-f18d-5650-8f20-e0fba57c8267 | note | Hold Down Bolts dimensional check - min. 30mm from underside of plate to top of foundation & 220mm from embeded plate to top of threaded rod
3114a1a0-1a83-5fb3-b5ad-5d3e6757b0e3 | note | Installed electrical ducting to have a 32mm duct for earthing & 2x 50mm ducts with 400mm radius extending 800mm below the finished foundation and 200mm above the foundation
00a34af2-6e08-5d41-9b0d-508bb539b544 | note | Prepour Inspection
dd5320e1-00a4-4496-a49d-3afe8c6c74ba | checkpoint | Concrete Mixing
4fb66e45-e579-5d9a-a3d3-4b8b8376b2ff | note | Verify Certified Batching Plant is used
c31cf2d1-5f6b-5a4b-a3a0-42ed2334af91 | note | Concrete strength to be min of 25MPa
fca0acf6-2f67-5c47-94f4-ce0a9980149f | note | Concrete Mix Delivery Records
93f7fac8-8e15-4dac-95d0-f1df51270386 | checkpoint | Concrete Placement
844d2477-62bf-5b5a-9e44-c4052c0fac1a | note | Visual Inspection during pouring
84d44ab7-63f8-5427-921c-186dcf5995b3 | note | Proper compaction of poured concrete, no segregation or honeycombing
052e7820-0670-5a0f-86c3-a277af7579d4 | note | Each Pour
f1cc32a7-237c-47e5-9fe6-b24886c0ead5 | checkpoint | Slump Test
57d3f5d4-520e-5fcd-ae94-7ebd59a1bd17 | note | Tests Taken in accordance with NZS3112.2
c7c4a652-05e3-5f54-bba1-a0d57277f8fa | note | Slump Test Report
96d124e7-f418-5537-bf15-7a1444142796 | note | Delivery Dockets indicating slump
09168e06-9b6e-4e2e-9d1d-9e65352e4839 | checkpoint | Concrete Strength
a8030ce8-abfa-541f-85c2-b4faca2e8aa6 | note | Compression test on cylinders taken in accordance with NZS3112.2
c888e8c2-ca40-59dc-918a-72ebbb15a01c | note | Meets and exceeds 25MPa at 28 day test
be1dc705-805e-54af-90de-4a5a915ec1b7 | note | Test Report
6ec66220-8f7b-4bd6-8882-cd91d0d93257 | signoff | United Civil Hold Point
03c5b3c2-d80b-4d54-b4b5-5dd195147552 | section | Post Construction
f90403d7-76af-461d-bfc1-cb9e7195b22d | checkpoint | Curing
aaf4c5e8-6926-54ab-8e38-dd872834e177 | note | Visual Inspection of curing of concrete
48d5e346-4076-465e-93e8-862264b4be23 | checkpoint | Foundation Alignment
d181a816-e9f5-5e84-b187-dd11358c71a9 | note | Check position and alignment of foundation
7f619241-8263-5390-9537-35e9b6481ea4 | note | Dimensional checks & compliance with tolerance in drawings
42a99296-76e2-4179-9c20-d44fcb797560 | checkpoint | Surface Finish
67fc3750-b462-515c-b988-4701ed0c0822 | note | Visual Inspection of surface for cracks, voids, and finish quality
e0a40f2c-755d-517d-abac-abacf49e23fa | note | No visible defects or honeycombing for each foundation
244b7d5c-d42a-4ea3-87f9-87027d2152c4 | section | Post Construction and Handover
97ab37c4-4e67-44c1-b3f3-ab773c031e37 | checkpoint | Final Walkthrough & Inspection
34eb5770-2338-581a-b440-d16330b5c4c0 | note | Comprehensive inspection of all elements relating to the Light Pole Foundations
79328e9f-2895-5ff0-a1aa-a2d0ea76b11d | note | Compliance with IFC drawings and specifications
0a5ac852-d740-5793-b94c-60ae571deac9 | note | Verify all Light Pole Foundations meet design and functional requirements
c52d19e8-ab1e-544c-a1f7-cb7df96827bb | note | Light Pole Foundations ready for subsequent construction activities
1ef57d62-63e0-4166-93f6-47a061568486 | signoff | United Civil/CHINT Hold Point
0ffc9612-a928-4cf3-95dd-03b16644c6d1 | checkpoint | Non-Conformance-Reports
f2e1d1df-d7a6-5cae-be96-0cd092f7c3c9 | note | Each Non-Conformance Reported, Rectified & Closed Out
c96b058d-4903-407a-9270-34b8bd1a44ed | checkpoint | Punch List
4a9f15ac-a761-589f-88eb-cefc432218ca | note | Development of Punchlist with Client and Contractor Representative
725b527e-3dcc-5ef6-80f5-1c90d76fc2c3 | note | Punch List closed out in a timely mannor
c028214a-51a4-4d71-b465-3605b94a88ea | checkpoint | Documentation
03dc73d1-9cd8-5774-a21d-c47851112407 | note | On completion of the Light Pole foundations:
6e344650-9945-57c1-a615-b823f43c0ff7 | note | Submission of all test results, ITC's and any as-built drawings
b11063b3-b7b1-591c-8ffb-87d93d63d6b1 | note | Complete and approved by client
15f9688a-1e21-4961-8f99-b7cb420fa77a | signoff | United Civil Hold Point
7764bff6-43ab-4953-be92-49cc8d2044e7 | checklist | Ω (DEPRECATED) ITP - Accessways (v0) | itp | Accessways
eb44411e-7358-4f2c-a007-7b9ede5805e6 | section | Preconstruction
f0b19fe1-3d53-4b4a-b100-c8b48f75002c | checkpoint | Design
6b98d0ad-8ae1-5108-9935-cb9a89121bc6 | note | Issued For Construction Drawings:
91f65b03-5f68-5032-b750-db71d7a41a6e | note | MSF-EN-CIV-DRG-510
9df10d6d-b9f8-5651-9016-fa4888f52a93 | note | MSF-EN-CIV-DRG-511
24c3d089-3bd2-55f0-8a9a-a6847102203e | note | MSF-EN-CIV-DRG-512
e3ec4cdd-21c6-5698-b342-b66f0097d92b | note | MSF-EN-CIV-DRG-590
acc871ab-4f6e-5110-8a46-ed2ea77fb990 | note | KDC EES2011
789b6101-2934-4995-915b-d84e6fbacbae | checkpoint | Survey & Setout
94103601-f42f-5db8-9d52-dd2f121979f8 | note | Issued For Construction Drawings
79123cde-23d9-5856-af07-cc5663029d53 | note | KDC EES2011
34b14c6c-1a18-40e2-8490-cd85a6cb9fb4 | section | Material Procurement
b51652d0-f9f9-4285-aaa3-53f617f7ae95 | checkpoint | Granular Fill Material for subgrade improvement (If Required)
26a91109-7d97-5eff-9b59-32afdd8915cf | note | Issued For Construction Drawings
a43eb1b5-f5a7-5d71-a45a-f368a329a8d2 | note | Delivery Dockets if Imported Granular Fill from Offsite is Used
1875ad4b-b9f3-547a-b3d4-9868f38e8672 | note | Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite
f5eb650b-7d7a-4fd5-bcfe-c02f1a8d65df | checkpoint | Drainage Pipe
33a1658f-feb2-5ac9-8e78-46fbf5c179e1 | note | IFC Drawings
cc1f2aff-4625-5a9a-ab32-630c68ef7a9d | note | Manufacturers Specifications
e1bf37cc-3dc8-5c4c-ad43-6b9ec96f4c9b | note | KDC EES2011
c47e58c3-9271-5ecb-803d-5111f0838a13 | note | Delivery Dockets
3a30820f-c2cf-589e-b8c8-2691db06e2b9 | note | Visual Inspections
1683c8f3-93e8-4f82-aa11-03e826e78d45 | checkpoint | Drainage Bedding Material
fc1c298b-c2fb-5dd4-b292-77e02a5e6cca | note | IFC Drawings
c1f66b3b-952c-5e13-9358-a02a11251b9e | note | KDC EES2011
83c44c81-8d67-5bd7-9988-b15b04b5c28d | note | Delivery Dockets
25c90b0f-b24e-41f8-9984-581b7f18aee1 | checkpoint | Gap 65 Subbase Material
f1aed3b5-e8e9-593f-81b6-8ce2ed5e48b3 | note | Issued For Construction Drawings
5e90003e-769a-5c09-bda9-2063d1243487 | note | MSF-EN-CIV-DRG-020
fbb929b0-e819-555c-ae23-ec0bdc7e3e1c | note | Delivery Dockets
84143a42-41fe-41b1-8d2d-a115af5eec4d | checkpoint | Gap40 Basecourse Material
646cd695-8c89-5334-a876-2328fa54eda1 | note | Issued for Construction Drawings
5595ae99-7a76-4399-9876-733188a71f6a | section | Construction
c9fca17f-af4e-4b46-b54c-b7db6aed9db3 | checkpoint | Inspect Subgrade layer and Check Subgrade Strength
d7a656ba-8d74-52b7-ace0-14c6e034aba8 | note | Issued for Construction Drawings
4890f3c5-ef28-59d1-b2a8-18855d7e163a | note | Visual Inspection
2d630f4a-4551-5353-ae4a-01ca87c0c315 | note | Scalar Penetrometer with results recorded of No of blows per 100mm on ITC
31c29654-5b2d-4272-8b69-ab512d85be08 | checkpoint | Drainage Culvert Installation
72033076-ab35-50de-98c7-f96962d44074 | note | IFC Drawings:
3a42cb8a-8b5c-5a46-93d3-e566348d69b3 | note | MSF-EN-CIV-DRG-310
8a7498c3-36e1-5e1a-b81c-498fdcbb2c99 | note | MSF-EN-CIV-DRG-311
f8391e5b-6905-5f1c-926f-50cd423a6344 | note | MSF-EN-CIV-DRG-312
075f95d4-8c07-5d33-8a8c-9723c196f899 | note | MSF-EN-CIV-DRG-313
4af014fb-eca5-5333-b87f-319e40e1b1d5 | note | KDC EES2011 S06
b3f7a670-47f3-5a90-9e69-2932f800bb6e | note | Visual Inspection
ff7e6c06-aea3-5393-b4c2-d326e1aac559 | note | Meets requirements of Issued For Construction Drawings & KDC EES2011 S06
c6fec8aa-2f99-5cdc-adb4-f382bfc69948 | note | ITC - QF008 Pipelines
77840656-7cd5-4495-97cf-dfbe4866881b | checkpoint | 300mm Granular Material
62fe8a47-3387-564c-92c3-659a574a2dac | note | IFC Drawings
ced8b997-2eff-5ccc-bce0-8e2b5dd46985 | note | KDC EES2011
00825d5b-0279-5363-9254-be3ee07e27c2 | note | Check granular layer is minimum of 300 thick. Take photos and measurements
923a7538-16e8-4b46-982f-c12cbc6c38c7 | checkpoint | Gap 40 Basecourse Construction
274fb8e6-0447-5888-8768-f39445922bab | note | IFC Drawings
c789ec65-0c02-5083-a389-4a814e6a24ac | note | KDC EES2011
ff769968-93b8-5f94-b646-5d6b3594a8f3 | note | Visual Inspection
9904891e-6094-5613-bae6-02d32156d581 | note | Clegg hammer reading of >25 recorded onto QF022 Clegg Hammer Test Report
60558203-6883-48f3-b1d2-0dc94f796c3a | section | Close-Out
b8e2bf98-e339-4e4d-9861-9cf797cee585 | checkpoint | Non-Conformance-Reports
d8678374-ca06-5b0e-87b3-e87e30b0637f | note | Non-Conformances Closed Out
4dbf2774-f95c-445e-9911-2773d7d7f8f7 | checkpoint | Handover
de7b20e0-27b0-5779-a9bc-12cf6cfa5df8 | note | At completion of works QA/QC Pack is handed to client
9e9faa7a-803d-5007-9d52-99b6c71222bb | note | Client Verifies Work has been completed correctly and all quality documents are in order
9b42f0b3-df03-4035-ae5b-572231961d30 | signoff | HOLD POINT
de3c1bbb-f660-42cc-9b37-55c300b0e3f3 | checklist | Ω (DEPRECATED) ITP - Inverter Foundations (v0) | itp | Inverter Foundations
59a0ec18-7bed-434b-ac60-312a9296b0b8 | section | Preconstruction
eb2dd0be-505d-4ab5-bd90-96c3113ec6e6 | checkpoint | Design
b56a07fd-73c8-5512-ae0e-8c9dac5ca9bb | note | Issued For Construction Drawings MSF-EN-CIV-DRG-910
00924679-d926-4775-9355-f35bf416ab48 | checkpoint | Survey & Setout
6c2b39c6-98b6-5fcf-9673-cabb6133048d | note | Issued For Construction Drawings MSF-EN-CIV-DRG-910
bc233d78-f462-4e11-9209-e6b744faf3d1 | section | Material Procurement
e05fc5f8-be18-4fe3-8a14-a8a2378c9520 | checkpoint | Structural Steel
74f9c0da-d98e-5aeb-b0e8-d470d62fa7e2 | note | Issued For Construction Drawings
a99459bb-db23-5497-b498-c541fc840107 | note | Manufacturers Documentation
d612e0d8-a21a-5906-88b8-6fc5bc7e9605 | note | Inspection Records
31f6712a-096c-5d2e-9645-aaf1d12e7ac4 | note | All reinforcing bars shall be Grade 300E to AS/NZS 4671 as shown in IFC Drawings NZS3109/3112
987f8e1a-755b-53b7-9cea-ef900e20213b | note | All reinforcing and formwork to comply with IFC drawings
f59d4451-aca6-4d6e-adee-11288440cd46 | checkpoint | Concrete
eaf7c8e9-ac7d-59cd-beb8-63a8e1bd175a | note | Concrete shall be 30MPa Minimum Strength for precast elements
15d1d4b5-d153-4fbb-a6f0-de62af57e92b | section | Construction
bb3f0ea7-3b51-4840-bde2-3afcf9fd6814 | checkpoint | Excavation of Foundation
1a5da599-70e6-56fa-aaf2-b751bfdcb073 | note | Issued for Construction Drawings
5ed13c5d-795f-5d31-8dd3-76a82d0bab11 | note | Remove topsoil back to subgrade material and place in suitable storage location with silt controls
bd95f6a1-d875-565b-92f9-57f297119dbe | note | Foundation excavated to line and level shown in IFC Drawings
4db4c888-08af-5d3d-abc9-09f45ebb345c | note | Scalar Penetrometer test results recorded on Checksheet
e6987a3d-f17a-4f96-aaec-937c56895840 | checkpoint | Compacted Harfill under Inverter Foundations
25bcec1e-dcf3-566c-95ca-1539c52c2e07 | note | Issued for Construction Drawings
e9b8aed0-b631-51e1-9d5f-71bd9b204446 | note | 200x800 Compacted Hardfill Pad under footings
a505b5c4-c886-587d-b2b2-c2477c6cfff2 | note | Results Recorded on Clegg Hammer Checksheet
17794923-7566-4060-ae74-d10c0d99878e | checkpoint | Concrete
37908c62-1c0b-5b94-a290-3e7f71a2de31 | note | Lines, levels and dimension as per Issued for Construction Drawings MSF-EN-CIV-DRG-910
fa3e9e98-aa58-5224-9357-6692c70bde46 | note | Concrete to be min 30MPa at 28 days
921278a0-e6e7-5019-9ffe-592f6d46bb35 | note | Test cylinders taken
9ba80f64-fbd7-590d-b055-10efb88a50cb | note | Dimensions to match IFC Drawings with tolerance of +/- 1mm
c9090453-e3a5-5d85-8f00-69f9783809b6 | note | 50mm minimum cover to steel
a420436d-0276-5475-803a-fde1674bd17c | note | Prepour Inspection Record completed prior to pouring
01c9fc68-9a61-4f34-8739-aefbe53b320f | checkpoint | Placement of Concrete Elements
64749212-9f2e-52c9-bb18-f4e520ce19b9 | note | Lines and levels as per Issued for Construction Drawings
507834a2-6053-51f2-ab4e-82d09c47c000 | note | Use drypack for installation of inverter if required with min thickness of 20mm
4ea374b0-96d4-5dca-8614-eea13a470555 | note | Middle block must be setup for container to sit fully on level and true
3db2480f-eeba-55d6-ba28-8f1655f7f8d7 | note | The outside blocks shall be set lower than the centre block
8ab61453-d374-4b35-a3b3-3f098aeea3e4 | checkpoint | Backfill
a539dd9a-03fe-54c5-96fa-7d3eaf3fc273 | note | Issued for Construction Drawings
aed4fbf8-bbdf-5229-be8b-edaa747d8681 | note | Sand Backfill to be watered and compacted in by mechanical means to provide backfill and support around the foundations without voids or areas of non-compaction
c4099739-fe37-4d18-8b8e-c1086c3591bf | section | Close-Out
f4d99418-1283-4aa3-824d-4f08dd620254 | checkpoint | Asbuilt Recording
b54dfc68-2789-5c6a-a4c8-332b5222cb31 | note | Asuilt records supplied of inverter foundations in place
d3d95e49-335d-4fc9-9e6e-7f6615782a7d | checkpoint | Non-Conformance-Reports
3df03fa2-d666-5eb6-a8f9-27e0ef42f3dd | note | Non-Conformances Closed Out
74b7aa2b-6c09-4428-af8d-938e940f06a7 | checkpoint | Handover
6431aa81-5311-54cd-b718-cdc51e6a5ba9 | note | At completion of works QA/QC Pack is handed to client
c86bdd48-dcc2-530c-95e9-496ba70b9da3 | note | Client Verifies Work has been completed correctly and all quality documents are in order
0167b8f0-2878-41bd-ad24-9def06d3f6c5 | signoff | HOLD POINT
4553f8ca-75ef-457a-b3e7-dca763385291 | checklist | Ω (DEPRECATED) ITP - Laydowns (v0) | itp | Laydowns
be5ca94f-622c-4646-b293-242c1b81e7bf | section | Preconstruction
9d8b0d70-4dfc-481a-9c10-2ce88aabe462 | checkpoint | Design
c628de2f-de23-5213-a5dc-7d90ed6a618b | note | Issued For Construction Drawings
11285c88-5e2c-42ed-87f5-081405efa843 | checkpoint | Survey & Setout
2dc701fc-0576-518e-b33a-c7dd60f9de04 | note | Issued For Construction Drawings
f1fbb0e5-0369-54f1-a9bc-0f1884c738df | note | Agree and Confirm Locations and Areas Onsite
0d9c17d5-da0c-4679-abcd-5490a7773a0e | section | Material Procurement
d05d1f64-48f7-422e-9bfe-c85da59d7fe9 | checkpoint | Granular Fill Material for subgrade improvement (If Required)
f86b0c34-d475-5ebd-8337-a49996dc4e9b | note | Issued For Construction Drawings
20224b78-a6a9-5994-9ff1-c8950e8d2909 | note | Delivery Dockets if Imported Granular Fill from Offsite is Used
3c505003-042e-5453-9d86-67e5dbeffbf5 | note | Photos if sourced from Onsite Quarry or Delivery Dockets if Sourced Offsite
660aaeb6-bba2-4b24-8a3a-8ff6b6186fab | checkpoint | Gap 65
7c012d0f-600d-55dd-9e2c-dad2fdd19028 | note | Issued For Construction Drawings
244de326-152d-5ef1-bbe5-99d133aca03f | note | MSF-EN-CIV-DRG-020
89611d25-8b76-50f5-924d-252cf61b8e7a | note | Delivery Dockets
0bc62211-51e3-4df3-9132-ec41c6220232 | section | Construction
928f2289-e3d2-4f6f-ad13-4ea5b8055516 | checkpoint | Inspect Subgrade layer and Check Subgrade Strength
7cdac74e-84c1-5dc4-bd2d-11495d689dde | note | Issued for Construction Drawings
cb9b35fc-e053-538e-b616-bf47fa83ae90 | note | Visual Inspection
c1bbad87-deee-5ca8-8e85-7ac754cb9a80 | note | Scalar Penetrometer with results recorded of No of blows per 100mm on ITC
961df082-a9b5-4d52-8c17-b781abf48ead | checkpoint | Granular Fill Construction As Required
eb0af80b-bf17-5e3e-89ea-393e8fe601ef | note | IFC Drawings
33db383b-1c05-50fa-ae62-f6c36e2df4af | note | Visual Inspection of completed Gap65 after light rolling
6c03afef-6373-4710-b43c-c7b188c8bcea | checkpoint | Gap 65 Construction
8a34dab8-03c3-583d-9399-19327a52ebe0 | note | IFC Drawings
371e5d43-f947-5277-a4e4-529e8d67942d | note | Visual Inspection
378e0697-60d8-5074-b03e-a232020efde8 | note | Proof Rolling
29662279-38cb-4e68-86f1-e4c6ee11a9f8 | signoff | HOLD POINT
ff74ccdd-b836-46af-8b00-f120f5673eae | section | Close-Out
df20b992-26b4-47ea-b87e-d352794f3444 | checkpoint | Non-Conformance-Reports
fa384922-93a6-5ff5-abf8-c8864da4413e | note | Non-Conformances Closed Out
ba7b12c1-c615-40a1-bdfb-aa6be7f39ebb | checkpoint | Handover
b71c06d6-55bc-5800-9e1f-51a20bc9e7e5 | note | At completion of works QA/QC Pack is handed to client
260a3ad6-a6ac-5478-81c4-3a3b9543cfdd | note | Client Verifies Work has been completed correctly and all quality documents are in order
968fda64-b812-4de1-832a-2aac68fa0305 | signoff | HOLD POINT