## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | RMU2 Building Drainage ITP | itp
section | Location
checkpoint-no-status | Drainage Location
textbox | Location of Installed drainage
section | Preconstruction
checkpoint | Design Drawings
label | Issued for Construction Drawings available
holdpoint | United Civil Hold Point
checkpoint | Site Preparation
label | Visual inspection of cleared and levelled area
label | Site free from debris, vegetation, and unevenness
checkpoint | Survey and Marking
label | Verification of layout and drain alignment & grades
label | Alignment with approved IFC drawings
label | Local site datum found, marked & protected
section | Wastewater Construction & Installation
checkpoint | Material Approval
label | Review and approval of pipes, culverts, and other materials to comply with IFC drawings and specifications
label | Wastewater pipework shall be DN100 PN12 PVC-U, all fittings shall be rated & compatible with the pipe
label | Wastewater tank shall be a Promax Enduro 5000L Septic Tank
label | Material test certificates and or delivery dockets attached
holdpoint | CHINT / United Civil Hold Point
checkpoint | Excavation
label | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework to comply with IFC Drawings
label | Depth, dimensions, and cleanliness checked and maintained
checkpoint | Soil Stability
label | Inspection of trench stability and shoring/battering/benching is installed where necessary
label | Stable and safe for pipe and tank laying
checkpoint | Pipe Installation
label | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
label | Pipes to have 75mm of Gap7 bedding and top cover
textbox | Wastewater pipe grade installed to
label | ITC Completed for pipe installation
holdpoint | United Civil Hold Point
checkpoint | Tank Installation
label | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
label | Tank to sit on 100mm of compacted gap20 then be backfilled with Pap7 to the pavement layers
label | Tank half filled with water before backfilling
holdpoint | United Civil Hold Point
checkpoint | Backfilling
label | Visual inspection of backfill material and compaction
label | Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
label | Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
label | ITC Completed for Compaction Testing
holdpoint | United Civil Hold Point
checkpoint | Hydrostatic Test
label | Visual Inspection of hydrostatic leak test being performed
label | Hydrostatic pressure testing of pipes for leakage As per NZS4404 Appendix C
label | Leakage/make up water does not exceed 0.5L / Hr per metre length per metre diameter (0.5 * 5.5 * 0.1 = 0.275 L / Hr)
label | Hydrostatic test holds and passes
holdpoint | CHINT / United Civil Hold Point
section | Subsoil Pipe Construction & Installation
checkpoint | Material Approval
label | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings
label | Subsoil pipe shall be 110mm dia Novaflo subsoil drainage pipe with geotextile sock surrounding
label | Material Test Certificates / Delivery Dockets attached
holdpoint | CHINT / United Civil Hold Point
checkpoint | Excavation
label | Visual inspection and measurement of trench to comply with IFC Drawings
label | Depth, dimensions, and cleanliness checked and maintained
checkpoint | Soil Stability
label | Inspection of trench stability and shoring/battering/benching is installed where necessary
label | Stable and safe for pipe and tank laying
checkpoint | Pipe Placement
label | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
label | Subsoil pipe to have a 1% grade to outlet
holdpoint | United Civil Hold Point
section | Stormwater Construction & Installation
checkpoint | Material Approval
label | Review and approval of pipes, culverts, and other materials to comply with IFC Drawings and Specifications
label | Pipework shall be DN90 SN4 PVC-U, all fittings shall be rated & compatible with the pipe
label | Stormwater Channel to be lined with Bidim A19 Filter Cloth
label | 150x50 H4 Radiata Timber edging for the water tank surround
label | Material test certificates and or delivery dockets attached
holdpoint | CHINT / United Civil Hold Point
checkpoint | Excavation
label | Visual inspection and measurement of trenches with minimum of 600mm cover maintained for all pipework
label | Depth, dimensions, and cleanliness checked and maintained to comply with IFC Drawings
checkpoint | Soil Stability
label | Inspection of trench stability and shoring/battering/benching is installed where necessary
label | Stable and safe for pipe and tank laying
checkpoint | Pipe Installation
label | Visual Inspection of pipe placement, alignment, and bedding to comply with IFC Drawings
label | Pipes to have 75mm of Gap7 bedding and top cover
label | ITC Completed for Pipe Installation
holdpoint | United Civil Hold Point
checkpoint | Tank Installation
label | Visual Inspection of tank placement, alignment, and bedding to comply with IFC Drawings
label | Tank to sit on 150mm of compacted Gap40 and 100mm of compacted sand
label | Compliance with approved IFC Drawings
holdpoint | United Civil Hold Point
checkpoint | Backfilling
label | Visual inspection of backfill material and compaction
label | Pipe Compaction as per Typical Section - RMU2 Pipe Bedding - Gap7 then Gap65 to a CIV of >20
label | Compacted backfill thickness to be a minimum of 600mm including the overlaid pavement
label | ITC Completed for Compaction Testing
holdpoint | United Civil Hold Point
section | Post Construction and Handover
checkpoint | Material Approval
label | Final Walkthrough & Inspection
label | Comprehensive inspection of all elements relating to the RMU Drainage
label | Compliance with IFC drawings and specifications
label | Verify all Drainage meets design and functional requirements
holdpoint | CHINT / United Civil Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely mannor
checkpoint | Documentation
label | On completion of the RMU Drainage
label | Submission of all test results, ITC's and any as-built drawings
label | Complete and approved by client
holdpoint | CHINT / United Civil Hold Point