## HV
|  |  |  | Process Control Plan |  |  | Approved |  | Signature
|  |  |  | Contract Name: | Ponsonby_Pompallier Pedetrian Improvement |  | FH Engineer
|  |  |  | Procedure: | Ducting and Streetlight Installation |  | FH Project Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding SWMS: |  |  |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | W | Obtain Permits | As required | Document Review | Control Checklist - Digging / Excavating (incl. marking out & potholing existing services). Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
2 | Traffic Management | W | Ensure TMP is approved and check that the requirements are correctly interpreted and understood by the STMS | Prior to commencement | Document Review | TMP is approved by AT for the site and works are completed within the approved dates | TMP on MyWorksites/ On Site | Site Engineer
3 | Pre-construction sign offs | W | Ensure that Sub-Contract and Supplier Agreements are signed and that personnel have gone through the NWBI induction. | Prior to commencement | Document Review | Signed subcontract & Supplier agreements. Issued induction stickers and number | Signed Agreements, Updated Induction Register | Site Engineer
4 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | IFC label on drawings | Check Drawing Register | Site Engineer | Engineer's Rep / MSQA
5 | Survey Setout | W | Setout ducting alignment and Street light locations. Setout and mark all known services along the cable corridor. | Prior to commencement | Survey |  | Survey Records Services Ducting Checksheet | Site Engineer
6 | Locate existing services by hand digging/ hydrovac | W | Ensure all services conflicting with the line of trench has been exposed by hand digging | Prior to Installation | Potholing | All conflicts have been located | Digging/Excavating Permit, Service Ducting Checksheet | Site Engineer
7 | Material Compliance | H | Ensure bedding and cover material is as per vector specifications | Prior to commencement | Document Review | Crushing Resistance not less than 100kN. Maximum percentage of weight passing 0.075mm sieve shall not exceed 10% | Test Report | Site Engineer | Engineer's Rep / MSQA
|  | H | Ensure duct pipes are as per drawings & spec. | Upon delivery to site | Ensure delivery docket matches materials | Vector requirements as per ESE303, EDE3020, EDE3024 | Delivery Docket, Vector Specifications, Services Ducting Checksheet | Site Engineer | Engineer's Rep / MSQA
8 | Trenching | M | Inspect trench profile to ensure vertical depth and trench widths as per vector specifications EDE 3024 and EC-21-ACIP4-304 (900mm min cover and 650mm min. trench width for two ducts and 350mm min. trench width for singular ducts) | 10m Intervals | Visual Inspection | Ensure trench profiles conform with corresponding vector specifications EDE 3024 and EC-21-ACIP4-304 | Vector Specifications, Services Ducting Checksheet | Site Engineer
9 | Bedding | H | Bedding depths for Ducting as per vector specifications EDE 3024 and EC-21-ACIP4-304. | 10m Intervals | Visual inspection | As per vector specifications EDE 3024 and EC-21-ACIP4-304 | Vector Specifications, Site Photos, Services Ducting Checksheet | Site Engineer | Engineer's Rep / MSQA
10 | Warning Tape and Polymeric Slab | H | Install Marker tape at 50% depth of duct cover or as per utility owners specification. | 10m Intervals | Visual inspection | Vector specifications as per EDE3021 | Vector Specifications, Site Photos, Services Ducting Checksheet | Site Engineer | Engineer's Rep / MSQA
11 | Backfill/ Compaction (also refer to specific utility owners requirements) | H | Depth Range >1m Carriageway GAP40, max. compaction layer 200 mm, as per TNZ B/2 Specification, CIV >=30 Depth Range >1m - outside 1m from Kerb Selected backfill, max. compaction layer 200mm, as per TNZ B/2 Specification, CIV >=20 | 10m Intervals | Lab/ testing | Pass Test Results | Test Records/QA Sheets, Services Ducting Checksheet | Site Engineer | Engineer's Rep / MSQA
12 | Assemble & Install Street Lighting Column | W | Confirm column type, height and outreach arm correct for location as per AS/NZS 1158 | Before Column Installed | Document Review | As per vector ATCoP Street Lighting | This ITP | Site Engineer
|  | W | Luminaire types as detailed on drawings | Prior to supplying to site | Document review | Refer to IFC Streetlight Drawings | Delivery dockets | Site Engineer
|  | W | Strretlighting to be position no more than 1m away from face of kerb to face of column | Column Installation | Visual Inspection | As per vector ATCoP Street Lighting | This ITP | Site Engineer
|  | W | Foundation to be excavated as per manufacturer specification for ground planted columns | Column Installation | Visual Inspection | As per vector ATCoP Street Lighting | This ITP | Site Engineer
|  | W | Backfilling with granular or concrete as per manufacturer specs | Column Installation | Visual Inspection | Refer to IFC Streetlight Drawings | This ITP | Site Engineer
|  | W | Confirm column is bolted to base stub as per Manufacturer's Instructions | Column Installation | Visual Inspection | Refer to IFC Streetlight Drawings | This ITP | Site Engineer
13 | Tud/Pit/Chamber Installation | H | Where needed, Ensure TUDs/pits and chambers are installed in the correct locations at asset owner's instruction to manufacturer and asset owner specifications | During Installation | Site Inspection/Design Review | Sign off and approval by asset owner/MSQA | Site Photos/ Checksheets | Site Engineer | Engineer's Rep / MSQA / Vector or Northpower Rep
14 | Commisioning | H | Ensure that certification, testing and commissioning undertaken according to Utility Service Provider's guidelines. After livening a test sheet recording the measured voltage at each light and each circuit current is required. | Post Installation | Document Review | Commisioning completed by vector authorities for Certificate of Compliance and Record of Inspection before operational sign off | Test Certificates, COCs and ROIs | Site Engineer | Engineer's Rep / MSQA / Vector or Northpower Rep
|  | W | Equipment labels for Poles, Lighting Supply Boxes and internal equipment installed | Post Installation | Visual Inspection | All relevant labels placed | Photos,This ITP | Site Engineer
15 | As-builts | H | Cable installation records, Electrical test records, materials and equipment schedule, Survey As-Built | At the completion of the Lot of work | Drawings/Documents |  | Survey Asbuilt Documents | Site Engineer | Engineer's Rep / MSQA
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices etc.):
| QA Compiled By: |  |  |  | Signature: |  |  | Date:
| QA checked By Project Manager: |  |  |  | Signature: |  |  | Date:
| Accepted By Design Engineer: |  |  |  | Signature: |  |  | Date: