## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | Stormwater Drainage | [5 empty] | Ponsonby - ITP - Stormwater Drainage
checkpoint | 1 - Permits
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Obtain Permits
note | Frequency - As required
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Control Checklist - Digging / Excavating (incl. marking out & potholing existing services). Notify Worksafe NZ if required.
note | • Ensure all necessary Permit to Works & Controlled Checklists are in place
note | Records - Permit attached or permit number noted
checkpoint | 2 - Traffic Management
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Ensure TMP is approved and check that the requirements are correctly interpreted and understood by the STMS
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - TMP is approved by AT for the site and works are completed within the approved dates
note | Records - TMP on MyWorksites/ On Site
checkpoint | 3 - Pre-construction sign offs
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Ensure that Sub-Contract and Supplier Agreements are signed and that personnel have gone through the NWBI induction.
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Signed subcontract & Supplier agreements. Issued induction stickers and number
note | Records - Signed Agreements, Updated Induction Register
checkpoint | 4 - Design
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Ensure that Design is approved and Drawings are of the latest revision
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - IFC label on drawings
note | Records - Check Drawing Register
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5 - Survey Setout
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Set out pegs installed every 10m of the footpath showing the FL.
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Survey
note | Records - Visual Inspection
checkpoint | 6 - Material Compliance
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Bedding, Haunching and Backfill Material
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - AS/NZS 3725, AS/NZS 3500.3
note | Conformance Criteria - Crushing Resistance not less than 100kN. Maximum percentage of weight passing 0.075mm sieve shall not exceed 10%
note | Records - Test report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7 - Pipes and Precast Units
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
note | Frequency - Delivery to site
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - Pipe - Diameter & Class, Manholes, Catchpits as per SW CoP and AS/NZS 3725
note | Records - Delivery Dockets
checkpoint | 8 - Trenching and Excavation
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Inspect trench profile and ensure it is correct to lines and levels to design
note | Frequency - Daily
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - Line and level is correct
note | Records - Checksheet
checkpoint | 8 - Trenching and Excavation (2)
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Ensure trench width is sufficient as per AS/NZS 3725 namely 3x Diameter of Pipe
note | Frequency - Daily
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - As per AS/NZS 3725
note | Records - Checksheet
checkpoint | 9 - Foundation Compliance
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - As per specification, Shear Vane <50 KPa 2%<CBR<3% Undercut 150mm, CBR<2% Seek Design Engineer's advice
note | Frequency - 1 Test every 20m
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Testing
note | Conformance Criteria - Shear Vane >50 Kpa, CBR > 3%
note | Records - QA Sheets
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10 - Undercut Backfill Material Compliance Testing
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Undercut If subgrade fails testing requirements and replace with copmpacted GAP40 for depth of undercut
note | Frequency - 1 Test every 20m
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Testing
note | Conformance Criteria - CIV> 15
note | Records - QA Sheets
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 11 - Pipe and Structure Bedding
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Specified Bedding Construction Material
note | • Pipe Diameter<300mm bedding, side and haunch zones to be 100mm
note | • Pipe Diameter >300mm bedding, side and Haunch zones to be 150mm
note | • Stucture Bedding to comprise of a 75-100mm levelling course GAP20
note | Frequency - 1 Test every 20m
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Testing
note | Conformance Criteria - As per AS/NZS 3725 Minimum Bedding, Side and Haunch Zone CIV > 15
note | Records - Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Structure and Pipe Backfill
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Backfill zone compacted in GAP40 layers no greater than 200mm .
note | Frequency - Test Per Structure
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Compliance with requirements from Specifications and SW CoP.
note | ○ Under Carraigeway
note | • CIV >=32
note | ○ Under Footpath and Berm
note | • CIV >=25
note | Records - Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 13 - Pipe Laying
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place and sealed.
note | • Ensure Pipes do not exceed ±25 mm from design levels for any five metres of pipe
note | Frequency - Prior to backfilling
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - No defects/ gaps / pipes are aligned correctly. Compliance with the Stormwater Contract specification
note | Records - Photos, Checksheet
checkpoint | 13 - Pipe Laying (2)
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - As-built survey of pipes installed
note | Frequency - Once line is completed between 2 structures
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Survey
note | Conformance Criteria - Survey Receipts
note | Records - Checksheet
checkpoint | 14 - Trench Overlay Zone
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Ensure correct thickness of compacted overlay zone - 150mm overlay above top of pipe for Pipe Diameter between 300 and 1500mm
note | Frequency - During Backflling
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - Compliance with the drawings . 150mm overlay above top of pipe. Refer to AS/NZS 3725
note | Records - Checksheet
checkpoint | 15 - Pipe Backfill Compliance
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Backfill zone compacted in GAP40 layers no greater than 200mm . Requirements based on pipe location. Minimum cover 1200mm from top of pipe in carraigeway and 800mm in berm. If Cover cannot be achieveded seek advice from design engineer
note | Frequency - 1 Test every 20m
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review & Testing
note | Conformance Criteria - Compliance with requirements from Specifications and SW CoP.
note | ○ Under Carraigeway
note | • >=95% Compaction and CIV >=32
note | ○ Under Footpath and Berm
note | • >=85% Compaction and CIV >=25
note | Records - Checksheet, Lab Report, QA Sheets
checkpoint | 16 - Structure installation (Manhole, Catchpit)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Galvanised Step irons required in chambers over 1500mm deep
note | Frequency - As required
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - Maximum 600mm from manhole frame to first rung. Maximum 300mm between rungs. As Per ATCoP
note | Records - Photos
checkpoint | 16 - Structure installation (Manhole, Catchpit) (2)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Structures to be installed to the design survey location and level
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - Survey markouts for centre of structure and insatllment to be from centre of structure
note | Records - Checksheet
checkpoint | 16 - Structure installation (Manhole, Catchpit) (3)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - All joints are to be sealed including rungs and lids
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - 25 MPa concrete to be used for throat haunching and cradle around inlets an outlets
note | Records - Photos
checkpoint | 16 - Structure installation (Manhole, Catchpit) (4)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Adjustment rings to ensure correct level and fall to cover
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - Maximum throat depth on manholes to be 450mm. Miminimum riser usage is required and minimum riser height to be 300mm. All Joints between risers must be epoxied
note | Records - Photos
checkpoint | 16 - Structure installation (Manhole, Catchpit) (5)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Concrete benching
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection
note | Conformance Criteria - Benching at base of Manhole shall be formed with 25 Mpa concrete.
note | Records - Delivery Dockets
checkpoint | 16 - Structure installation (Manhole, Catchpit) (6)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Manhole covers & frames set to correct level
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection/ Check
note | Conformance Criteria - Heavy Duty Class E manhole covers required in trafficable areas as per AS 3996 400 KN rating
note | Records - Checksheet, Delivery Dockets, SW CoP
checkpoint | 16 - Structure installation (Manhole, Catchpit) (7)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Catchpit sump depth
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Measurement
note | Conformance Criteria - Minimum sump depth to 450mm as per AT CoP
note | Records - ATCOP
checkpoint | 16 - Structure installation (Manhole, Catchpit) (8)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Catchpit grate levels are set to correct level
note | Frequency - During structure construction
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual/Inspection/ Check
note | Conformance Criteria - Measure on site and must be Cycle friendly Class D lids as per AS/ 3996 rating 210 KN
note | Records - Checksheet, Delivery Dockets, SW CoP
checkpoint | 17 - CCTV
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - CCTV record at completion of trench backfill and prior to final surfacing
note | Frequency - At completion of the works
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection/ CCTV inspection
note | Conformance Criteria - No Defects
note | Records - Inspection Report CCTV
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 18 - As-builts
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Red pen mark up drawings to be included in QA file
note | Frequency - At the completion of the Lot of work
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Drawings
note | Records - Asbuilt Drawing
holdpoint | AUTHORITY HOLDPOINT