## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | Ducting and Streetlight Installation | [5 empty] | Ponsonby - ITP - Ducting and Streetlight Installation
checkpoint | 1 - Permits
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Obtain Permits
note | Frequency - As required
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Control Checklist - Digging / Excavating (incl. marking out & potholing existing services).
note | • Notify Worksafe NZ if required.
note | • Ensure all necessary Permit to Works & Controlled Checklists are in place
note | Records - Permit attached or permit number noted
checkpoint | 2 - Traffic Management
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Ensure TMP is approved and check that the requirements are correctly interpreted and understood by the STMS
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - TMP is approved by AT for the site and works are completed within the approved dates
note | Records - TMP on MyWorksites/ On Site
checkpoint | 3 - Pre-construction sign offs
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Ensure that Sub-Contract and Supplier Agreements are signed and that personnel have gone through the NWBI induction.
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Signed subcontract & Supplier agreements. Issued induction stickers and number
note | Records - Signed Agreements, Updated Induction Register
checkpoint | 4 - Design
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Ensure that Design is approved and Drawings are of the latest revision
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - IFC label on drawings
note | Records - Check Drawing Register
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5 - Survey Setout
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Setout ducting alignment and Street light locations.
note | • Setout and mark all known services along the cable corridor.
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Survey
note | Records - Survey Records Services Ducting Checksheet
checkpoint | 6 - Locate existing services by hand digging/ hydrovac
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Ensure all services conflicting with the line of trench has been exposed by hand digging
note | Frequency - Prior to Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Potholing
note | Conformance Criteria - All conflicts have been located
note | Records - Digging/Excavating Permit, Service Ducting Checksheet
checkpoint | 7 - Material Compliance
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Ensure bedding and cover material is as per vector specifications
note | Frequency - Prior to commencement
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Crushing Resistance not less than 100kN. Maximum percentage of weight passing 0.075mm sieve shall not exceed 10%
note | Records - Test Report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7 - Material Compliance (2)
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Ensure duct pipes are as per drawings & spec.
note | Frequency - Upon delivery to site
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Ensure delivery docket matches materials
note | Conformance Criteria - Vector requirements as per ESE303, EDE3020, EDE3024
note | Records - Delivery Docket, Vector Specifications, Services Ducting Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8 - Trenching
note | ACTION (Hold, Monitor, Witness) - M
note | Detail - Inspect trench profile to ensure vertical depth and trench widths as per vector specifications EDE 3024 and EC-21-ACIP4-304 (900mm min cover and 650mm min. trench width for two ducts and 350mm min. trench width for singular ducts)
note | Frequency - 10m Intervals
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - Ensure trench profiles conform with corresponding vector specifications EDE 3024 and EC-21-ACIP4-304
note | Records - Vector Specifications, Services Ducting Checksheet
checkpoint | 9 - Bedding
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Bedding depths for Ducting as per vector specifications EDE 3024 and EC-21-ACIP4-304.
note | Frequency - 10m Intervals
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual inspection
note | Conformance Criteria - As per vector specifications EDE 3024 and EC-21-ACIP4-304
note | Records - Vector Specifications, Site Photos, Services Ducting Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10 - Warning Tape and Polymeric Slab
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Install Marker tape at 50% depth of duct cover or as per utility owners specification.
note | Frequency - 10m Intervals
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual inspection
note | Conformance Criteria - Vector specifications as per EDE3021
note | Records - Vector Specifications, Site Photos, Services Ducting Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 11 - Backfill/ Compaction (also refer to specific utility owners requirements)
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Depth Range >1m
note | ○ Carriageway
note | • GAP40, max. compaction layer 200 mm, as per TNZ B/2 Specification, CIV >=30
note | ○ Depth Range >1m - outside 1m from Kerb
note | • Selected backfill, max. compaction layer 200mm, as per TNZ B/2 Specification, CIV >=20
note | Frequency - 10m Intervals
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Lab/ testing
note | Conformance Criteria - Pass Test Results
note | Records - Test Records/QA Sheets, Services Ducting Checksheet
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12 - Assemble & Install Street Lighting Column
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Confirm column type, height and outreach arm correct for location as per AS/NZS 1158
note | Frequency - Before Column Installed
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - As per vector ATCoP Street Lighting
note | Records - This ITP
checkpoint | 12 - Assemble & Install Street Lighting Column (2)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Luminaire types as detailed on drawings
note | Frequency - Prior to supplying to site
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document review
note | Conformance Criteria - Refer to IFC Streetlight Drawings
note | Records - Delivery dockets
checkpoint | 12 - Assemble & Install Street Lighting Column (3)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Streetlighting to be position no more than 1m away from face of kerb to face of column
note | Frequency - Column Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - As per vector ATCoP Street Lighting
note | Records - This ITP
checkpoint | 12 - Assemble & Install Street Lighting Column (4)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Foundation to be excavated as per manufacturer specification for ground planted columns
note | Frequency - Column Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - As per vector ATCoP Street Lighting
note | Records - This ITP
checkpoint | 12 - Assemble & Install Street Lighting Column (5)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Backfilling with granular or concrete as per manufacturer specs
note | Frequency - Column Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - Refer to IFC Streetlight Drawings
note | Records - This ITP
checkpoint | 12 - Assemble & Install Street Lighting Column (6)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Confirm column is bolted to base stub as per Manufacturer's Instructions
note | Frequency - Column Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - Refer to IFC Streetlight Drawings
note | Records - This ITP
checkpoint | 13 - Tud/Pit/Chamber Installation
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Where needed, Ensure TUDs/pits and chambers are installed in the correct locations at asset owner's instruction to manufacturer and asset owner specifications
note | Frequency - During Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Site Inspection/Design Review
note | Conformance Criteria - Sign off and approval by asset owner/MSQA
note | Records - Site Photos/ Checksheets
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 14 - Commisioning
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Ensure that certification, testing and commissioning undertaken according to Utility Service Provider's guidelines. After livening a test sheet recording the measured voltage at each light and each circuit current is required.
note | Frequency - Post Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Document Review
note | Conformance Criteria - Commisioning completed by vector authorities for Certificate of Compliance and Record of Inspection before operational sign off
note | Records - Test Certificates, COCs and ROIs
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 14 - Commisioning (2)
note | ACTION (Hold, Monitor, Witness) - W
note | Detail - Equipment labels for Poles, Lighting Supply Boxes and internal equipment installed
note | Frequency - Post Installation
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Visual Inspection
note | Conformance Criteria - All relevant labels placed
note | Records - Photos,This ITP
checkpoint | 15 - As-builts
note | ACTION (Hold, Monitor, Witness) - H
note | Detail - Cable installation records, Electrical test records, materials and equipment schedule, Survey As-Built
note | Frequency - At the completion of the Lot of work
note | Inspection / Test Method (Submission, Visual Inspection, Testing, Measurement, Review) - Drawings/Documents
note | Records - Survey Asbuilt Documents
holdpoint | AUTHORITY HOLDPOINT