## OHLE Structure Installation
ConQA Team Notes:
Document Title: |  | ITP-037-RAIL-OHLE Structure Installation
ITP Description: |  | OHLE Structure Installation
Discipline (e.g. CIV/STR/RAIL) |  | RAIL
Revision Number: |  | 1
Revision Date: |  | 2023-05-16
ITP prepared by: |  | Nikhil Siram
ITP approved for use by: |  | MRPA Quality Team
Special Notes to ConQA Team : |  | ITP to be used in Brunt Rd & Camms Rd Projects Only
Inspection & Test Plan - OHLE Installation
|  |  | Document No.: ITP-037-RAIL-Brunt & Camms-OHLE Structure Installation | [5 empty] | Revision: | 1
[9 empty] | Date: | 2023-05-16
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsible person | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Overhead Line Electrification | L1-CHE-STD-011(1) MEST 000002-02(1) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Structure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | VRIOGS 001 AS 4100 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Electrical Networks Standard Electrical Networks Principles and Performance | L1-CHE-STD-015(1) MEST 000002-06(1 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Fabrication of Steelwork | VicRoads Section 630 January 2023 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.5 | Structural Steel Work - Fabrication and Erection | AS 5131:2016 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Structural Steel Components and Fasteners | IFC Drawings | Fabricator is required to provide the Manufacturer's Data Record (MDR) for each component. Typically this consists of but not limited to: i. Completed fabrication ITP ii. Weld Procedure Specifications iii. Weld Procedure Qualifications iv. Welder Qualifications v. Material Certificates vi. Coating certificate(s) vii. Non-destructive Testing (NDT) Reports (if any) viii. As-built Drawings to demonstrate compliance with dimensional tolerances of structural steel Bolts, nuts and washers for Property Class 4.6 bolting shall be supplied in accordance with AS 1111 and AS 1112 Bolts, nuts and washers for Property Class 8.8 bolting shall be supplied in accordance with AS/NZS 1252. All bolts nuts and washers are hot-dipped galvanized. Collate: Structural Steel Quality Assurance Documentation. Attach: Collated QA documents in ConQA | Document Review | Where applicable/ Each element | HP | PE | ConQA Hold Point Release
2.2 | Bolted Connections Using Direct Tension Indicators (DTIs) | AS4100 Clause 15.2.5.3 (a) AS5131 Clause 8.5.7 (a) | Direct tension indicators (DTIs) shall not be used unless approved by the Nominated Authority and accompanied by: i. technical data sheet or information on the product | Document Review | Where applicable, once, | HP | Nominated Authority | ConQA Hold Point Release
2.3 | Overhead Wiring Small Parts Steel and conductor wires | Relevant MTM Standard Drawings | Overheading Wiring Small Parts Steel to be procured as detailed in the drawings and as per relevant MTM Standard Drawings. Deliveries are to be inspected to match the purchase order Attach: Purchase order/Delivery dockets/Certificate of conformity | Visual inspection and measurement | Upon delivery | IP | PE | This ITP Signed Off
2.4 | Grout | IFC Drawings | All grout under base plates shall be CONBEXTRA C or equivalent as approved. Approved grout to be Flowable shrinkage compensated with minimum 50 Mpa compressive strength. Enter: Teambinder Material Approval number [free text box] | Document review | Where applicable | HP | PE | This ITP / Material Approval
3 | Preliminaries - Procedures & Documentation
3.1 | Installation Methodology & Works Method Statement | AS5131 Clause 11.2.3 | Details of how the Structural & Architectural Steel will be Installed will need to be privided including the following: - Transported to site; - Handled on site; - Installation Procedure (subcontracor ITP's); Submission of Work Package Plan and MRPA approval and acceptance. Enter: WAP number [free text box] | Document Review | Prior to Works Start | HP | MRPA/CAT5 Engineer | This ITP Signed Off
4 | Pre-construction Activities
4.1 | Approval of IFC drawings | Contractor Design Management procedure | Ensure correct and most recent revision of IFC design drawings are used for construction. | Document/ Drawings Review | Prior to Works and at regular intervals. | HP* | MRPA/CAT5 Engineer | This ITP Signed Off
4.2 | Cantilever assembled. | Cantilever assembled as per IFC design. | Relevant checks followed and adhered to-Cantilever Fabrication Check sheet. Attach: Signed off Cantilever fabrication Checkshit | Visual Document Review | Each Task prior to works start. | IP | MRPA/CAT5 Engineer | This ITP Signed Off
5 | Construction Activities
5.1 | Mast istallation | IFC Drawings: | Mast installed as per IFC. Mast rake is as specified in the drawings | Measure | Where applicable | IP | PE | This ITP
5.2 | Cantilever installed. | Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1) | Work instructions in accordance to IFC design | Measure Visual | Each OHLE Structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
5.3 | Bearing type Joints TB Friction type joints TF | IFC Drawings | BOLTS DESIGNATED TB & TF ARE TENSIONED AS PER AS 5131 and Table 8.5.6 - Bolt mark ups (in case of partial tensionening) should be visible for inspection - DTI squirts are to be visible for inspection | Visual | Where applicable | IP | PE | This ITP Signed Off/Visible marks
5.4 | Install SPS to correct height / position relative to track | Design drawings, IFC cross sections &S tructure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | Ensure SPS is installed as per IFC design drawings/MTM design range. Supervision / checking to ensure that equipment is installed correctly. | Measure Visual | Each OHLE Structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
5.5 | Cantilever checked once installed. | Cantilever checked as per IFC design drawings/MTM design range.Completed check sheet.CAT5/OHLE/CHK002 | Supervision checking to ensure that equipment is installed correctly. | Measure Visual | Each OHLE Structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
5.6 | Base Plate Grout | IFC Drawings | Grout to be mixed as per manufacturer TDS. Grout to be poured under base plate as per IFC drawings. Grout over pour is to be 6mm and cover area with Nom 50mm offset around the base plate. | Visual | Where applicable | IP | PE | This ITP
5.7 | Installation of wire supports at the correct height and stagger. | Install as per design drawings. | Engineer checking to ensure that equipment is installed correctly. | Visual | Each OHLE BWA structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
5.8 | Install to correct tension | Install as per design, use span/ambient temp. tension charts. | Engineer checking to ensure that equipment is installed correctly. | Measure Visual | Prior termination | IP | MRPA/CAT5 Engineer | This ITP Signed Off
6 | Post-construction Activities
6.1 | Defects/Temporary Works | IFC wiring layouts, cross sections and design drawings. | Ensure all Defects/Temporary works are capture and closed out correctly. Defect list to be provided at the end of Occo identifying planned work to rectify Attach Design mark up, Defect list, temporary bond register, and approved TW design | Document Review Visual | Each OHLE Structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
6.2 | Relevant documentation readily available. (As-built Survey) | As built drawings and check sheets to accordance to MTM Design spec. | Ensure delivery of relevant documentation to client. As built drawings and check sheets.CAT5/OHLE/CHK/002 check sheets. . | Document Review Visual | Each OHLE Structure | IP | MRPA/CAT5 Engineer | This ITP Signed Off
6.3 | Non-conformance Report (NCR) Closure | MTM Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP | MRPA/CAT5 Engineer | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /