## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-010-003-002 ITP Retaining Wall 4 Watermain | itp |  |  |  |  | DN1210-SP2-010-003-002 ITP Retaining Wall 4 Watermain Rev 1
section | SECTION 3.0 - PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
checkpoint | 3.1 - Pipe Laying
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Watermain Construction Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Pipeline Pressure Testing
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Watermain Pipeline Pressure Testing Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - EF Weld Tests
label | Detail / Activity - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory)
label | Acceptance / Conformance Criteria - Passing result in accordance with ISO21751 (strip bend test) tested by an IANZ accredited laboratory.
label | Standard / Specification - ISO21751, TCC IDC, DS-7.6.4.b.ii, PS 22.9
label | Verifying Document - Laboratory Test Report
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Butt-Fusion pre construction weld test
label | Detail / Activity - One weld on the most common size of pipes used for the project.
label | ○ One weld on the thickest wall (highest PN) pipe
label | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode. WMS Report
label | Standard / Specification - PS 22.9.6 (a) ISO 13953 Standard
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Extent of Line Setout
label | Detail / Activity - Ensure line and level of Watermain has been marked out and agreed with Engineer in accordance with Watermain drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Pipe and fittings.
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings. 32735.02-WSP-DR-WAT
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.7 - Valves, Adaptors, Flanges, Caps and Fittings
label | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.8 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
label | Detail / Activity - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.9 - Bidim/Geogrid
label | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.10 - Pre-cast Manholes
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - 32735.02-WSP-DR-WAT
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.11 - KWIK Spacers
label | Detail / Activity - Confirm Specification and material in good condition. Spacers for DN315 pipe and DN560 sleeve.
label | Acceptance / Conformance Criteria - Model: HDXT43
label | ○ Height: 43mm
label | ○ Spacing: 1.5m
label | ○ Installation: Centred and restrained
label | Standard / Specification - Manufacturer’s Installation Guide. 32735.02-WSP-DR-WAT
label | Verifying Document - Photographic Evidence
label | Testing Quantity Required (based from schedule qtys) - Every spacer
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 3.12 - DN560 Sleeve
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the sleeves are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT (Sheet #0312)
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
section | SECTION 4.0 - PRE-CONSTRUCTION - MATERIAL TESTING
checkpoint | 4.1 - Material grading: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - Lab Test Report NZS 4407.3.8.1
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | ○ 0-400 - 2 tests
label | ○ 400-1,500 - 3 tests
label | ○ 1,500-4,000 - 4 tests
label | ○ >4,000 - 1 test for each additional 1,000m3
label | — Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Weathering index: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.3 - Crushing Resistance: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.4 - Maximum Dry Density and Optimum Water Content
label | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
label | Acceptance / Conformance Criteria - Report Value Only
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.5 - Material grading: Materials (GAP20/19mm chip/Sand SAP7)
label | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 85-100% passing
label | 9.5mm ¦¦ 25-55% passing
label | 4.75mm ¦¦ 0-10% passing
label | 2.36mm ¦¦ 0-5% passing
label | 0.075mm ¦¦ 0-2% passing
label | Standard / Specification - AS/NZS 2566.2, PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | 400-1500m3 ¦¦ 3 Test
label | 1500-4000m3 ¦¦ 4 Test
label | >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 5.0 - PRE-CONSTRUCTION - MATERIAL TESTING (Pipes)
checkpoint | 5.1 - Pipes (PE)
label | Detail / Activity - Manufacturer's record and location of extrusion plants.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Full Traceability information and certification of Material and resin.
label | Standard / Specification - PS-22.4.1 (d)
label | Verifying Document - Full Traceability information and certification of Material and resin. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - DN560 Sleeve
label | Detail / Activity - Butt fusion Weld 13 x 17m DN560 PN16 pipes into 210m string
label | Acceptance / Conformance Criteria - 95% tensile strength; welds aligned
label | Standard / Specification - NZS/AS 2033:1980; Appendix XXII(a)
label | Verifying Document - Butt Fusion Welding Record; Photos
label | Testing Quantity Required (based from schedule qtys) - Every Joint
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Valves, Adaptors, Flanges and Fittings
label | Detail / Activity - Have a pressure rating no less than the designed pressure.
label | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
label | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
label | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.4 - Fusion Joint Compatibility
label | Detail / Activity - Confirm pipe and fittings compatibility for fusion welding
label | Acceptance / Conformance Criteria - No defects, compatible resin types per NZS/AS 2033
label | Standard / Specification - NZS/AS 2033:1980, Clause 4.2
label | Verifying Document - Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 per material type
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - ENG
section | SECTION 6.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE INSTALLATION - Excavation and Laying
checkpoint | 6.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 6.2 - Undercut approval
label | Detail / Activity - Trench Foundation
label | Acceptance / Conformance Criteria - 300mm Max cut
label | ○ IFC Drawing Sheet 320
label | (Or)
label | ○ Engineers approval
label | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.3 - Undercut Backfill Compliance
label | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Visiual Inspection
label | Standard / Specification - IFC Drawing WST 0320
label | Verifying Document - Lab Test Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.4 - Bedding Zone Compaction Testing
label | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
label | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction - 85%MDD
label | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per SW Specification. One test per 10m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.5 - Laying of Pipes (DN560 sleeve and DN315 PE Pipe)
label | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings. Facing upwards
label | Standard / Specification - PS22.7.1 C
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.6 - Pipe Installation on Curved Alignments
label | Detail / Activity - All Industry Guideline PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
label | Acceptance / Conformance Criteria - AS Per POP 202
label | Standard / Specification - PS 22.7.1 D
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - M
label | ○ Monitor on Random Basis
label | Verification Activity: By - SE
checkpoint | 6.7 - Anchor block and to extend past edge of concrete
label | Detail / Activity - REFER to ANCHOR BLOCK TYPE TABLE on drawings based on pipe size
label | Acceptance / Conformance Criteria - IN ACCORDANCE WITH PROJECT SPECIFICATION as per sheet 0321
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - ER APPROVAL
label | Testing Quantity Required (based from schedule qtys) - SH29/Camrbridge Rd
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 7.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Joint and Connection
checkpoint | 7.1 - Flanges
label | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
label | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
label | Standard / Specification - PS 22.7.5 Appendix XXII
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - First flanged joint
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.2 - Bends
label | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
label | ○ Fitting must meets the same PN rating as the adjacent PE 100.
label | ○ Fittings must be suitable for producing the joints shown on the Drawings.
label | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
label | Standard / Specification - PS 22.4.2 Appendix XXII
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 8.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
checkpoint | 8.1 - Butt-Fusion Construction weld test
label | Detail / Activity - Test at least two welds from the first 50 welds.
label | ○ One of the welds to be selected by the Engineer for satisfactory result.
label | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
label | ○ 95% tensile strength; welds aligned
label | Standard / Specification - PS- 22.9.6 (a) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8.2 - Butt-Fusion Welding
label | Detail / Activity - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP). WMS Report
label | Standard / Specification - Appendix XXII PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist. WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8.3 - Survey
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | ○ Horizontal design Setout: +/-30mm variance
label | Standard / Specification - PS- 21.7.6 Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 8.4 - Photograph of Each Weld
label | Detail / Activity - Take sharply focused photo while clamped
label | Acceptance / Conformance Criteria - Unique weld identifier visible
label | Standard / Specification - N/A
label | Verifying Document - Weld Records; Photos
label | Testing Quantity Required (based from schedule qtys) - Each weld
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SUB
checkpoint | 8.5 - Weld Treatment for Corrosion Resistance
label | Detail / Activity - Treat welded areas to restore corrosion resistance
label | Acceptance / Conformance Criteria - Treated weld areas
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - QA Documents from Welders
label | Testing Quantity Required (based from schedule qtys) - Each weld
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - ENG
section | SECTION 9.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Backfill
checkpoint | 9.1 - Emebment Zone - (Side Haunch Overlay)
label | Detail / Activity - Granular Sand backfill Compacted in 200mm Layers.
label | ○ NDM/CleggTesting to be completed on maximum 200mm lifts of overlays .
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - In 200mm layers.
label | ○ More than 85% of MDD.
label | Standard / Specification - IFC Drawing 0320-1
label | Verifying Document - Lab Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - One test per 10m evenly spaced intervals. 200mm lift
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 9.2 - Pipe Markers
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 9.3 - Backfill Compaction Testing
label | Detail / Activity - GAP65/AP65 Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65or site won material Backfill Compacted in 200mm layers.
label | Testing to be completed on maximum 200mm lifts of backfill.
label | ○ 95% NDM on Shared and Carriageway.
label | OR
label | ○ 28% CIV
label | For site won min >60kpa
label | ○ Ave > 80kpa
label | Standard / Specification - PS- 22.13.5 NDM Standerd 25832, NZS 4402 Test 4.1.3, IFC Drawing 0320-1
label | Verifying Document - Lab Report / Watermain line record
label | Testing Quantity Required (based from schedule qtys) - As per Specification. One test per 10m evenly spaced intervals.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 10.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Inspection
checkpoint | 10.1 - Pipe Inspection
label | Detail / Activity - Inspection of Drainage line
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Watermain line record
label | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
section | SECTION 11.0 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE TESTING
checkpoint | 11.1 - Pressure Acceptance Testing
label | Detail / Activity - Backfill/cover with embedment before testing
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | Acceptance / Conformance Criteria - Potable Watermain Pipelines – 1250kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b)
label | Verifying Document - Test Report. Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 11.2 - Swab New PE Watermain
label | Detail / Activity - Swab to remove debris and air
label | Acceptance / Conformance Criteria - Water running clear & removed entrapped air
label | Standard / Specification - TCC IDC TS-7
label | Verifying Document - Swabbing Check Sheet
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 11.3 - Pressure Test New PE Watermain
label | Detail / Activity - Conduct pressure test. Due to not commissioning the pipe until later in the project, CB will complete there own pressure testing upon installation of the pipe, with the full pressure testing and chlorination to be completed once the pipe is ready to be commissioned.
label | Acceptance / Conformance Criteria - No leaks, no failure of any pipe, fitting or other pipeline component.
label | Standard / Specification - TCC IDC TS-7.1c Pressure Rebound Test Method; TS-7.1a Constant Pressure Test Method
label | Verifying Document - TS-7.1a/c Pressure Test Method (Test Report)
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & swabbing passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 11.4 - Chlorinate New PE Watermain
label | Detail / Activity - Chlorinate watermain
label | Acceptance / Conformance Criteria - 5+ pH on chlorine tester
label | Standard / Specification - TCC IDC IT-7.4.1 Disinfection Procedure
label | Verifying Document - Picture; Signed Chlorination Check Sheet
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & pressure test passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
checkpoint | 11.5 - E. Coli Test New PE Watermain
label | Detail / Activity - Test for bacterial contamination
label | Acceptance / Conformance Criteria - <1 E. coli; <1 Coliforms
label | Standard / Specification - TCC IDC IT-7.5 E. coli Sampling
label | Verifying Document - E. coli Test Report
label | Testing Quantity Required (based from schedule qtys) - All new pipe installed & chlorine test passed
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/SE
section | SECTION 12.0 - CONSTRUCTION ACTIVITY - WATERMAIN Manhole installation
checkpoint | 12.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Shear vane or Scala test result
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - W
label | ○ Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
checkpoint | 12.2 - Undercut approval
label | Detail / Activity - On Subgrade
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - Table 21.5
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12.3 - Undercut Backfill Compliance AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.4 - Bedding Compaction Testing AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - PS- 16.5.12, PS- 21.6.11
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.5 - Survey
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
label | Standard / Specification - PS- 21.7.6
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 12.6 - Sidefill Compaction Testing
label | Detail / Activity - From the bedding layer to the overlay layer of pipe.
label | Acceptance / Conformance Criteria - AP20/GAP20
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
label | ○ AP20/19mm chip
label | Standard / Specification - PS- Table 21.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.7 - Backfill Compaction Testing
label | Detail / Activity - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65-Clegg28%CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.8 - Manhole
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings 232735.02-WSP-DR-WAT
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019) Manhole checksheet
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site/ per manhole
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 12.9 - Installation of concrete chamber for Air Valves
label | Detail / Activity - NEW 1200mmØ PRECAST CONCRETE
label | ○ MANHOLE Concrete cut a hole in the base of the concrete chamber to a suitable size as to fit the pipelines. CONTRACTOR TO FORM HOLE IN
label | ○ CONCRETE CHAMBER WALL. HOLE TO BE SIZED JUST ENOUGH FOR FITTING SIZE, REPAIRED WITH SIKADUR 42
label | ○ OR EQUIVALENT NON-SHRINK GROUTand 2 layers of Malthoid placed arouind pipe3
label | Acceptance / Conformance Criteria - TYPICAL IN-LINE DN50 AIR VALVE INSTALLATION as per drawings
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - MANHOLE CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
checkpoint | 12.10 - Installation of manhole vent offset in the berm
label | Detail / Activity - 50mmØ GALVANISED STEEL VENT - TO BE SET BACK IN BERM. LOCATION IN BERM TO BE DETERMINED ON SITE
label | Acceptance / Conformance Criteria - To be determined on site
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - MANHOLE CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 12.11 - Deep drainage sump installation
label | Detail / Activity - 150 x 150 x 100mm DEEP DRAINAGE SUMP FITTED WITH DN80 PVC PIPE PIECE, 300mm LONG AND COVER GRATE
label | Acceptance / Conformance Criteria - As per drawings
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - MANHOLE CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 12.12 - 25MPa CONCRETE THICKENING, Corbels for the pipe entries/exiits
label | Detail / Activity - YD12 REINFORCING STARTER BARS DRILLED 50mm INTO MANHOLE WALL AND EPOXY GLUED
label | Acceptance / Conformance Criteria - As per drawings
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - MANHOLE CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
checkpoint | 12.13 - Installation of heavy duty chamber lid and backfill of manhole
label | Detail / Activity - Install the chamber lid onto the concrete chamber cover and frame as per the manufacturers specifications and backfill.
label | Acceptance / Conformance Criteria - As per drawings
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT)
label | Verifying Document - MANHOLE CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 12.14 - MH joints inspection
label | Detail / Activity - Inspection of joints
label | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
label | Standard / Specification - PS 22.7.10
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12.15 - Inspection
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
label | Standard / Specification - PS- 21.6.11
label | Verifying Document - Manhole Record
label | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 12.16 - Plumb
label | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Standard / Specification - PS-22.7.10
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 12.17 - Step Rungs
label | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
label | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
label | Standard / Specification - PS-22.7.11
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 13.0 - CONSTRUCTION ACTIVITY - AIR VALVES
checkpoint | 13.1 - Valves/Fittings
label | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | ○ Air valve 10 & 11 is DN50 size.
label | Standard / Specification - PS-22.4.2, PS 22.5.10
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | ○ Hold Point (Internal)
label | ○ (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 13.2 - Installation of Isolation Valve
label | Detail / Activity - Verify installation per manufacturer’s instructions
label | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions. Project Specifications
label | Standard / Specification - PS-22.4.2, PS 22.5.10
label | Verifying Document - Air Valve & Isolation Valve Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Each isolation valve
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
checkpoint | 13.3 - Installation of Air Valve
label | Detail / Activity - Verify installation per manufacturer’s instructions
label | Acceptance / Conformance Criteria - Installed as per manufacturer’s instructions
label | Standard / Specification - PS-22.4.2, PS 22.5.10
label | Verifying Document - Air Valve & Isolation Valve Check Sheet
label | Testing Quantity Required (based from schedule qtys) - Each air valve
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
section | SECTION 14.0 - CONSTRUCTION ACTIVITY - FIRE HYDRANTS
checkpoint | 14.1 - CHAMBER LOCATION
label | Detail / Activity - LOCATION OF HYDRANTS AND AIR VALVE CHAMBERS ARE TO BE CONFIRMED ON SITE WITH THE TCC ENGINEER AND OFFSET AS FAR BACK OFF THE SEAL AS POSSIBLE.
label | Acceptance / Conformance Criteria - TCC Engineer approval
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
label | Verifying Document - TCC sign-off
label | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
label | Verification Activity: Activity - HP
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 14.2 - HYDRANT SURROUND BLOCKS, HEIGHT TO SUIT
label | Detail / Activity - HYDRANT BOX WITH 150 x 150mm CONCRETE SURROUND TO BE FINISHED FLUSH WITH SURROUNDING GROUND
label | Acceptance / Conformance Criteria - Typical FH SHEET 0322
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
label | Verifying Document - CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
checkpoint | 14.3 - INSTALL DUCTILE IRON FH
label | Detail / Activity - HEAVY DUTY VALVE BOXI NSTALLED AS PER TCC's CODE OF PRACTICE
label | Acceptance / Conformance Criteria - CONTRACTOR TO ENSURE FLANGE DRILLING ON DN80 END OF REDUCER MATCHES FLANGE DRILLING ON DN80 HYDRANT RISER
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
label | Verifying Document - CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - CHECKSHEET
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
checkpoint | 14.4 - Concrete Pedestal on OFFSET bend
label | Detail / Activity - 3mm RUBBER SEAT BETWEEN BEND AND PEDESTAL 25MPa CONCRETE PEDESTAL
label | Acceptance / Conformance Criteria - Typical FH SHEET 0322
label | Standard / Specification - Project Drawings (232735.02-WSP-DR-WAT), PS 22.4.2 i, PS 22.5.11
label | Verifying Document - CHECKSHEET
label | Testing Quantity Required (based from schedule qtys) - Per offset
label | Verification Activity: Activity - I
label | ○ Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - ENG
section | SECTION 15.0 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
checkpoint | 15.1 - Survey As-Builts
label | Detail / Activity - Quality Check on Nee pipeline and structure based on the tolerances in RITS
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | ○ Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature
checklist | DN1210-SP2-011-006 ITP NAR & Carpark Streetlight | itp |  |  |  |  | DN1210-SP2-011-006 ITP NAR & Carpark Streetlight Rev 1
section | SECTION 3 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
checkpoint | 3.1 - Location of Lighting Poles and Cameras
label | Acceptance / Conformance Criteria - Confirm with surveyor and mark out the exact locations of lighting poles, Cameras, Cable Pits and Montrose boxes before installation.
label | Standard / Specification - IFC Drawings
label | Verifying Document - Survey data/Comms with Client
label | Frequency - Prior to Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 3.2 - Material grading: Materials (GAP20/AP20)
label | Acceptance / Conformance Criteria - Material grading:PSD
label | Standard / Specification - Sieve Size ¦¦ % Passing
label | 19.0mm ¦¦ 100% passing
label | 13.2mm ¦¦ 80-95% passing
label | 9.5mm ¦¦ 64-76% passing
label | 4.75mm ¦¦ 37-58% passing
label | 2.36mm ¦¦ 30-40% passing
label | 1.18mm ¦¦ 18-28% passing
label | 0.600mm ¦¦ 12-22% passing
label | 0.300mm ¦¦ 6-14% passing
label | 0.150mm ¦¦ 2-7% passing
label | 0.075mm ¦¦ 0-3% passing
label | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.2
label | Frequency - Lab Test Report NZS 4407.2015 Test3.8.1
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Weathering index: Materials (AP20)
label | Acceptance / Conformance Criteria - Weathering index:
label | Standard / Specification - AA to CA
label | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.3
label | Frequency - Lab Test Report NZS 4407.3.11
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Crushing Resistance: Materials (AP20)
label | Acceptance / Conformance Criteria - Crushing Resistance
label | Standard / Specification - >100kN
label | Verifying Document - PS-21.5.7, PS-21.7.2 Table 21.4
label | Frequency - Lab Test Report NZS 4407:1991 Test.3.10
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Luminaires & Poles - WK & TCC NAR & Carpark
label | Acceptance / Conformance Criteria - Luminaire and Pole types shall be supplied and installed as detailed on the drawings or as per instruction of Client
label | ○ Luminaire Controller - PDL- 56SS10.
label | Standard / Specification - PS 23.1.5 g) & Drawing 0411, 0412
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before each Installation
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - CCTV Cameras and DIN rail-mounted switch board
label | Acceptance / Conformance Criteria - TCC Approved IP67 IK10+
label | ○ With Weatherproof Housing , Vandal Resistant and PoE Dome (HD1080p, 2MP), Sensitivity down to 0.01 lux
label | ○ Have intelligent auto exposure to offer front and back light compensation.
label | ○ TCC IT-approved DIN rail-mounted switch board min 8 ports and 2 SFP ports
label | Standard / Specification - PS23.1.5 n)
label | Verifying Document - Material data sheet and engineers approval
label | Frequency - Before each Installation
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – CONSTRUCTION
checkpoint | 4.1 - Lighting Equipment-Luminaires & Poles (WK & TCC)
label | Acceptance / Conformance Criteria - Types of luminaires and poles shall be installed as per details on the drawings or as per instruction of Client
label | ○ Luminaire Controller - PDL- 56SS10.
label | ○ Luminaires shall be fitted with Shorting Caps.
label | Standard / Specification - PS 23.1.3 c-d); 23.1.5 f-g) & Drawing 23273502-WSP-DR-LIG- 0004; 0112; 0410
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each Installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 4.2 - Lighting equipment- Circuit Cabling (WK & TCC)
label | Acceptance / Conformance Criteria - Supply and Install final circuit cabling to Luminaires from via underground ducts and conduits as per Drawing
label | Standard / Specification - PS23.1.3 g); 23.1.5 e) & Drawing 23273502-WSP-DR-LIG- 0112
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 4.3 - CCTV- Camera and Cabinet Location
label | Acceptance / Conformance Criteria - All CCTV cameras will be installed at a high level, either on lighting columns or other designated high-level mounting points, providing optimal coverage
label | ○ The CCTV lockable cabinet will be securely mounted at a high level on lighting column TC94, ensuring a stable and protected enclosure for network and power components.
label | Standard / Specification - 23273502-WSP-DR-LIG- 0410
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Prior to installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
checkpoint | 4.4 - CCTV- Circuit Cabling
label | Acceptance / Conformance Criteria - All CCTV cameras will be installed at a high level, either on lighting columns or other designated high-level mounting points, providing optimal coverage
label | Standard / Specification - 23273502-WSP-DR-LIG- 0414
label | Verifying Document - Photo/Visual Inspection
label | Frequency - Each installation
label | Verification Activity: Activity - I
label | Verification Activity: By - PE/SE
checkpoint | 4.5 - CCTV- IP Addressing, Programming of PoE Network Switches
label | Acceptance / Conformance Criteria - Liaison with TCC for IP addressing and Programming of PoE Network switches.
label | Standard / Specification - PS 23.1.4 m)
label | Verifying Document - Comms Record
label | Frequency - Prior Installation
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
section | SECTION 5 – Commissioning and Testing
checkpoint | 5.1 - Luminaires (TCC)
label | Acceptance / Conformance Criteria - Carry out full commissioning of the Light Controls as detailed on the drawings.
label | ○ Also record "Benchmark" energy meter reading from the lighting switchboards of all levels to demonstrate power consumption when ALL luminaires are running at 100%.
label | Standard / Specification - PS 23.1.5 g) & h)
label | Verifying Document - Photo/Visual Inspection and Commissioning Records
label | Frequency - Each Commissioning
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
checkpoint | 5.2 - CCTV- Cameras
label | Acceptance / Conformance Criteria - Testing CAT6A U/UTP Cabling from CCTV Cabinet to each CCTV Camera.
label | ○ Liaison with TCC for Commissioning and Testing including camera adjustment to achieve the desired FOV.
label | Standard / Specification - PS 23.1.4 m)
label | Verifying Document - Testing/Commissioning Record
label | Frequency - Each Testing/Commissioning
label | Verification Activity: Activity - H
label | Verification Activity: By - PE
section | SECTION 6 – POST CONSTRUCTION ACTIVITY
checkpoint | 6.1 - Electrical Certificate of Compliance (CoC) & Record of inspection (ROI) Electrical Safety Certificate (ESC)
label | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
label | Standard / Specification - PS 23.1.5 p)
label | Verifying Document - CoC,ROI and ESC
label | Frequency - Post commissioning
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 6.2 - As-Built
label | Acceptance / Conformance Criteria - As-built drawings with
label | 1) ducting routes.
label | 2)) control groups,
label | 3) scene settings
label | 4) override sequences,
label | 5) luminaire and pole locations,
label | 6) the individual addresses of each luminaire, and their corresponding groups (if DALI) shown clearly for maintenance purposes.
label | 7) All changes to design to be noted, highlighted or markup clearly.
label | Standard / Specification - PS 23.1.5 h) & 23.8.5 a)-b)
label | Verifying Document - As-built Drawing/Survey Data
label | Frequency - Post construction
label | Verification Activity: Activity - H
label | Verification Activity: By - PE/ENG
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature