## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-sectioned | ITP021 - AGL Conduit & Boring Installation | itp |  |  |  | Yes | ITP021 - AGL Conduit & Boring Installation | b35ce456-eaa4-4b1a-b144-316ff3fe4058
checkpoint-group | 1.0 Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint-status | 1.1 - Check for Correct Documentation
label | Frequency: Prior to commencing activity
label | Acceptance Criteria:
label | • Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | Reference Documents: Drawings / Aconex Register
label | Inspection/ Test Method: Verify
label | Record of conformity: Drawings and drawing registers
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 1.2 - Implementation of all measures and controls
label | Frequency: Prior to commencing activity
label | Acceptance Criteria: All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
label | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | HP*
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 1.3 - Definition of the work Area & Survey check
label | Frequency: Prior to commencing activity
label | Acceptance Criteria: Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined as per For Construction drawings prior to trenching and install.
label | Reference Documents: IFC Drawings 12554937-E014 to E028
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | SCP
label | Responsibility: Site Engineer / Site Supervisor
date | Date Completed:
checkpoint-status | 1.4 - AGL Drainage Survey
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • Survey for new pit and duct to be carried out & services in the area located to confirm works at each of the 6 drainage locations. This is to include:
label | ○ Surface levels over locations of all proposed drainage structures (pit, pipe and headwalls)
label | ○ Full survey detail of all existing drainage infrastructure in the vicinity of the connection points (SLs, ILs, size of pipes, size of pits, size and depth of trench grates, infrastructure location, material, confirmation of condition suitability for connection).
label | ○ Invert levels required at all connections to existing infrastructure (pit, pipes and swales/surface)
label | ○ Location, level, depth, size and type of all existing services within works area.
label | Reference Documents: Aconex Reference: BecaCPL-TENADD-000007
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | SCP
label | Responsibility: Site Engineer / Site Supervisor
date | Date Completed:
checkpoint-status | 1.5 - Check Conduit Compliance
label | Frequency: Prior to commencing activity
label | Acceptance Criteria:
label | • Ensure that uPVC conduits comply with AS 1477 or equivalent AS 2053. Shall be heavy duty, orange for electrical services and white for communication services.
label | • Ensure that pipe diameter is correct as per the drawings
label | Reference Documents:
label | • Appendix K- Technical Specifications Cl 4.5.4
label | • Appendix J- IFC Drawings 12554937-E041 & As 1477, As 2053
label | Inspection/ Test Method: Verify
label | Record of conformity: Manufacturer’s certificate of compliance, This ITP signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 1.6 - Check Bedding Material Compliance
label | Frequency: Prior to commencing activity
label | Acceptance Criteria: Ensure that conduit bedding material is the Approved Hornfells Dust or an approved equivalent.
label | Reference Documents: FHPL-Contadv-000293
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP signed, Product Data Sheet, Aconex Approval
label | TP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 1.7 - Service Locating/Proving
label | Frequency: Prior to commencing Excavation Works
label | Acceptance Criteria:
label | • Location of services to be found and marked on the ground within the works;
label | • Obtain excavation permit from APAM prior to any demolition works.
label | • Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
label | Reference Documents:
label | • APAM- DBYD Job:32711991 Seq:215891341
label | • FH Permit
label | • Appendix K- Technical Specifications Cl.3.9.3
label | Inspection/ Test Method: Verify
label | Record of conformity: Melbourne Airport Excavation Permit
label | HP*
label | Responsibility: Site Engineer / Surveyor
date | Date Completed:
checkpoint-status | 1.8 - Backfill Compliance
label | Frequency: Prior to commencing activity
label | Acceptance Criteria:
label | • If the excavated soil is not compactible material free of rocks or will not pass through a 25 mm sieve then:
label | – The bottom of the trench must comprise a bed of 50 mm of Hornfells Dust placed before the first enclosure or cable is laid; and
label | – A layer of Hornfells Dust must be placed to cover the conduit with 75 mm of sand before backfilling.
label | • Ensure to use Fill Material that is totally free of organic content, deleterious and/or perishable matter such as bricks, concrete, glass, plastic, timber, steel, or steel by-products.
label | • Backfill of trench to be as per project documentation.
label | Reference Documents:
label | • Appendix K- Technical Specifications )2011.C.I
label | • Appendix K- Technical Specifications )Cl.3.9.9
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP signed
label | TP/AP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 1.9 - Under bore
label | Frequency: Prior to commencing activity
label | Acceptance Criteria:
label | • Prepare and implement a Quality Plan that includes the following documentation at a minimum:
label | – Full details of the methodology to be used; and
label | – Details of equipment to be used.
label | • This must be submitted at least 7 days prior to the commencement of site work
label | Reference Documents: Appendix K- Technical Specifications Cl.3.10.3
label | Inspection/ Test Method: Verify
label | Record of conformity: Melbourne Airport Excavation Permit
label | HP
label | Responsibility: Site Engineer / Principal’s Representative Surveyor
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 1.10 - Native Grass Protection
label | Frequency: Prior to commencing activity
label | Acceptance Criteria: Native grass protection installed. As per native grass model, 8m wide corridor delineated by bollards/ fencing.
label | Reference Documents: Relevant Native Grass Permit
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer/Site Supervisor
date | Date Completed:
checkpoint-group | 2.0 Construction
checkpoint-status | 2.1 - Existing drains
label | Frequency: Each
label | Acceptance Criteria:
label | • Where cables cross open drains, lower the cables to pass under the drains to maintain the minimum specified depth of cover.
label | • Run the cables in conduits encased in a concrete mix across the drain as detailed on the drawings.
label | Reference Documents: Appendix K- Technical Specifications Cl.3.9.4
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed
label | IP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 2.2 - Existing services crossing new conduits
label | Frequency: Each lot
label | Acceptance Criteria:
label | • Only approved methods of excavation that has been approved by the Principal’s Representative shall be used. The owner of the service as per the DBYD plans must be contacted prior to disturbance of area containing service.
label | • Minimum vertical distances between perpendicularly crossed services must be 100 mm.
label | • Details of existing services that conflict with conduit installation discovered during excavation shall be provided to Contract Administrator for approval.
label | • Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents:
label | • APAM- DBYD Job:32711991 Seq:215891341
label | • Appendix K- Technical Specifications )Cl.3.9.3
label | Inspection/ Test Method: Verify
label | Record of conformity: As-built Survey Report and This ITP Signed
label | HP
label | Responsibility: Site Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 2.3 - Existing duct banks
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • All duct banks must be extended to new terminating pits provided either side of the duct bank, providing access to the conduits. The new pits must be installed flush with the surrounding ground level.
label | ○ Cleaning of duct banks
label | • Expose and clear all ducts at each location prior to use. Provide clear written details of the proposed cleaning method and equipment to be utilised to the Contract Administrator for approval prior to commencing the works.
label | Reference Documents: Appendix K- Technical Specifications )3.10.1
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | WP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.4 - Condition of existing duct banks
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • The Contractor must inspect and record the quantity, condition, capacity and configuration of all ducts at each location following cleaning.
label | • Inspections must be identified in the Contractor’s Quality Plan and implemented as a witness point for the Contract Administrator.
label | Reference Documents:
label | • Appendix K- Technical Specifications )3.10.2
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | WP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.6 - Excavate Trenches for Conduits
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
label | • The depth of Primary trenches to be a minimum of 1050mm from the finished ground level and for the Secondary trenches, 600mm from the finished ground level.
label | • The width is to be a minimum of 200mm as specified on the drawings.
label | • Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
label | • New trenches containing airfield lighting cables must be as indicated on the drawings and in particular excavated to provide a minimum cover to cables or conduits of:
label | – 750 mm for primary cables
label | – 500 mm for secondary cables.
label | Reference Documents:
label | • Appendix J- IFC Drawings 12554937-E041
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP Signed
label | IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.7 - Excavation Obstruction
label | Frequency: Each lot
label | Acceptance Criteria:
label | • Any rock found to impose significantly on excavations (i.e. rock that cannot be excavated by means of a Rock Saw, Caterpillar D7 with single tyne ripper or similar suitably equipped machine) must be brought to the attention of the Contract Administrator
label | • Cable pits must be relocated as necessary to avoid significant areas of rock that cannot be excavated. Provide details of proposed pit relocations to the Contract Administrator for approval.
label | Reference Documents:
label | • Appendix K- Technical Specifications )3.9.7
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | HP
label | Responsibility: Site Engineer / Foreman / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 2.8 - Under Bore
label | Frequency: Each lot
label | Acceptance Criteria:
label | • Services installed under road and taxiway pavements and shoulders by under boring must have a minimum cover below the surface as shown in the drawings.
label | • Boring by water jetting is not permitted
label | • Notify the Contract Administrator at the following stages of construction:
label | – At setting up for the commencement of drilling; and
label | – At completion of drilling prior to connection of ducting to pits and backfilling.
label | Reference Documents: Appendix K- Technical Specifications )Cl.3.10.3
label | Inspection/ Test Method: Visual inspection
label | Record of conformity: This ITP signed
label | HP
label | Responsibility: Site Engineer / Foreman / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 2.9 - Duct Encasement Material
label | Frequency: Each lot
label | Acceptance Criteria:
label | • Under Pavements and Drain Crossings:
label | ○ Conduits to be encased in 5MPa lean mix concrete as per drawings.
label | • Under Grass:
label | ○ Conduits to be encased in compacted sand bedding. The material shall be Hornfells Dust or an approved equivalent
label | Reference Documents:
label | • Appendix K- Technical Specifications )Cl.3.9.4
label | • Appendix J- IFC Drawings 12554937-E041
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Verify
label | Record of conformity: Delivery Docket and This ITP Signed
label | IP
label | Responsibility: Site Engineer/ Foreman
date | Date Completed:
checkpoint-status | 2.10 - Conduit Markers & Warning Tape
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
label | • Warning tape shall be of polythene not less than 150mm wide and 0.1mm thick. They shall be orange/white in colour and bear "Caution - Buried Electric Cables Below” or similar repeatedly in black letter not less than 30mm high.
label | Reference Documents:
label | • Appendix K- Technical Specifications )Cl.3.9.5
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP Signed
label | IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.11 - Conduit Draw Chord
label | Frequency: Each Lot
label | Acceptance Criteria:
label | • Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be polypropylene rope and be 4mm in diameter to facilitate the installation of future cables. Draw cords shall be installed following the installation of the primary cables to prevent entanglement.
label | • Seal the buried entries to ducts and conduits with a pliable non setting waterproof compound.
label | • Seal spare ducts or conduits immediately after installation with a temporary cap, and seal the others after the Cable.
label | Reference Documents:
label | • Appendix K- Technical Specifications )3.9.1
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.12 - Bedding & Backfilling
label | Frequency: Each lot
label | Acceptance Criteria:
label | • In trenches, the lower layers to the level of 300 mm above the top of the conduits must be carefully bedded and consolidated at the appropriate moisture content under, around and on top of the conduits to not less than 90% MDD in accordance with test No. 5.1.1 of Australian Standard 1289 in the case of cohesive material, and not less than 70% of the density index in accordance with test No. E6.1 of Australian Standard 1289 in the case of cohesionless material.
label | • If the excavated soil is not compactible material free of rocks or will not pass through a 25 mm sieve then:
label | – The bottom of the trench must comprise a bed of 50 mm of sand placed before the first enclosure or cable is laid; and
label | – A layer of sand must be placed to cover the conduit with 75 mm of sand before backfilling
label | • Compaction Testing under roads must be carried out at a rate of not less than:
label | – Bedding: 1 test per 25 m of backfill laid
label | – Backfill: 1 test per 25 m of backfill laid per 0.5 m of backfill depth
label | – Subgrade: 1 test per 25 m of backfill laid – Base: 1 test per 25 m of backfill laid
label | Reference Documents:
label | • Appendix K- Technical Specifications )3.9.9
label | • AGL Conduit Install ITC
label | Inspection/ Test Method: Verify
label | Record of conformity: Test Report and This ITP Signed
label | TP/IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.13 - Bedding & Backfilling
label | Frequency: Each lot
label | Acceptance Criteria: In wet ground conditions, backfilling above the level of 300 mm above the top of the service may be carried out by mechanical plant, but care must be taken to ensure that material is not dumped into the trench and that no rock is placed in the trench until the service are covered by at least 600 mm of backfilling.
label | Reference Documents: Appendix K- Technical Specifications Cl 3.9.9
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.14 - Compaction Tests
label | Frequency: Each lot
label | Acceptance Criteria:
label | • In all conduit trenches, the lower layers to the level of 300 mm above the top of the conduits must be carefully at the appropriate moisture content under, around and on top of the conduits bedded and consolidated:
label | • For Cohesive material:
label | ○ To not less than 90% of the maximum dry density for cohesive material,
label | • For Cohesionless material:
label | ○ To not less than 70% of the density index.
label | • Compaction Testing generally must be carried out at a rate of not less than:
label | – Bedding: 1 test per 400 m of conduit laid (minimum 3)
label | – Backfill: 1 test per 400 m of conduit laid per 0.5 m of backfill depth (minimum 3)
label | • Where trenches are under constructed pavements and shoulders, or generally in dry conditions, the backfill must be compacted to:
label | • For Cohesive material:
label | ○ a relative dry density of not less than 95% of maximum dry density , or
label | • For Cohisionless material:
label | ○ 75% Density Index (test No. E6.1 of AS1289
label | Reference Documents:
label | • Appendix K- Technical Specifications Cl 3.9.9
label | • AGL Conduit Install ITC
label | • Test No. 5.1.1 and test No. E6.1 of Australian Standard 1289
label | Inspection/ Test Method: Visual Inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer / Foreman
date | Date Completed:
checkpoint-status | 2.16 - Soil Stabilisation
label | Frequency: Each Lot
label | Acceptance Criteria: Soil to be stabilised in disturbed areas within jet blast zones, adjacent to the runway with an approved equivalent as directed by the Client such as Vital Bon-Matt Stonewall, Flexterra HP Bitumen emulsion spray
label | Reference Documents:
label | • Appendix K- Technical Specifications Section 7205b
label | • Aconex Reference: BecaCPL-RTRFI-000123
label | Inspection/ Test Method: Verify / Inspection
label | Record of conformity: This ITP signed, Product Data Sheet, Aconex Approval
label | TP
label | Responsibility: Site Engineer
date | Date Completed:
checkpoint-status | 2.18 - AGL Drainage Install
label | Frequency: Each Lot
label | Acceptance Criteria: Install AGL drainage pits and ducts at 6 locations across the aerodrome as per project drawings
label | Reference Documents:
label | • Appendix J- IFC Drawings 12554937-E052,
label | • Appendix J- IFC Drawings 12554937-E053
label | • Appendix J- GHD Standard Specification for Airside Works- Hold Point 2018-3
label | Inspection/ Test Method: Verify
label | Record of conformity: This ITP Signed & Sub-contractor ITC
label | HP
label | Responsibility: Contract Administrator
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint-group | 3.0 Post Installation
checkpoint-status | 3.1 - Survey As-built
label | Frequency: Prior to Backfilling Each Lot
label | Acceptance Criteria: Surveyor to pick up completed conduit runs before backfill
label | Reference Documents: Appendix K- Technical Specifications Cl 3.18
label | Inspection/ Test Method: Verify / Inspection
label | Record of conformity: Survey Report
label | SCP / IP
label | Responsibility: Site Engineer / Surveyor
date | Date Completed:
checkpoint-status | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
date | Date: