## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Pile Predrilling | itp |  |  |  |  | ITP - Pile Predrilling
section | Location Details
checkpoint-no-status | Site Reference - Block
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
section | Preconstruction
checkpoint | Design Review
label | Verification of Piling Design and Layout
label | Compliance with approved drawings and geotechnical report
label | Design Approval Documentation
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
label | Schletter FS DUO - Fixed-tilt Installation Manual
label | Schletter Piling Instructions for Maungaturoto Solar Farm
holdpoint | CHINT / United Civil Hold Point
checkpoint | Material Approval
label | Approval of drilling fluids or stabilizers (if applicable)
label | Compliance with specifications
label | Material Test Certificates / Delivery Dockets for each delivery
holdpoint | CHINT / United Civil Hold Point
checkpoint | Survey & Marking
label | Visual Inspection of marked drilling points
label | Visual Inspection of alignment and marking of pile locations
label | Alignment with approved layout drawings
holdpoint | United Civil Hold Point
checkpoint | Equipment Verification
label | Visual Inspection of drilling equipment functionality and calibration
label | Drilling equipment in good working condition
label | Visual Inspection of Plant Prestarts
section | Drilling Operations
checkpoint | Drilling Alignment
label | Check verticality and alignment of drilled holes for every hole
label | Hole should be within 3° of vertical in both North/South and East/West directions
label | Visual Inspection and Measurement
label | ITC Record Updated for every table
checkpoint | Rock Penetration
label | Confirm penetration into rock (if applicable)
label | Achieves specified embedment depth
label | Drilling Logs
checkpoint | Spoil Removal
label | Spoil has been removed from each hole
label | Hole is clean and ready for pile placement
label | Visual Inspection of the holes drilled
checkpoint | Drilling Depth and Width
label | The minimum depth for all holes shall be 1.5m
label | The minimum width for all holes shall be 300mm
label | ITC Record Updated for every table
checkpoint | Predrill Hole Fill Media
label | Predrill hole media to be Stabilised Sand
label | Material Test Certificates/Delivery Dockets Attached
section | Post-Drilling Activities
checkpoint | Cleaning and Preparation
label | Visual Inspection of cleanliness and condition of drilled holes
label | Free from debris and loose material
checkpoint | Stabilization
label | Verify stabilization measures (if required)
label | Free from debris and loose material
checkpoint | Survey Verification
label | Visual Inspection of resurvey alignment and location of drilled holes for piling
label | Compliance with design tolerances
section | Maintenance and Monitoring
checkpoint | Equipment Maintenance
label | Inspect and maintain drilling equipment Daily
label | Proper functioning and safety compliance
label | Visual Inspection of daily maintenance records completed
checkpoint | Drilled Holes
label | Monitor for collapse or deformation
label | Holes maintain structural integrity
section | Post Construction & Handover
checkpoint | Final Inspection & Walkthrough
label | Comprehensive Visual Inspection of all drilled holes
label | Compliance with approved design, function and specification requirements
label | Verify readiness of drilled holes for piling
label | Area ready for subsequent construction activities
holdpoint | CHINT / United Civil Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely mannor
checkpoint | Documentation
label | On completion of the Predrilling works for this Block
label | Supply all documentation on completion of the Piling works for the block
label | Submission of all test results, ITC's and any as-built drawings
holdpoint | CHINT / United Civil Hold Point
checklist | ITP - Piling | itp |  |  |  |  | ITP - Piling
section | Location Details
checkpoint-no-status | Site Reference - Block
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
section | Preconstruction
checkpoint | Design Review
label | Verification of Piling Design and Layout
label | Compliance with approved drawings and geotechnical report
label | Design Approval Documentation
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
label | Schletter FS DUO - Fixed-tilt Installation Manual
label | Schletter Piling Instructions for Maungaturoto Solar Farm
label | In terms of the Piling Operation, in the event that early refusal is not observed, the Pile Testing done by Schletter prior to the construction phase is the extent of the Pile Testing done. Please refer to the Pile Testing Report provided for further details.
holdpoint | CHINT / United Civil Hold Point
checkpoint | Material Approval
label | Approval of Piles and Coating
label | Compliance with specifications (e.g., grade, dimensions, corrosion resistance)
label | Material Test Certificates
holdpoint | CHINT Hold Point
checkpoint | Design Verification
label | Visual Inspection of Design
label | Client Review of ULS Testing and Geotechnical Reports
label | Pile Design Report/Drawings available
holdpoint | CHINT Hold Point
checkpoint | Survey & Marking
label | Visual Inspection of alignment and marking of pile locations
label | Alignment with approved IFC Drawings
checkpoint | Ground Preparation
label | Visual Inspection of clearing and levelling of the site
label | Free from debris, vegetation, and obstructions
checkpoint | Equipment Verification
label | Inspect equipment and tools for installation
label | Equipment is functional and calibrated
label | Equipment Records where applicable
section | Construction
checkpoint | Pile Installation
label | Schletter FS Duo Fixed-tilt Installation Manual
label | Schletter Piling Instructions for Maungaturoto Solar Farm
label | Piles installed in the correct locations as per Schletter drawings and electronics Setout data
label | All piles in every table are installed to the designs and every pile is checked for the following tolerances:
label | North/South +/- 3°
label | East/West +/- 3°
label | Pile Twisting from axis +/- 5°
label | Distance E/W +/- 100mm
label | N/S +/- 50mm
label | Reveal Height +/- 100mm
label | Height difference foundation posts within one row +/- 50mm
label | Piles have no damage deformation and in correct orientation
label | Piling ITCs completed for each table
holdpoint | United Civil Hold Point
checkpoint | Pile Depth
label | Drive piles to marked embedment depth or until they reach the point of refusal
label | Pile locations recorded and marked in Piling Maps
label | Record Actual Pile embedment Depth and reveal heights in Data Tracker
label | Pile refusal in accordance with Pile Installation Manual
label | Piles cut and holes drilled and cold galvanising applied as per Schletter Installation Instructions
label | Piles are installed to a minimum driven depth of 1.8m
label | If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN.
label | If Pile refusal is found at shallow depth of <1.5m consider predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with stabilised sands and perform one pile test per area to determine foundation strength.
label | Piling ITC's completed for each table
holdpoint | United Civil Hold Point
checkpoint | Pile Predrilling
label | For every pile predrilled:
label | Predrill pile holes to be drilled and cleaned out to a minimum of 1.5m deep and results recorded
label | Predrill holes are a minimum of 300mm diameter and results recorded
label | Pile Predrill holes are backfilled with an approved material
label | Predrilling ITC's completed for each table
holdpoint | United Civil Hold Point
checkpoint | Cold Galvanisation Product Application
label | Review & approval of galvanisation product
label | Top 30mm of each pile must be sealed with an appropriate zinc coating as per Schletter FS Duo Installation Manual
label | Application of zinc protection follow paint manufacturers recommendations
label | Predrilling ITC's completed for each table
section | Post Installation Testing
checkpoint | Refusal at depth (1.5-1.7m or less)
label | If Pile refusal is found at 1.5-1.7m Perform individual Pile Test with Vertical SLS Load: 11.31kN with a displacement of less than 5mm after resetting to 0kN and Horizontal SLS Load: 5.77kN with a displacement of less than 5mm after resetting to a load of 0kN.
label | If Pile refusal is found at shallow depth of <1.5m predrilling a 300mm diameter hole to a minimum of 1.5m in depth and backfill with an approved material and perform one pile test per area to determine foundation strength.
label | Hold Point for United Civil
holdpoint | United Civil Hold Point
section | Post Construction & Handover
checkpoint | Final Inspection & Walkthrough
label | Comprehensive Visual Inspection of all installed piles
label | Compliance with approved design and specifications
label | Verify all piles meet design and functional requirements
label | Area ready for subsequent construction activities
holdpoint | CHINT / United Civil Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely manor
checkpoint | Documentation
label | On completion of the Piling works for this Block
label | Supply all documentation on completion of the Piling works for the block
label | Submission of all test results, ITC's and any as-built drawings
holdpoint | CHINT / United Civil Hold Point
checklist | ITP - Racking Installation | itp |  |  |  |  | ITP - Racking Installation
section | Location Details
checkpoint-no-status | Site Reference - Block
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
section | Preconstruction
checkpoint | Design Review
label | Verification of Racking Design and Layout
label | Compliance with approved drawings and structural analysis
label | Design Approval Documentation
label | Schletter FS Duo - Fixed Tilt Installation Procedure
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
holdpoint | CHINT Hold Point
checkpoint | Material Approval
label | Approval of Racking components (e.g., frames, bolts etc)
label | Compliance with material specifications & standards
label | Material Test Certificates
holdpoint | CHINT Hold Point
checkpoint | Equipment Verification
label | Inspect equipment and tools for installation
label | Equipment is functional and calibrated
label | Equipment Records where applicable
checkpoint | Survey and Marking
label | Visually Inspect & Verify alignment and marking of racking locations
label | Alignment with approved layout drawings
checkpoint | Ground Preparation
label | Visual Inspection of clearing and levelling of the site
label | Free from debris, vegetation, and obstructions
checkpoint | Foundation Verification
label | Verify foundation conditions and readiness for racking
label | Foundation integrity meets specifications
label | ITC completed for each table with piles installed
holdpoint | CHINT / United Civil Hold Point
section | Racking Installation
checkpoint | Frame Assembly
label | Inspect assembly of racking frames
label | Proper assembly as per Schletter FS Duo Installation Manual specifications
label | Visual Inspection of each frame
holdpoint | United Civil Hold Point
section | Post Installation Checks
checkpoint | Mounting of Girders
label | Mechanical Installation ITC's are completed for Mounting of Girders
label | Each M12x30 bolt passed through from the Girder and fixed on the Pile with a M12 Washer and M12 Flange Serrated Nut
label | Torqued to value of +/- 5% of 56Nm and pass/fail recorded
label | Each bolted connection shall be marked after torquing
label | K&T to check 100%, United Civil to check 15%, CHINT to Check 5%
checkpoint | Girder to Foundation Post Step Check
label | Mechanical Installation ITC's are completed for Girder to Post Installation
label | All Angles of the Girders to the horizontal are an angle of 23° +/- 1°
label | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
checkpoint | Purlin Connector Installation
label | Mechanical Installation ITC's completed for purlin connector installations
label | Purlin Connector placed under purlin
label | Purlin Connectors are screwed together with Four x M10x25 bolts for LC/LT Purlins
label | Tightened to a torqued value of +/- 5% of 32Nm and pass/fail recorded
label | Each bolted connection shall be marked after torquing
label | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
checkpoint | Purlin Mounting Checks
label | Purlins have been placed on top of the girders in correct direction
label | FS Gen3 Girder Purlin connector bottom attached
label | FS Flex Claw Installed
label | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
checkpoint | Bolted Connection of Girder and Purlin
label | Mechanical Installation ITC's are completed for each bolted connection
label | M10x35 bolt and nut tightened to a torque of +/- 5% of 32Nm
label | M21x30 bolt and nut tightened to a torque of +/- 5% of 56Nm
label | K&T to check 100%, United Civil to check 15%, CHINT 5%
section | Post Construction and Handover
checkpoint | Final Walkthrough & Inspection
label | Comprehensive Visual Inspection of installed racking system
label | Compliance with approved design and specifications
holdpoint | CHINT / United Civil Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely manor
checkpoint | Documentation
label | On completion of the Racking works for this Block
label | Supply all documentation on completion of the Racking works for the block
label | Submission of all test results, ITC's and any as-built drawings
holdpoint | CHINT / United Civil Hold Point
checklist | ITP - Module Installation | itp |  |  |  |  | ITP - Module Installation
section | Location Details
checkpoint-no-status | Site Reference - Block
dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19
section | Preconstruction
checkpoint | Design Review
label | Verification of Module layout and mounting details
label | Compliance with approved drawings and structural analysis
label | Design Approval Documentation
label | Schletter FS Duo - Fixed Tilt Installation Procedure
label | 01_Maungaturoto_FS2V-23°-12_DUO_EX
label | 02_Maungaturoto_FS2V-23°-12_DUO_EX
holdpoint | CHINT Hold Point
checkpoint | Material Approval
label | Approval of Solar Module components and hardware
label | Compliance with material specifications (e.g. certifications & warranties)
label | Material Test Certificates
holdpoint | CHINT Hold Point
checkpoint | Racking Inspection
label | Verify racking system readiness for module installation
label | Properly installed and inspected as per Racking Installation ITP
label | Inspection of all tables
holdpoint | CHINT / United Civil Hold Point
checkpoint | Equipment Verification
label | Inspect equipment and tools for installation
label | Equipment is functional and calibrated
label | Equipment Records where applicable
section | Construction
checkpoint | Module Handling
label | Visual inspection of modules for damage during unloading
label | No visible cracks, chips, or scratches
checkpoint | Mounting Hardware
label | Verify assembly ITCs as per Schletter FS Duo - Fixed Tilt Installation Procedure and secure mounting of hardware
label | As per manufacturer’s specifications within Schletter FS Duo Installation Manual
label | Visual Inspection
checkpoint | Module Mounting
label | Check alignment, tilt angle, and secure attachment
label | Compliance with approved layout and tolerances within Schletter FS Duo Installation Procedure
checkpoint | Align Modules and Tighten Clamps
label | Check alignment and verticality of installed frames and modules
label | Top panel to bottom panel to be between 5-10mm
label | Horizontally between panels with module clamps: 22mm
label | Panel clamps torqued to 15Nm and recorded as pass/fail in ITC's
label | K&T to check 100%, United Civil to check 15%, CHINT to check 5%
section | Post Construction and Handover
checkpoint | Final Walkthrough & Inspection
label | Comprehensive Visual Inspection of installed modules
label | Inspect modules for alignment and cleanliness
label | No misalignment, defects, or debris
label | ITC's Completed for each table
holdpoint | CHINT / United Civil Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely manor
checkpoint | Documentation
label | On completion of the Module works for this Block
label | Supply all documentation on completion of the Module works for the block
label | Submission of all test results, ITC's and any as-built drawings
holdpoint | CHINT / United Civil Hold Point