## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-010 Asphalt & Checklist - Rev.3 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-010 Asphalt & Checklist - Rev.3 | 07fd1739-3cd2-4468-b82e-ce3eaa1d74fc
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 8b521ed9-7662-5896-8505-bd58f3557f5d |  | note | Ref docs - Issued drawings / Site copy drawings
label | 859f3fc5-f72e-53ac-b7dc-82dd33d87728 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 583bc2a1-2c0d-5539-82f2-19934689195e |  | button | Acceptance | Yes,No,N/A
label | 2cf26ec4-39f0-5406-a419-111db80df5d8 |  | note | Key - S
label | fd84de87-d34e-58a5-8b6a-dbd8a82846b5 |  | note | UGL Key - S
label | c3b37027-e624-5c93-b9b0-57cdbdabe56f |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | f7745aad-a272-54c1-84c8-d7d38f65302f |  | note | Ref docs - Spec. 0161 Quality [Cl 7.8]
label | 6ef52324-8f3d-5ee9-8fa1-05aa6f1d95a7 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | 3bde29ae-ef82-5357-8c27-7c5fedb2754d |  | button | Acceptance | Yes,No,N/A
label | bda9a801-dcc8-5cd1-91e3-5ace2a115f40 |  | note | Key - S
label | 76de787b-929b-521b-ab7b-e908e1b16d75 |  | note | UGL Key - S
label | 7ff77f10-7690-5d21-9da9-839a864220fd |  | note | SHL Key - S
label | 4ed16aff-40bd-5d1e-941a-86dd27eb77da |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 826d393e-93ea-591d-8cd0-1c75d2bb37f4 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Set out
label | 6219cf74-449f-59fc-af25-40dfc92f41e9 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], Drawings
label | a7dbba5c-55b1-5e38-b2e4-ee1a3987c34f |  | note | Acceptance Criteria - Has the pavement been set out by an accredited Surveyor?
label | b59a8e4b-7704-5876-9b84-3f8b1af9b116 |  | note | ○ Set out comply with drawings?
button | 5918bf82-de0b-5229-a11a-2025f820e1ae |  | button | Acceptance | Yes,No,N/A
label | fe80df2f-8a27-56bd-82fa-91e7105dde58 |  | note | Key - S
label | ec95b0f7-01d0-518e-ab79-049d4331de86 |  | note | UGL Key - S
label | 7e08768b-64e9-50d5-8d19-ede75c33439e |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Mix design approval
label | f26bc0c0-1fb9-5670-9a3c-58dd59751bf2 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 2.4]
label | 3bae8603-1f21-548d-b433-9ac94c0939a8 |  | note | Acceptance Criteria - Provide all mix designs. Mix design is to be assessed by the Superintendent for compliance.
label | fa63228e-1ed7-5b88-ab34-7fd2d5e98cce |  | note | ○ Mix design to be approved by Superintendent before use.
label | 0612e515-6941-592e-b1d2-f7eb2654d8a3 |  | note | Notice: 14 working days before using mix
label | 1b6881f5-43e8-5ab5-b731-9976e109a15a |  | note | HOLD POINT
button | 80341d04-6964-5a45-beb8-95fd4df41c60 |  | button | Acceptance | Yes,No,N/A
label | df7fd1f5-833f-5e47-8038-011253702a8e |  | note | Key - H
label | c0e10a1b-0cb7-5038-b45f-80bf369d8e05 |  | note | UGL Key - H
label | d512979e-0a7e-5f1d-803b-41e416340039 |  | note | SHL Key - H
label | c9d2c77b-a9c4-5d54-aaf7-5d3c9aa4016c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 62928efd-5ffd-56e0-8078-af5ceed39b0b |  | tickbox | Mix design
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.5 - Tolerances of mix production
label | ed27058c-513f-5814-82a2-882943ca8160 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.1]
label | d6f0829c-bcf6-5851-987a-8f8d94cc4e2c |  | note | Acceptance Criteria - Is the Binder within 0.3% of total mix?
label | 4bf8c551-e5fd-5a97-a1cb-ebe0b29fd911 |  | note | ○ Has the daily particle size distribution been within tolerance?
label | 2aa03937-012f-51e9-9d9d-c078eb4c2fab |  | note | ○ Has the daily moisture content been within tolerance – not to exceed 0.5% on completion of mixing?
button | 7b6f2f36-b2a8-55e0-8d54-5159129cc624 |  | button | Acceptance | Yes,No,N/A
label | 7f352cdb-1807-50ba-8772-eea3390ebd70 |  | note | Key - S
label | f7623238-d572-5d55-af91-7ea4869f0df7 |  | note | UGL Key - S
label | ad4d115d-020d-51ac-bf46-d2ac0089f418 |  | note | SHL Key - S
label | 72edbd1b-028b-5183-866a-a713fba500cc |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0097cea3-4aa7-5dab-b09e-f368751c1a41 |  | tickbox | Test report
checkpoint-status |  |  | checkpoint | 1.6 - Production temperatures
label | 8d2f26a1-a703-5b99-98f8-863d5611035b |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.2]
label | 19e4d441-7b99-5fcd-b815-13f3d90f1443 |  | note | Acceptance Criteria - Do the temperatures listed below comply with requirements for max. temperature?
label | eef3c871-cb17-5ac1-9509-ed2cfbcdd807 |  | note | – Class 170, Class 320, Class AR450 Bitumen delivered into mixer – 165ºC
label | 48d62586-9334-5b7d-b970-08162b75ffd7 |  | note | – Class 600 Bitumen delivered into mixer – 175 ºC
label | 683aa177-ca61-508a-8272-7c6ffcb3b250 |  | note | – Aggregates before binder – 200 ºC
label | 9c5ccf56-0320-524e-937b-04f424199a0f |  | note | – Asphalt at discharge point – 175 ºC
button | db60cb45-ba60-559a-bb06-8330f1127506 |  | button | Acceptance | Yes,No,N/A
label | ef811113-f851-5373-8de0-ee6a9f80ccf6 |  | note | Key - S
label | 426bb2cf-af9f-5a40-ac69-c83d67a65af7 |  | note | UGL Key - S
label | 0cbae04a-8d59-5c90-a61b-fc7f9c24d33b |  | note | SHL Key - S
label | ecae07ed-8979-599c-b4f2-6cbe7fce5442 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9efd3428-e751-55a3-9d10-fa4a17c6d6a4 |  | tickbox | Test report
checkpoint-status |  |  | checkpoint | 1.7 - Certification of specification Compliance
label | 38b3cff9-37a2-5abc-b1df-20bde532e89e |  | note | Acceptance Criteria - Has each delivery come with a certificate of compliance?
button | 9904636d-b84c-5b0e-96a0-0313bd919137 |  | button | Acceptance | Yes,No,N/A
label | 798d2633-4bfa-5331-8f5b-7724f701f23b |  | note | Key - S
label | ec4d409b-b55f-504c-8aed-8d75f3cb5230 |  | note | UGL Key - S
label | 12f7763a-fd37-5ad9-9fe2-b7a24f99cc15 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 104e799d-21e9-5ea2-9c9d-7530cc02f5d7 |  | tickbox | Certificate of compliance
checkpoint-group |  |  | section | 2.0 Preparation
checkpoint-status |  |  | checkpoint | 2.1 - Conformance of previous layer
label | 9756e67a-82cd-586a-a595-2ad5b8d3a357 |  | note | Acceptance Criteria - Has the previous layer passed acceptance criteria? Refer to ITP of previous layer.
button | 68be4587-485c-5ba7-9e3d-1283a83c9c91 |  | button | Acceptance | Yes,No,N/A
label | 4a919f5c-ef15-5325-910e-b7fca293ba21 |  | note | Key - S
label | 4318d43f-0662-5825-be45-67eaa9023522 |  | note | UGL Key - S
label | 0649d373-2a64-5f35-a656-5c60de574c03 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Joints
label | a7398b08-ae70-5673-8595-e1b067900eac |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
label | 97470b1a-d00a-5633-b98f-b642a3fff057 |  | note | Acceptance Criteria - Transverse joints shall be offset by not less than 2m in adjoining paver runs and from later to layer.
label | a2ddd95f-2419-5667-afc8-2961a8624a67 |  | note | Longitudinal joints shall meet the following requirements:
label | d6a5ff50-ee40-5894-b523-c17c086e9af1 |  | note | – Wearing course joint coincide with location of intended traffic lane lines
label | 0afcfd20-7d3b-5e8e-bcc1-5dbbad94ce39 |  | note | – Intermediate and base course offset from layer to layer by not less than 150mm provided that no joint is placed directly below a trafficked wheel path
label | b16687eb-96ac-5866-a5fc-c28ff4690de2 |  | note | – Parallel to traffic lanes
label | f0e66604-1f2d-54e3-aba9-27081561c43e |  | note | ○ Location of planned joints is a Hold Point.
label | 32dfa3ff-3cc3-5ccb-bf66-7089b7e4010f |  | note | Notice: 7 working day before commencing
label | 5ae9eb62-75ca-568b-a385-16b371f54b45 |  | note | HOLD POINT
button | 85211aa7-81fc-54dc-ad7b-7f03bd4464fc |  | button | Acceptance | Yes,No,N/A
label | 78546ddc-9b73-552c-bd2f-f38ea153ea2e |  | note | Key - H
label | bd72c196-d59b-507b-bc69-9b9c9c866d5e |  | note | UGL Key - H
label | 4517ebbc-710e-57f3-a37f-dd347a9d0dc2 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Prime application rate
label | fcf7443f-f1fc-5333-8923-de0f1c379b87 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
label | de6b2ff3-e15f-5369-b90f-0ea329e41f6a |  | note | Acceptance Criteria - Unless otherwise directed, tack coat is to be applied to provide a uniform application rate of residual binder of between 0.10L/m2 and 0.20L/m2
label | a5fea104-e91e-595e-b1c6-affa4e7dd1ac |  | note | ○ Is the application rate for tack coat between the following?
label | 5d71cc18-490c-5736-a1d4-3aab33cd8909 |  | note | 0.15 to 0.30 litres/m 2 (60% bitumen content)
label | 80f2cc6f-30e2-5868-b77b-e248fe913fe3 |  | note | 0.30 to 0.60 litres/ m 2 (30% bitumen content)
button | 1b52a630-2993-5636-b305-9852b98bfa9f |  | button | Acceptance | Yes,No,N/A
label | 949f6d4b-ca15-539e-ad2d-95b1bab59fd4 |  | note | Key - S
label | 7a4331a0-9f43-5c82-b69a-5755675670da |  | note | UGL Key - S
label | 2130067a-d4a8-52fb-9109-ee324b30dfc9 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.4 - Approval to proceed
label | 0d4a5655-eed8-5fbc-923c-428b09c7e153 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 2.4]
label | 5e286f86-b856-57d2-a3e8-3a5aa9e97eca |  | note | Acceptance Criteria - Has approval to proceed been obtained from the Superintendent?
label | 2237ecd8-e004-5a6d-b3c3-f5a72ffa9c12 |  | note | Notice: 7 working days before commencing production
label | 3ae4c6e4-4acc-5210-bc7e-f7a28c49fa0a |  | note | HOLD POINT
button | 867faeb1-8098-5e61-b300-f7be6b1cfdf8 |  | button | Acceptance | Yes,No,N/A
label | ff20d91c-3c67-5ba3-b8f6-5c6aa185f948 |  | note | Key - H
label | 796b3d99-d020-5097-af77-36a1eeb48e69 |  | note | UGL Key - H
label | 6343a640-2edf-5028-b532-18ae22812404 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 Placement of Asphalt
checkpoint-status |  |  | checkpoint | 3.1 - Conditions for placing
label | 11f5254a-75b9-5a42-8cf6-bbdb9bff7afc |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4]
label | bc392876-ff12-5ff4-91d0-2521a322f23c |  | note | Acceptance Criteria - Is the area essentially dry and free of surface water?
label | 1c3b83b0-7a60-5b3d-b6e2-6e3ec8529094 |  | note | ○ Does the surface temperature meet requirements?
label | 7c6c5119-dc40-5d3d-a46b-d6b412004fdb |  | note | – Intermediate and base courses: 5ºC
label | 76753cb6-a6a4-59fe-975a-f0a698bf7090 |  | note | – Wearing course: 10ºC
button | 5075e9d0-9202-5347-90b6-328b337954ab |  | button | Acceptance | Yes,No,N/A
label | bff6132e-8889-5728-82a8-81a15eca3197 |  | note | Key - S
label | d6e16ecb-772f-5fda-8f15-3220758ba7df |  | note | UGL Key - S
label | 47145dbb-daa6-5ef0-a819-4066fed54f13 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Spreading
label | 2670cfb6-0d56-53f2-a2de-4963c617f5e5 |  | note | Ref docs - Drawings Spec. 1144 Asphaltic Concrete [Cl 3.4]
label | 09b3295d-aeef-556e-b415-079a0cdc2bd4 |  | note | Acceptance Criteria - Has the asphalt been spread in layers at compacted thicknesses as per the drawings:
label | d24ff81c-afaa-526b-962f-ed9573068fb7 |  | note | – Wearing Course: 40mm
label | a624d6eb-a47c-5c90-9169-b043285a53f1 |  | note | – 7mm Primer Seal
label | 8adb2fe9-7b50-56f2-819c-21bf2b131cb2 |  | note | ○ Has all asphalt been spread with a purpose designed asphalt paving machine to form a uniformly smooth asphalt mat?
label | b193a0da-f36c-5326-a9b5-f95896f98ad1 |  | note | ○ Does the width of a single paving run not exceed 6m?
button | b92ef0af-b461-5dfa-83f4-73cc60bafe1e |  | button | Acceptance | Yes,No,N/A
label | c03f2958-67f2-51fc-af97-d4839720d876 |  | note | Key - S
label | 095722c9-10a6-5d14-8bfb-78d5fdfc130c |  | note | UGL Key - S
label | eb059e84-5ab7-5f9d-a512-e92e0c7345fe |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.3 - Compaction
label | d5f5cd82-afbb-5850-9682-c330e8e1d5e0 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.4, 3.5]
label | b060dc59-8620-53fb-98ed-0fb4ba7f5de5 |  | note | Acceptance Criteria - Uniformly compact asphalt to below requirements as soon as the asphalt has cooled sufficiently.
label | 1e0738df-9754-5f4e-baf7-a83cfdf834af |  | note | ○ Confirm Frequency of testing and target requirements
label | 2c1fbc99-e486-56a2-81f7-de98a9afe74f |  | note | ○ 6 cores per lot
label | 7d482035-1373-5d74-b426-74db69bb788c |  | note | ○ 10 nuclear density tests per lot
label | 7ee0636d-b592-554b-92eb-1f437b28ae28 |  | note | Tested to the following criteria (acceptable values to be calculated bases off formula in standard):
label | 6a8ad818-5726-572e-b70f-83327e128a32 |  | note | – Density ratio greater than 94% for thickness less than 50mm
label | d493789d-6067-57c0-9f63-f790456a10ba |  | note | – Density ratio greater than 96% for thickness greater than 50mm
label | 7967a33f-fdeb-51f7-9714-391358ab4396 |  | note | Notice: Progressive
label | 0f14293d-d521-541e-930f-6b405bdb3e54 |  | note | HOLD POINT
button | 90c2dc2f-12c0-52da-8496-7b1fd4ce3935 |  | button | Acceptance | Yes,No,N/A
label | 866645c8-450f-5542-b86a-9990e1b12420 |  | note | Key - H
label | b9146d52-e344-52b5-be22-039df9357d6a |  | note | UGL Key - H
label | 661a5740-0ddf-5c17-a39e-7425e4b92c63 |  | note | SHL Key - H
label | bdf350fb-f1f0-5fc8-96ee-581a20868b78 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | dd65b3c4-5599-5806-9b5a-f3c0c84f9f74 |  | tickbox | Test reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 Finishing
checkpoint-status |  |  | checkpoint | 4.1 - Surface finish
label | ab7d3b3c-db88-596c-8cda-f2cf4ffee238 |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.5]
label | 86a8bdc0-a3d8-523e-aca1-0a0ba0e82006 |  | note | Acceptance Criteria - Asphalt shall be consistent and uniform?
label | 5bc22015-8654-5313-9021-d7f3b1c05ec5 |  | note | ○ Top of asphalt shall be not more than 10mm above specified level?
label | 9e79b1e6-524d-536d-9499-5bf7113111cf |  | note | ○ Asphalt against the kerb and channel shall be flush or not more than 5mm above the lip of the channel?
label | 33fa4170-1573-5153-8686-ca883a6b1225 |  | note | ○ Do no points on the finished surface lie more than below (medium to light traffic roads):
label | 06d077c8-a7b1-52e0-86c4-ab4daf366126 |  | note | Parallel to centreline
label | 562fd82b-c421-5237-9375-42657bd22d14 |  | note | – 7mm below a 3m straight edge for wearing course
label | 62be2f78-03b2-503b-aa01-b77ce3ce1230 |  | note | Transverse to centreline
label | 40362b99-6402-5da0-8076-b5e8e9e6f503 |  | note | – 10mm below a 3m straight edge for wearing course
button | 5c53008f-9b76-515e-9a3d-1f5efe2cde0f |  | button | Acceptance | Yes,No,N/A
label | d65f3e07-be60-5429-a62a-2df56b664204 |  | note | Key - S
label | 11de4bf3-948c-5746-8a90-2c52a7a36c2a |  | note | UGL Key - S
label | da81a204-e6cc-5afb-b15d-12c12670ad3e |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.2 - Survey pickup (Top layer only, N/A for all intermediate layers)
label | ef95502c-3898-5775-b4e9-7d90ba5c486a |  | note | Ref docs - Spec. 1144 Asphaltic Concrete [Cl 3.5]
label | 03573f23-f321-5089-9870-0ab9ea044868 |  | note | Acceptance Criteria - Has the prepared layer been surveyed in accordance with and verifying specified requirements?
label | 1fb302d8-97b9-5b55-806e-221d25d1d3ff |  | note | ○ The horizontal location of any point on the pavement not to vary by more than ± 50mm from the corresponding points shown on the documents, expect where alignment with existing is required.
button | 79ed943f-a84a-50d9-98e7-cfd0e4efa8cb |  | button | Acceptance | Yes,No,N/A
label | 429ecb42-e12f-5663-9467-41e7f29f42f8 |  | note | Key - S
label | 99639c07-a4fb-5d64-9fba-9fe14cf072f4 |  | note | UGL Key - S
label | 6503ba2a-45be-5c15-809f-7048c24aa7ee |  | note | SHL Key - S
label | 9c3331ad-33cc-542b-ace8-ec3b29e4f1a3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 124de1e3-d778-592c-852a-86bbff968811 |  | tickbox | As built reports
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-015 FRP Works (Structures) & Checklist - Rev.7 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-015 FRP Works (Structures) & Checklist - Rev.7 | 12afd405-da64-4e19-98f1-187dc3b12406
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | d02148e4-76bf-527c-ac3e-b0c803b30a54 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 557e59b6-ca20-55bc-82d7-986d6acc25f0 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 8773b788-06c0-5ad5-af96-35ad65030ea1 |  | button | Acceptance | Yes,No,N/A
label | 2f81033d-11cc-56c1-b3b4-d455966e450c |  | note | Key - S
label | dbe8be94-e2b5-5028-a15c-00b2b1523444 |  | note | UGL Key - S
label | 8802a477-6ba6-5f82-b922-51de244cc978 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 7b4865af-eef6-5848-b9dd-de5aab1ef48d |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | ac255880-00ba-5d0f-99fa-ed0ab9b4f051 |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
button | 0605cc47-c5ea-5cbf-a758-1deb8b2d2747 |  | button | Acceptance | Yes,No,N/A
label | 8a32006d-62d1-542d-b8d5-266768fa2a3c |  | note | Key - S
label | ac7720ec-fc0e-5370-9159-b6e2a98b7eeb |  | note | UGL Key - S
label | e1488b99-6b9e-5871-b975-93fc06c19187 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Set out
label | b52110b2-d380-59d4-a150-f8d9d8488d74 |  | note | Ref docs - Drawings
label | bb0cae5f-9a30-51d4-a1e8-f375511d2608 |  | note | Acceptance Criteria - Setout structure to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | 7433ae24-947c-5dc7-83ec-38f82cb08d89 |  | button | Acceptance | Yes,No,N/A
label | f4788699-ff0c-5e80-92c2-e65ea7d4341a |  | note | Key - S
label | 5057e893-01ee-5cac-be3e-f7351e810c13 |  | note | UGL Key - S
label | 187ac2f2-a18f-5ead-8967-fb472ef3e4c7 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Underlying Lot Conformance
label | 2d0b2d4f-e693-5b1d-9e99-041e8c8b68a6 |  | note | Ref docs - Underlying Lot ITP
label | 3e957f67-0178-5684-98d8-c9aec23b4ca8 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
button | cf265676-efe0-54c7-8bfe-83e71de2633a |  | button | Acceptance | Yes,No,N/A
label | 0774cec0-27e0-5bbd-a9a9-296b3115fbc3 |  | note | Key - S
label | 6dacb4b0-c0b5-5ed6-8987-c44af29d3312 |  | note | UGL Key - S
label | 7fea661d-c1a7-5676-99e7-a563696b605b |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and bedding
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | bc9df847-688f-5105-9043-2e2fb51cca0d |  | note | Acceptance Criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
label | 0ac153f5-9818-5e32-a531-a642693947ab |  | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
button | 0a9b3b2e-87fc-59f1-a4cd-9c0ec361e2c9 |  | button | Acceptance | Yes,No,N/A
label | a4f6d45d-a099-578f-b8d0-0a8565876879 |  | note | Key - S
label | 57791f77-6584-572e-8c99-c8d2460c2c5a |  | note | UGL Key - S
label | eef4c5d7-6313-5150-a6d0-8ca1e71d676c |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable Material
label | 6b996e20-4adf-5a5c-ab76-92d7ca93b945 |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.6]
label | 6381c62e-8117-54a8-b5dd-71aeb5bbb993 |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | 1ab47ce7-1a5a-56da-b181-b7d1b78e6515 |  | note | HOLD POINT
button | fce682c3-4686-54ce-858d-6faafd08b15d |  | button | Acceptance | Yes,No,N/A
label | 3d0791f3-7f61-565d-bde5-59cb52526c5c |  | note | Key - H
label | 223e17a9-e2ea-597b-b2b8-93878eb9b7a3 |  | note | UGL Key - H
label | cbbe94df-1de7-504e-9a71-73f09bc762e2 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Compaction - Foundation
label | 466ff5f6-9c92-5262-92e1-3b0bd1e8e91b |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.7, 4.13] Spec 0161 [CL 7.2]
label | 06892e50-060a-5fcb-8e08-8a6a571f545e |  | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 97% modified to a depth of 200mm below foundation level
label | fb5d1a06-22fb-5822-a2a9-985ea09f6246 |  | note | ○ Test Frequency = 1 per 500m2
button | 44b7a3f1-0085-5a99-93e6-f30398d4d997 |  | button | Acceptance | Yes,No,N/A
label | f0646193-5d5c-53bd-ac2d-8853f9d3d225 |  | note | Key - S
label | 0242ae6e-af61-5d37-91c0-2741caedc82f |  | note | UGL Key - S
label | dc7a336c-0e52-52e6-a3cb-92683c4b264b |  | note | SHL Key - S
label | e7441847-477f-5945-b52c-fe184d4331af |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9eee0f75-427e-580e-b07d-4e7580121098 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Foundation Inspection
label | e8e5549d-e9a6-5f66-a0f7-26a6f0bbde28 |  | note | Ref docs - Spec. 1112 Earthworks [4.7]
label | 63b17777-52bc-51f4-a493-ab849e72b68d |  | note | Acceptance Criteria - Foundation to be inspected by the Superintendent prior to placing blinding
label | 21a1a2d0-73dd-544b-8888-ac84a02692f2 |  | note | HOLD POINT
button | 38d7b776-b505-5dfe-a476-692c26235ae0 |  | button | Acceptance | Yes,No,N/A
label | 1cca8e88-7668-5cff-bab2-fac9ec0a6547 |  | note | Key - H
label | 72d0065c-5484-5646-9d1f-37018c55411a |  | note | UGL Key - H
label | b2c2cf30-87e6-543a-8971-48bb450b3661 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Blinding
label | a2545660-86a3-5870-8c56-60aa31408e27 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
label | eb67bdc5-3e3a-5404-8029-33ff7e386452 |  | note | Acceptance Criteria - Blinding (N15) for Reinforced Concrete Bases to be a 100mm thick mass concrete layer or as otherwise shown on the drawings.
label | b259dfa7-2578-52b6-b320-627b569f77d8 |  | note | ○ Unreinforced bases can be poured directly on the earth
button | bc1b58f1-8ee2-5c26-bca3-bd99dc561323 |  | button | Acceptance | Yes,No,N/A
label | 61863c85-7028-559a-afa5-dad3525e8e86 |  | note | Key - S
label | 33741f61-f74e-5a05-8c87-6e197c31a884 |  | note | UGL Key - S
label | 8fb77736-479a-536a-ab36-91f8bd0077dd |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.6 - Mating Concrete Surface Preparation
label | 014058b8-3e66-55c2-9597-5067fa59f166 |  | note | Ref docs - Spec. 0002 [CL 3.9]
label | 2a77f820-1903-5f77-91b7-488d521cad59 |  | note | Acceptance Criteria - Construction joints prepared and free of loose material
label | 7c941c0f-6b32-52cf-bbf1-13e585b4a7c6 |  | note | ○ Dowelled joints prepared and bond breaker applied for expansion joints if applicable
button | 72301dc7-57e5-57aa-be41-d97525f7ee1f |  | button | Acceptance | Yes,No,N/A
label | a9761d1d-14b5-5ba7-bb2e-c643aba70195 |  | note | Key - S
label | c00696cb-776f-513c-b779-7ac7afe55b1b |  | note | UGL Key - S
label | 2d21b50c-390d-5ef5-baae-ff524f35d29e |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Installation of cast in-situ structures
checkpoint-status |  |  | checkpoint | 3.1 - Formwork
label | f086adf7-8ab0-5271-a5ef-de700ce460fd |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.0], Drawings
label | 52ec8c9f-e0ff-50c3-9f87-742ebe8d5fe2 |  | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | 40abe801-9e32-504d-922d-ab8f04434b50 |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | c375ad68-987e-5164-b9e5-2e201741f678 |  | note | ○ Formwork engineers inspection certificate complete and received
label | e69e14a8-06ba-5f80-8e7d-cbdc0ee333bf |  | note | HOLD POINT
label | 6e9507e6-081e-5606-a8f1-3e80dc4ce462 |  | note | Before Placing Concrete
button | c3fe19d9-d56a-5209-b968-e1a4f140d80a |  | button | Acceptance | Yes,No,N/A
label | b209f27e-058f-5660-a5e5-a86da15949f6 |  | note | Key - H
label | 38cd80c2-2b5a-5b1e-a77f-a075e5ebc2be |  | note | UGL Key - H
label | 58a48d50-2083-54e8-8a25-ba50814b480f |  | note | SHL Key - H
label | c9a31f98-4818-5c00-b417-ae1ae4dfb698 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e2803bd6-387e-5f4e-a6eb-7e5a02b329fe |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Steel reinforcement
label | d6a26407-b061-5e28-b84b-695610478a6d |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.0], Drawings
label | ef688f89-60eb-5051-b589-1720c3116fed |  | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars. Inspection per layer installed.
label | 133ad2ae-472c-52db-a880-d21af6e01b09 |  | note | ○ Concrete pre-pour inspection complete.
label | 70152781-dc5e-5cf8-ab7c-cf53661567f5 |  | note | HOLD POINT
label | bdc10d8a-944c-5c6e-b189-3e03db1157a1 |  | note | Before Placing Concrete
button | 02dc72e3-0e31-52ce-9b09-a7c4ac8dd1d0 |  | button | Acceptance | Yes,No,N/A
label | 804d7420-e748-5f31-ab01-c776a559c174 |  | note | Key - H
label | 22aa627c-5dc4-5dd4-b301-4a863783fe8f |  | note | UGL Key - H
label | 3abdc47d-1fb9-5cd3-8f3b-57633280e20b |  | note | SHL Key - H
label | bdb43c0c-6a5f-5ab9-a87d-8d15f7e4d249 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | cb32b5c9-5f36-5fba-9e40-b7333c1268a4 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Reinforcement Splice Lengths
label | b8fe3a01-ab67-5d00-bd6c-a750eff2af5a |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 5.7]
label | f03494b6-0322-5506-9e96-95a92a07cc12 |  | note | Acceptance Criteria - Where splicing of reinforcement is not shown on drawings min. lap lengths shown below shall be adopted. (SPT-0002 Table 6)
label | 571fc8bb-6809-53d9-966e-3e5d52c6af69 |  | note | – – – – – – – – – – – – – – – –
label | b36559f9-7f94-5da6-adea-29924c42d1f5 |  | note | Table 6 Reinforcement Splice Lengths
label | b15e6c17-1efe-5013-8dd3-213b11170fab |  | note | – – – – – – – – – – – – – – – –
label | e85b4f4d-3f21-51e6-81b0-38730a053e8a |  | note | Reinforcement Size ¦¦ Lap Length (mm)
label | 5f4dbc3e-3c4b-5946-9967-d614190c1dcc |  | note | – – – – – – – – – – – – – – – –
label | 2e927fd1-aa8a-5270-bf4a-670cdf8b824e |  | note | N12 deformed bar ¦¦ 500
label | d648ef04-9503-59e2-8f68-158aa6ca8959 |  | note | N16 deformed bar ¦¦ 800
label | 7480f6b6-15cb-5178-9551-af7088d9aa30 |  | note | N20 deformed bar ¦¦ 1150
label | 0b441248-65ee-5dd8-96e0-10d1cf226497 |  | note | N24 deformed bar ¦¦ 1350
label | 75275349-1859-5211-8bea-6653b224e088 |  | note | N28 deformed bar ¦¦ 1600
label | 3fc862a8-8bec-570e-a610-ada750de53fa |  | note | Welded wire fabric ¦¦ 225*Minimum 2 cross wires
label | 2d55374c-00b0-5603-8ce1-9696187fc8fd |  | note | Trench mesh ¦¦ 500
label | 180f2506-2961-5bce-bb82-a57b9190cef4 |  | note | – – – – – – – – – – – – – – – –
button | e8d833b7-a9b4-5463-9298-1e77381dccf6 |  | button | Acceptance | Yes,No,N/A
label | 20abee87-862a-57da-9ab3-5f89c03712fe |  | note | Key - S
label | 8a59565d-2aa8-53fc-9565-73ca9dafeca7 |  | note | UGL Key - S
label | 0e92a123-b418-5c4e-b340-a275587bb960 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.4 - Pit & Pipe Connections
label | 025c9242-660b-53f9-a66d-2d9616b2c546 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3], Spec. 0002 Concrete supply, construction, and grouting [Cl 2.6], Drawings
label | 085c6f7e-12c5-5b31-ad24-e4b3bc5659fc |  | note | Acceptance Criteria - Inlet and outlet pipes to be integrally cast into foundation/pit walls and the joint waterproofed as per design requirements.
label | dee824c3-66c3-5881-ac1f-fae1ea7ac607 |  | note | ○ Embedded pipes to be adequately restrained against flotation
label | d57243c4-118b-5086-a594-60a6cc1b3e9c |  | note | HOLD POINT
button | 7042a272-61ba-5111-bc84-d4ddf642803b |  | button | Acceptance | Yes,No,N/A
label | 3700a480-7f3c-5b9a-94c5-5192d0d2244f |  | note | Key - H
label | 8475ae73-584b-505e-bdd8-f666346f151f |  | note | UGL Key - H
label | bb841c4d-1dc6-5276-8c4a-690e14fef873 |  | note | SHL Key - W
label | 0928c6b9-0ea3-5e7a-9533-b96b1848efe0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - ITP for associated pit/pipe reviewed for conformance
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Installation of Core Holes, Voids, HD Bolts and Embedments
label | 769730c5-a288-51a7-a842-e52c8d91bd61 |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
label | 61da65a2-86a1-5ccb-ac01-0f0efdb5394a |  | note | Acceptance Criteria - Firmly Fixed in position in all directions
label | 86747513-6a4f-52d5-9794-889cd2ea988b |  | note | ○ Reinforcement displaced where necessary, bars requiring cutting approved by superintendent
label | 6020f86a-2866-5a5a-ab84-9bce9daed9bd |  | note | ○ Integrity of surface treatments maintained (galvanising, painting etc)
label | dc553281-de25-5a25-b0ad-60164e5d7831 |  | note | ○ Threads covered
button | 879d19d4-cc94-58b0-80bb-da901d607c32 |  | button | Acceptance | Yes,No,N/A
label | 39c137f0-7279-59a3-8aff-d43295cb024a |  | note | Key - S
label | 3eb653bd-62b0-53b8-a636-8f36da4a46dc |  | note | UGL Key - S
label | 980cf9e9-5c78-5cb9-b628-56b519d57845 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.6 - Tolerances of Core Holes, HD Bolts and Embedments
label | 1ef40727-7501-57eb-aef7-27b11cd19172 |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [CL 2.6, 7.1, 7.2, 7.3]
label | fd512a4b-4f73-5721-81a8-c34b2bbfa591 |  | note | Acceptance Criteria - HD bolts positioned using a template. Tolerance for HD bolts as per CL 7.2 (see below table)
label | f00d3552-0d20-5d06-bd8e-4418a096dc7e |  | note | – – – – – – – – – – – – – – – –
label | 85b17883-c18d-5a82-911e-5d054da719c5 |  | note | Condition ¦¦ Tolerance
label | 7a74d9c6-703c-55a5-9363-e36da081e8c5 |  | note | – – – – – – – – – – – – – – – –
label | 04d744b7-c580-56f2-9848-64f68f4bf9e2 |  | note | Any 2 bolts within a group ¦¦ ± 3mm Centre to Centre
label | b5db0a53-7cf7-57b0-b29c-5b9428886253 |  | note | Adjacent HD bolt groups ¦¦ ± 6mm Centre to Centre
label | c5d345c7-6426-5ff3-ab96-dca3386f50c0 |  | note | Bolt Projections - From concrete level ¦¦ + 5mm, -0mm
label | 4ad20b3b-d9be-513b-bf27-4d7d920ca64b |  | note | Embedded steel finishing flush with surface ¦¦ ± 3mm from surface
label | 2a78d256-801e-5241-a0d1-3f1550ca18a0 |  | note | Bolt reduced level ¦¦ + 5mm, -0mm
label | 11af52cc-74b4-535b-9149-620541687309 |  | note | Verticality of any bolt ¦¦ 1:300
label | 1404fa69-7b48-570d-a1a4-b746d7392ebd |  | note | Maximum accumulation of 6 mm per 30,000mm along an established column line of multiple HD bolt groups, but not exceed a total of 25 mm.
label | d03869c4-bd35-5987-96a2-9831a4769348 |  | note | 6 mm from the centre of any HD bolt group to the established column line through that group.
label | 3054a8df-8a2a-5aa2-9397-077d43f05786 |  | note | – – – – – – – – – – – – – – – –
label | f5468fa6-5d8e-5294-816c-edb5a164ea3a |  | note | *Before poruing concrete of the GT & GEN foundation, MPW TA will check the setting condition of GT & GEN anchor bolt. Witness Point as per MHI ITP.
label | 1a909a8d-af74-5d86-9f65-1693b3b6c28b |  | note | ○ Tolerances for other embedded fabricated items in line with AS 3990 or AS4100 as applicable.
label | b49cd147-29c0-5da6-89c4-06f65ad629a2 |  | note | ○ Pre-pour survey performed and recorded to verify location
label | 7dca92ae-980a-589d-8907-b5a6fcea628a |  | note | HOLD POINT
button | 925de734-2d0e-547e-a831-62278c98929e |  | button | Acceptance | Yes,No,N/A
label | a0d40960-3d1f-5d19-b22c-1a81e75fe0ce |  | note | Key - H
label | 5370fc6f-c4a7-5396-9732-0a78c4ff398e |  | note | UGL Key - H
label | 5426f039-4709-55f3-9950-97796f08be97 |  | note | SHL Key - W
label | f059ee1b-591b-5575-be78-0320427d1b4b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f669cfe0-2bf9-5a58-a925-4dfdddb084b5 |  | tickbox | Pre-pour inspection and Survey Records Inc MHI Check Sheet for GT & GTG Anchor Bolt Setting CG-64294
checkpoint-status |  |  | checkpoint | 3.7 - Earthing for Concrete Structures
label | 38195817-04ed-563f-b2d8-09d597ded1a2 |  | note | Ref docs - Drawings Spec. 0002 Concrete supply, construction, and grouting [CL 2.6]
label | ba360a78-c507-5952-8728-bd4ff3063c11 |  | note | Acceptance Criteria - Earthing installed for concrete structures as per provided Drawings
label | 2507d19f-1ee4-5eba-8b4b-759447d122ce |  | note | HOLD POINT
button | bff0a028-1e76-5099-a3f4-1d0acd1e7582 |  | button | Acceptance | Yes,No,N/A
label | 5a6a04b9-98ed-5113-bb9e-60b1b0e4fc46 |  | note | Key - H
label | 85ed65f8-73f0-5f10-9a0b-498a1f13130d |  | note | UGL Key - H
label | 1311df57-d509-5448-92b9-dbf2a2a2b942 |  | note | SHL Key - W
label | fb5a6268-8c7a-5c10-beb7-783b5a71c57e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1ac0c9c0-6938-57be-a82c-f48dfb4a35cc |  | tickbox | UGL Earthing FIC
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.8 - Concrete Mix and properties
label | aacd227d-7c65-5019-a4be-f585dced14d3 |  | note | Acceptance Criteria -
text | 381b0ac8-4a54-578d-89f6-1e737893ebe6 |  | textbox | Concrete compressive strength required (28 days) = |  |  | MPA
text | 208925a9-41c2-516a-812c-4b1026624daf |  | textbox | Approved Concrete mix ID =
text | 164d6bd3-8eeb-5c11-80af-1a49b28a0299 |  | textbox | Slump = |  |  | mm
button | 0a18a453-c2b8-584d-927d-21b31ad95383 |  | button | Acceptance | Yes,No,N/A
label | ee3d4a2f-146f-55a0-842a-e57001b74a3a |  | note | Key - S
label | 76ec3611-aad9-5255-a869-2457b09fb028 |  | note | UGL Key - S
label | 5040019b-3f65-558c-b04d-cb96564b5da2 |  | note | SHL Key - S
label | 321b8f62-9b49-554d-9e37-8a0218d383c8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 65acb076-f826-5b2f-a851-31d10aec19bb |  | tickbox | Material dockets
boolean | ebe85780-452a-5934-9bdc-45e9d3cb333f |  | tickbox | Concrete pour records
checkpoint-status |  |  | checkpoint | 3.9a - Concrete Supply Temperature - GT Foundation Only
label | e0cc7b6c-e35f-5eb5-a3e7-801da7b8491e |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2], Thermal Analysis Report
label | 158ce6c2-468a-5f38-b956-c65a5aa9ba7a |  | note | Acceptance Criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 25°C.
label | 50207366-8364-5d5b-8f2d-a747c7cbad81 |  | note | ○ Ambient air temperature at the time of placement must be between 5oC and 30oC.
label | 2ac10273-3215-57c5-8d55-b0610434d1c5 |  | note | Key - S
label | a8489b26-25f7-5f21-85b9-e7df8fa81b57 |  | note | UGL Key - S
label | f3ba78da-cfe4-5a90-911f-285650b596b8 |  | note | SHL Key - S
label | 8ff7ccd7-8bb5-551f-b886-5d443cb72af4 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 3a2e4428-ebfd-5cee-88f7-d9225971bdc1 |  | tickbox | Material dockets
boolean | 67254708-6bc0-52cd-b189-2df6ec5e3e13 |  | tickbox | Concrete pour records
checkpoint-status |  |  | checkpoint | 3.9b - Concrete Supply Temperature – Other foundations
label | 58071e07-fd4f-5c74-8074-aae2c311c9c1 |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.2]
label | dfeb4a86-bd8e-53f5-b09d-05424501ad0a |  | note | Acceptance Criteria - Temperature of concrete at the time of placement must be minimum 10°C and maximum 30°C.
label | e9cdb38c-df00-5349-b43a-9c648c44a8bd |  | note | ○ Ambient air temperature at the time of placement must be between 5oC and 32oC.
label | b9404258-580d-5e0e-b918-4f197c29e387 |  | note | ○ If ambient temperature is between 32oC and 38oC, seek approval from superintendent to proceed by taking special precautions noted in the specification.
label | 4bf1dee2-d95c-522f-84d1-5f8247708293 |  | note | Key - S
label | d829ebba-d699-5033-95b1-502bd11cf681 |  | note | UGL Key - S
label | 031ce80d-6ad4-5531-8116-ed82ed23663f |  | note | SHL Key - S
label | c4a09a8f-efb7-5947-b3c1-4554fa03e743 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ab427342-380f-5e6e-96fe-aadc3f95408c |  | tickbox | Material dockets
boolean | 44f91894-360f-5709-bae5-ae36dd7f5d25 |  | tickbox | Concrete pour records
checkpoint-status |  |  | checkpoint | 3.10 - Concrete Placement
label | 8ed7b180-0c03-5e54-b167-bc4670c11aad |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.1.4]
label | d454f90e-4bda-56fd-a9e1-07b86bd330b0 |  | note | Acceptance Criteria - Ensure elapsed time between batching and discharge of the mix does not exceed 1.5 hours.
label | bf01e9a4-c49f-5f85-92f2-ef69cb81777c |  | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
label | 71e87cc9-deef-5d32-abf8-d33b7ee96398 |  | note | ○ Concrete thoroughly compacted – one internal vibrator per 10m3 concrete placed per hour
label | 4b0bf674-3d48-5b57-86df-b1dc27e009c8 |  | note | Key - S
label | 4a6582ba-190a-52c6-9fed-b5243f6e950c |  | note | UGL Key - S
label | 1188fc2e-adcf-5369-9758-805de15054fc |  | note | SHL Key - S
label | fa3c94d0-a619-5521-9f91-9aef93edb37f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 3f5b91ab-4d70-5bdd-bdd8-b7b55891e1bf |  | tickbox | Material dockets
boolean | c16ceb32-bac3-51fa-b354-b4ee1b2f1409 |  | tickbox | Concrete pour records
checkpoint-status |  |  | checkpoint | 3.11 - Concrete Slump Testing
label | 9ce2909f-f917-5316-9078-41d91585ff5d |  | note | Acceptance Criteria - Slump Test - One per batch of concrete
label | 7e4f0726-4fed-58e3-a8ee-d1572a1cba50 |  | note | Slump within tolerances specified in AS 1379
label | 3c301884-ffc8-5ad2-be3c-dde89022b5a9 |  | note | – – – – – – – – – – – – – – – –
label | 44a38783-905a-55bc-a6d1-798c477ffb05 |  | note | Table 5.1 Permissible Tolerance on Slump
label | 2d51011b-0fd6-5090-9051-abe945606034 |  | note | – – – – – – – – – – – – – – – –
label | fd9fae1f-d86e-5cad-8804-e33583354b17 |  | note | Specified slump, mm ¦¦ Tolerance, mm
label | d3357081-531e-5607-8f5b-8ab8d76733e1 |  | note | – – – – – – – – – – – – – – – –
label | b7efae44-e910-54f6-b733-fdc4a68dab26 |  | note | <60 ¦¦ ±10
label | b0cfcd69-fb75-51ca-8026-ef6144364c13 |  | note | ≥60 ≤80 ¦¦ ±15
label | 4cd7b149-7973-56e5-9d86-1444d00e99fd |  | note | >80 ≤110 ¦¦ ±20
label | 5d75f8cd-bcaf-5a28-afac-1db5babe9886 |  | note | >110 ≤150 ¦¦ ±30
label | 77bc07a9-b219-5201-88e2-8e126b995b41 |  | note | >150 ¦¦ ±40
label | 7c9f6a88-265e-5071-b9ae-5391fdb9e666 |  | note | – – – – – – – – – – – – – – – –
label | ef45e67f-3ada-54ad-a72b-5aacecb788bf |  | note | Testing to be executed by a NATA accredited test facility
button | 70b56dc6-7ca0-5eda-8a3f-6f9cee7e1f7e |  | button | Acceptance | Yes,No,N/A
label | 307b2597-4800-59f5-ad24-bbfd6e6fca05 |  | note | Key - S
label | 89c9b346-ce8a-566a-b572-d6c16bc25525 |  | note | UGL Key - S
label | 89d984d8-115d-5c13-8aa9-7bb041d0e6f2 |  | note | SHL Key - S
label | d55ddef9-1f3f-52aa-9dc4-cb9fbfd151c4 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 779bfbf4-5591-5a13-9cdc-6f87fb5382ae |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 3.12 - Concrete Compressive Strength Testing
label | 6452946e-1e84-571a-be7d-12da3d2595fc |  | note | Ref docs - Drawings
label | 62f55345-7611-5632-8368-a112ea565d6f |  | note | Acceptance Criteria - Compressive Strength Testing - 2 x 7day and 2 x 28day per 50m3
label | 1f25029b-0c10-56d2-9208-485454ff140c |  | note | ○ Testing to be executed by a NATA accredited test facility
button | 8409b014-5383-5528-9265-59d4461acf03 |  | button | Acceptance | Yes,No,N/A
label | ce0d0145-33de-565c-be7d-bd3e2270c6a2 |  | note | Key - S
label | 910902ce-16f1-5dfd-880f-e2660e8b9f91 |  | note | UGL Key - S
label | 8e4dd4d6-2ee6-5ab3-b941-87c1f768ecfa |  | note | SHL Key - S
label | 1ca9e828-9b05-5544-a340-9e6b875755af |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9e0e160a-f91a-5f46-8d70-9a6157869593 |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 3.13 - Surface finish
label | 2a53b644-67f3-5046-948f-c2d4e84ac587 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2], Drawings
label | 0281595a-1409-5a66-833a-e2e458b468f1 |  | note | Acceptance Criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
label | 5c1c3eb7-5833-5ef2-b5f6-7450681a4dd6 |  | note | ○ Formed surfaces conform with surface finish requirements of AS3610 for the surface class nominated.
label | 8adb6e57-9d39-584b-89fa-0b9341979e8d |  | note | WITNESS POINT
label | e3e2d541-7489-552a-b316-8cfb7e257e92 |  | note | 1 day prior
button | bb9e37ca-b3ed-565f-a009-58ebe14111b3 |  | button | Acceptance | Yes,No,N/A
label | 66c01ff3-9c68-5674-a882-817629bcbd21 |  | note | Key - W
label | b4705925-3384-5843-81c2-60eb07c53d58 |  | note | UGL Key - W
label | cf8ace51-ec66-5163-8388-96bd60059c1f |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 3.14 - Surface Treatments
label | a0aacf3c-8b50-5fb0-9430-03f8408b56bd |  | note | Acceptance Criteria - Any surface treatments to be applied are approved for use and appropriate dose rates have been determined
button | e08db6b7-26ed-5efa-830d-92ae484bdbc4 |  | button | Acceptance | Yes,No,N/A
label | ebfed0b4-1cd9-57db-a747-aa1caf399a24 |  | note | Key - S
label | 2b570d66-abec-5f0b-95e2-1386ec3d7061 |  | note | UGL Key - S
label | 99c32a7c-7531-58be-b9d3-0bed3210d88a |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.15 - Joints
label | 0b1dda2b-4ad5-5240-926e-a46677c4815f |  | note | Ref docs - As per drawings
label | 78a01543-ebb8-5103-8ff4-7c1487730b0c |  | note | Acceptance Criteria - As per design drawings. Sawn joints to commence as soon as the concrete has hardened sufficiently.
button | 51b28d05-4c2f-5224-9c98-41bf25900622 |  | button | Acceptance | Yes,No,N/A
label | 8220a9bb-37c3-5782-996a-a18c6ae194c7 |  | note | Key - S
label | e72590c7-4518-5add-b75b-847289fbc31a |  | note | UGL Key - S
label | ee10abef-7c80-5edd-a230-83de9d49ff9b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.16 - Curing
label | 47caa657-3e83-5a40-a925-1c5ea09bb132 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | 890e91c7-1d17-5c05-bdd8-6fd2755c9a3d |  | note | Acceptance Criteria - From completion of finishing cure continuously with an approved method for a min period of 7 days or as directed by the Superintendent.
label | 5238d57d-793d-5c88-a958-fd90a650fe8b |  | note | a. Ordinary Portland cement concrete – 7 days
label | 6f6fd0bc-f56a-5fd7-af93-c8853aab3c8c |  | note | b. High early strength concrete – 3 days
label | 1cb9e399-a139-5a27-9a73-34ac1eedbd04 |  | note | c. Concrete with cement or pozzolan materials – 10 days
button | 91abb0ec-634c-55cf-bd00-096c1ef66db8 |  | button | Acceptance | Yes,No,N/A
label | 2a7e839e-9fdb-510d-9a6c-eeb8b9348df8 |  | note | Key - S
label | e1fbe8c2-d8be-5333-a0b3-8e07f15879ca |  | note | UGL Key - S
label | e432882f-0040-53ba-a00a-2310a5499586 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.17 - Stripping of formwork
label | b78ad0ee-ce75-5bf8-a4e7-71063b9dbe23 |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 4.4.5]
label | 43ba6bc3-da12-545d-ae36-ab403fa8c67b |  | note | Acceptance Criteria -
label | 6cd64397-2edb-53a7-ae79-2d11976e9db3 |  | note | – – – – – – – – – – – – – – – –
label | 3634817d-c0e6-5a92-ab62-bedba13f351e |  | note | Member Type ¦¦ Member ¦¦ *Effective Span mm ¦¦ Minimum Stripping Time (days) for Average Air Temperature during period prior to Stripping
label | 6ae43905-bc65-5364-a233-518ef2a97749 |  | note | – – – – – – – – – – – – – – – –
label | d0a1f88e-ded6-5ddf-8344-87ba9552b91c |  | note | - ¦¦ - ¦¦ - ¦¦ 20°C and over ¦¦ 10°C to 20°C ¦¦ 4°C to 10°C ¦¦ Under 4°C
label | 5ca78118-9e46-5b2e-b6ce-aaaf2274ca09 |  | note | Vertical Unloaded ¦¦ Wall, column, beam side, slab side ¦¦ 0 ¦¦ 2 ¦¦ 3 ¦¦ 5 ¦¦ 7
label | 65b48f7f-ef57-5d4b-82f7-26b43f9ddc6f |  | note | Vertical Loadbearing ¦¦ Wall, column Or loadbearing Structure ¦¦ 0 ¦¦ 5 ¦¦ 6 ¦¦ 7 ¦¦ 9
label | bca83872-b9a2-50aa-98fb-0c23386bcb8c |  | note | Horizontal ¦¦ Slab ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 7, 10, 14 ¦¦ 10, 14, 21 ¦¦ 14, 21, 28 ¦¦ 21, 28, 28
label | 4f5bde31-c5cd-5c06-8feb-82774a89ba5e |  | note | Horizontal ¦¦ Beam ¦¦ Under 3000, 3000-6000, Over 6000 ¦¦ 10, 14, 21, ¦¦ 14, 21, 28 ¦¦ 21, 28, 28 ¦¦ 28, 28, 28
label | 065d99fe-bbe1-5b83-ae8b-5895ce34a338 |  | note | – – – – – – – – – – – – – – – –
label | f7c8d477-0fe6-5a00-b53d-cbebdf4f5286 |  | note | * Effective span is the maximum distance between supports (either temporary or permanent)
button | 52909241-9928-5bfd-912c-7aec80d6e0c9 |  | button | Acceptance | Yes,No,N/A
label | 33084da0-58fc-5765-8b3e-04545d2b9972 |  | note | Key - S
label | 055b44d1-6ec5-59c7-9be9-9e7657566d62 |  | note | UGL Key - S
label | ab25919c-95c8-5f75-be1a-9156a2730489 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.18 - Concrete Repair (If required)
label | 422b1db6-8ec5-540b-a562-8831aae43bf6 |  | note | Ref docs - Spec. 0002 Concrete supply, construction, and grouting [Cl 8.7]
label | f29df1da-c740-5f81-a77a-b31b44edd96d |  | note | Acceptance Criteria - Defective concrete shall be repaired or replaced. The materials and techniques of repair shall be examined and approved by the Superintendent prior to the commencement of repairs.
button | 9ce212d9-c67a-50cb-9e80-0f1ae42780e8 |  | button | Acceptance | Yes,No,N/A
label | 413697bf-441a-549c-8661-dde6cf9123cc |  | note | Key - H
label | f82b7ce5-ec07-521b-a851-fee8287e2f8c |  | note | UGL Key - H
label | 82546829-f039-53b9-8405-7f66d36a84f3 |  | note | SHL Key - H
label | f24d9f47-633d-545a-9410-cfcbf23481d0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | abf68c34-e05a-56e8-8fcd-3283632938c6 |  | tickbox | Grout Placement Checklist
boolean | 0b7460e2-b639-5fdd-bc19-3d3d4961d3eb |  | tickbox | Approved Aconex Corro for Repair Methodology
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 Backfill and Compaction
checkpoint-status |  |  | checkpoint | 4.1 - Structure Backfill
label | 46372a5b-b455-5680-b945-6bc194633a68 |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.10]
label | 4919311d-aa7d-584d-853b-83c6ef5908f1 |  | note | Acceptance Criteria - Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
label | 95e76a2a-b343-5391-a948-c9423cc2dace |  | note | ○ Placed in layers of maximum compacted thickness of 150mm
label | 844e9fee-4e43-5080-9104-2da0335ed8d4 |  | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
button | 4489bf16-a6fd-5afc-aeed-50f4360c2914 |  | button | Acceptance | Yes,No,N/A
label | fc4d975e-c814-5945-9db8-9c067a9e074f |  | note | Key - S
label | 27e011ac-cae9-5a40-b10f-2356186d0855 |  | note | UGL Key - S
label | 0f15a42e-23c2-5a38-a1d7-973f9bef8774 |  | note | SHL Key - S
label | 1c3b04ae-705b-53fc-a14c-2a8ae1b54d65 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 20050dd1-eef8-52c9-a4eb-0d8e34d7a56d |  | tickbox | Material Test Report
checkpoint-status |  |  | checkpoint | 4.2 - Compaction - Backfill
label | 3e35a1e5-f954-59bd-affa-825c4f7f6683 |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
label | 697c6ab0-40af-5bfd-8634-596ca012b392 |  | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against structures to be:
label | ab21886a-fc8b-5f79-bc24-bcc7cf87d2e9 |  | note | 92% for general fill
label | 054b33e8-b239-5d6b-8049-8873e4738dd0 |  | note | 97% for select fill
label | e6f29b1a-5cfe-5280-ad3a-c2dd53b532ab |  | note | ○ Test Frequency = 1 per layer
button | 5d27d9ad-e736-5bb7-86b5-3b8e8ee91516 |  | button | Acceptance | Yes,No,N/A
label | 3bbd0efb-0650-56b0-b429-908716b62c66 |  | note | Key - S
label | 80346087-7909-5291-8281-16cb3b24497a |  | note | UGL Key - S
label | 80bbb21a-e761-5601-934e-0e131475e428 |  | note | SHL Key - S
label | 931105e4-e245-5af2-afa4-daa9a92676b0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2670363d-66c9-5200-ab2d-0952e40854ad |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 4.3 - Moisture Content
label | 7a7053b7-8672-5cea-8d8e-18b71cdabd79 |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13 & 7.1]
label | f36b8884-6692-58d9-ad9b-64ec46493d04 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 90% OMC unless otherwise approved by Superintendent
button | 33d32df2-62f4-5231-b170-1db13f7fe150 |  | button | Acceptance | Yes,No,N/A
label | f435f174-31cc-5d44-8480-72c8e81d5d04 |  | note | Key - S
label | 7b8ab75d-d015-53d7-8331-7c29220d3cdf |  | note | UGL Key - S
label | 20e1e576-1127-5e06-9a06-a2af3862882c |  | note | SHL Key - S
label | 83d8935a-1259-5606-a73c-39304f6c780f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7be1012a-98a5-5a48-a854-704a19a64d23 |  | tickbox | Test reports
checkpoint-group |  |  | section | 5.0 Conformance check
checkpoint-status |  |  | checkpoint | 5.1 - Survey Report
label | 708daad9-9978-57fc-ae0a-fb854b5f173f |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], AS3610
label | 600d7a82-f9c0-57df-85d3-cfc5b647cd3d |  | note | Acceptance Criteria - An as-built survey of the structure has been completed to ensure all structures are within the following construction tolerances:
label | 0b0b11f6-41b5-5ee0-a370-abe900895212 |  | note | ○ Absolute position in plan shall be within 10 mm.
label | 587a2059-aeec-5ae8-b28c-49834c827fa5 |  | note | ○ Floor to floor plumb shall not exceed 0.002 times the dimension between the floors or 10 mm whichever is the greater.
label | b3f23b54-583d-5fdb-874e-2b2cec7422e0 |  | note | ○ Deviation from the specified dimension shall not exceed 0.001 times the specified dimension or 5mm, whichever is the greater.
button | 88eb668d-054f-5526-b33a-6344059ca5bf |  | button | Acceptance | Yes,No,N/A
label | d611b2c3-ba33-554c-94b1-8a32adc57c22 |  | note | Key - H
label | e0ec5a52-2975-5feb-8338-f0773f002605 |  | note | UGL Key - H
label | e7164dcd-4052-5a5f-aa38-67000b284a2a |  | note | SHL Key - W
label | 72c059d5-9f6a-513f-b010-b671947720d5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f608f85d-9724-5558-a608-d52415ef07ac |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 5.2 - Concrete Test Results
label | 8f8d6469-9cf5-5b4c-a8c3-6b2d2e08efea |  | note | Ref docs - Spec. 0002 [Cl 8.2]
label | e0f9ace5-c1e4-5d9e-8908-a684837fc3c0 |  | note | Acceptance Criteria - Certificates received, reviewed and conforming to requirements for each pour.
button | 4eb426c9-04e2-55d0-abf4-fe181d72f51e |  | button | Acceptance | Yes,No,N/A
label | 20061a7a-5f8c-51c5-9351-d432e534dba5 |  | note | Key - S
label | a766aa19-7ea8-5fbd-a66c-02024c6500a6 |  | note | UGL Key - S
label | 8c6d4835-5123-5219-91f4-0dbc945d2ce5 |  | note | SHL Key - S
label | c5087528-47a2-52f8-84e4-a7f217c61482 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2e5bd544-d118-5cb3-a268-9597d0e12e63 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 5.3 - Acceptance and closure of non-conforming items
label | 3166a3ea-35ec-52fa-a7b4-e8afe287b1b5 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | a97e207a-dc87-56eb-8f94-be71c9f6ed03 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | fb0f58f4-8506-5e79-9967-b9bd22f29960 |  | note | HOLD POINT
button | a1050b07-a080-5db0-ae9c-9af6c043f2d6 |  | button | Acceptance | Yes,No,N/A
label | 18d782fb-0300-5222-a6ac-1c741db11a64 |  | note | Key - H
label | a7a6af0c-0d7b-5d15-87e3-cb755c116a0a |  | note | UGL Key - H
label | bb7531ae-cf89-5a87-9f04-0dd3a978962e |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-007 Open Drains & Checklist - Rev.6 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-007 Open Drains & Checklist - Rev.6 | 2ba1c65d-33d9-4f70-b00a-487e128eebfd
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | cb1af059-92ef-57b0-b189-d829063a61f0 |  | note | Ref docs - Issued drawings / Site copy drawings
label | d9c6bc60-adca-5c0b-abd6-848338a60a33 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | ceb05951-4058-5384-b24b-fa8732646761 |  | button | Acceptance | Yes,No,N/A
label | a9b016f3-56bb-5d9d-87e5-f82fea58eae0 |  | note | Key - S
label | 3c97ec97-2afe-589b-a2f3-8393c0ea0d4d |  | note | UGL Key - S
label | 055f3f57-8536-5ede-bc8a-25ec973188b4 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | 133b1472-e4a3-567c-85be-c436467c7f6d |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | 9af5b6a6-1fa2-55c2-b256-9b138fa2d577 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot of map
button | 19b13a98-3135-5798-9bc2-7cbf345335b4 |  | button | Acceptance | Yes,No,N/A
label | a5fc2a47-c325-54c2-b56d-2e775fbf319c |  | note | Key - S
label | 81ccc1ad-752e-5c2b-83a0-ca10198633da |  | note | UGL Key - S
label | a2ca0971-77ac-5365-8f60-8e8d02e4e4d8 |  | note | SHL Key - S
label | 11996465-0c9c-53b8-b0ce-16902be48f55 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 21187f9a-ef77-5a5a-bde6-f17ce714207f |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Concrete Mix Design
label | af6fce5d-2639-5f6e-82a3-bce33f568dd3 |  | note | Ref docs - Spec. 1121 Open Drains [Cl 3.1]
label | 0aae758d-6e55-530d-b390-253e5de7ea14 |  | note | Acceptance Criteria - Submission of Mix Design and compliance certificates for concrete constituents
label | 248a4d81-0bb4-5325-9195-df24c0443c5d |  | note | HOLD POINT
button | 2ea28e9c-60f8-5215-8d73-da07fb600bf9 |  | button | Acceptance | Yes,No,N/A
label | 3ef9a6c9-9e44-5cc8-866b-1b6c13aa3276 |  | note | Key - H
label | b8df22db-8685-581c-bc38-bfb9ecfa07cf |  | note | UGL Key - H
label | 1ed66390-e1f7-5b2d-a45c-cea1ecdec522 |  | note | SHL Key - H
label | 4c6081a2-b14a-55fd-9115-c72880928a94 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 3c2426de-ad70-5719-98e9-5f3ccec4c91a |  | tickbox | Material conformance certificate
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.4 - Materials
label | 91cba01d-a891-5a1c-89e7-abb586fa44d7 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 3.0]
label | eb299376-870b-5666-84da-53cabbdadd76 |  | note | Acceptance Criteria - Submission of compliance certificates for joint fillers and sealants, proprietary products, wire mattresses, gabions, rock fill, and geotextile.
button | 7c4c48f5-6257-5904-866e-e80b2f97fe26 |  | button | Acceptance | Yes,No,N/A
label | 944093b5-696d-5111-a5fe-78f799d18221 |  | note | Key - H
label | e0c5752f-e17e-50c6-850b-2151f450c75b |  | note | UGL Key - H
label | 90ad517a-ce99-5e47-8a0c-41ebbaf0931c |  | note | SHL Key - H
label | 1ea92a57-09b0-51bd-9085-3c2017dfa9fd |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2653d2db-9eaa-56f8-b1c5-ae8222602760 |  | tickbox | Material conformance certificate
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | 77b10b66-2b53-5fcf-bc0c-acf645783192 |  | note | Ref docs - Underlying Lot ITP
label | 108b5f32-8fae-557f-b445-cea81627277b |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | db295ecc-494b-5a18-ab95-71501fa4ec3d |  | note | ○ Refer underlying lot ITP(s)
button | 1144325b-76f6-5540-a939-c26f103ad271 |  | button | Acceptance | Yes,No,N/A
label | 564b0563-a0cb-5200-8f9e-5cce844153b2 |  | note | Key - S
label | 4ff0d40e-153a-5663-9db2-27294bc71584 |  | note | UGL Key - S
label | d29777b6-40ca-5f37-a902-6f1e0625453a |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Survey set out
label | 0f9ccf4b-4037-5a22-abc5-f51653f385d3 |  | note | Ref docs - Drawings
label | 4c8a7962-0516-5b4f-9a68-6adca57f7420 |  | note | Acceptance Criteria - Has the set-out alignment been reviewed by the Superintendent?
button | 6e9f0ba2-13f0-5f5b-a0c5-f04d8690d548 |  | button | Acceptance | Yes,No,N/A
label | 959e75d4-2002-57cd-a579-50a7d77352c2 |  | note | Key - S
label | a8508106-cb3b-5b1e-b23b-4dd3fb9592f0 |  | note | UGL Key - S
label | 852c7b59-099c-5bf1-9d8d-259748ac4b72 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Open drain
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | e5e80ee7-7fe0-5695-bb9a-56c60ddec7a4 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
label | 5e064644-c056-58b5-8752-283e9ffb1e2c |  | note | Acceptance Criteria - Excavate to dimensions shown on drawings or where not shown to a depth of 300mm and minimum water way area of 0.2m2
label | 2e9cd7a1-223f-5e97-8a3b-77fa2e7fc3da |  | note | ○ Cross section: V-shaped or trapezoidal unless otherwise shown on drawings
label | 9d6b7051-491f-5203-962e-2ddc7b5d4e4d |  | note | ○ Batter slope: Not steeper than 2:1 (H: V)
button | 45837fd8-69d9-585e-bb80-182623af7ae0 |  | button | Acceptance | Yes,No,N/A
label | e5c6ffb0-084e-587b-bea6-9bd02e2b0a2d |  | note | Key - S
label | 9ee8fc5d-bbaa-5148-a22c-ff3435979ce5 |  | note | UGL Key - S
label | bd8b0796-e20e-5a09-a741-b362357e085d |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable material
label | 49de9350-9176-533a-afea-25c6df3af6d2 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
label | 3e240359-f176-5029-a361-c15f30cc1f60 |  | note | Acceptance Criteria - Notify the Superintendent of any unsuitable material and seek direction for removal. Dispose and replace material as directed.
label | 0b2abcf3-492b-55e0-80c7-5ca27706a9b3 |  | note | WITNESS POINT
label | b5d14a2d-a7be-5d22-bdcd-b14254be2151 |  | note | Notice: Progressive
button | db2914d5-7379-552e-a69e-ac75a0f41fa5 |  | button | Acceptance | Yes,No,N/A
label | c7757f45-74b8-5e18-84df-6134def22836 |  | note | Key - S
label | 6de31129-2f10-5661-90c4-a76467581349 |  | note | UGL Key - W
label | 0bd38e2a-6b19-5bef-aca2-2b22ea8534c2 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.3 - Embankment
label | 803698b6-26c4-5205-83b4-31a878145b5a |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
label | 760fb443-4c67-5cb1-b571-9cd63cf3735d |  | note | Acceptance Criteria - Construct embankment in compacted layers of max. depth 150mm.
label | 9716d428-6a4d-564a-ae6f-020810815f52 |  | note | ○ Revegetate the embankment after completion if necessary
button | 435acaef-a5c9-585c-9a55-a443f7dccc4b |  | button | Acceptance | Yes,No,N/A
label | ff1e99f1-999d-574d-8e74-4d92a642fe9c |  | note | Key - S
label | e359fa76-8ae4-57ec-bd8f-80a2af2ab5fc |  | note | UGL Key - S
label | abf13b88-94d9-5062-be3a-b57ce6649302 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.4 - Embankment compaction
label | c8c10ade-353c-519a-87dc-b106dc802567 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
label | 293de267-5f32-5e73-9600-7a1f1bd6e60d |  | note | Acceptance Criteria - Compact to a density equal to the naturally occurring material or alternatively to 95% standard compaction
label | 1d6f0899-27fd-5e6a-ba21-d0549227b119 |  | note | WITNESS POINT
label | ab2a937f-abd7-5f96-b121-5f005fe68766 |  | note | Notice: Progressive
button | 58dbda59-c317-59a8-a02c-7ef9346fe036 |  | button | Acceptance | Yes,No,N/A
label | e2aef0d0-2fd0-50ff-a324-0ab4e315ac98 |  | note | Key - W
label | 57bada76-1c91-569f-8a69-1c42e565e8d3 |  | note | UGL Key - W
label | 2fe61b54-f180-5538-9068-b485251aa001 |  | note | SHL Key - W
label | 8947e3dc-428d-5de5-bac7-e8706dbb6e1d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 4a1d49e1-0ae6-5abe-8dee-8ddd54cec111 |  | tickbox | Test report
checkpoint-status |  |  | checkpoint | 2.5 - Open Drain Construction
label | 2c7873a9-1f2a-5fcd-b499-7f25b24e7239 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.1]
label | 003b368e-8e76-5cd4-90e5-414ad92eed9a |  | note | Acceptance Criteria - Ensure free flow of water and minimum grade of 0.5%. Discharge into natural depressions, culverts or pits
label | 90fa97b9-f04e-5731-826e-a16cb76164e6 |  | note | ○ Compact any surface to be lined to 90% relative compaction
label | 03c71929-b78d-5cec-8abe-679613fea72e |  | note | WITNESS POINT
label | a802e533-6177-5b61-99d5-4ecbc5292931 |  | note | Notice: Progressive
button | 21a79f0f-06a1-53f5-8bbc-96a64cc5708c |  | button | Acceptance | Yes,No,N/A
label | 175d45e5-e5fd-5123-a15a-1fd47e0b132a |  | note | Key - W
label | 569a0b49-9bd7-59d8-bb1e-35cdc599bb52 |  | note | UGL Key - W
label | c4f39158-c35b-5614-bf3f-52b1ef4ce113 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.6 - Open Drain Lining
label | 2c25122c-635b-53de-b814-c05a889f4b23 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
label | 0ec70c4f-f677-5366-8c8c-f14a9cc15a57 |  | note | Acceptance Criteria - Unless shown otherwise on the drawings use the following linings:
label | 7381146a-af9b-53d8-b3a5-5e103744cc55 |  | note | – Organic fibre mat and vegetation for grades 1-5%
label | b3e224d3-1076-5b6a-a5c4-c7324ba3f3a2 |  | note | – Concrete for grades <1% or >5%
button | 2e9b46a4-0930-54e7-ae77-d2b000bff565 |  | button | Acceptance | Yes,No,N/A
label | e763a409-26a3-5c34-965c-cd0fbcd5e38c |  | note | Key - S
label | a486ab9b-a597-5fbf-9893-33aaa84e67f3 |  | note | UGL Key - S
label | 41d0cfef-efcb-5d2e-ae54-a33526a9fa35 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.7 - Proprietary Channel Linings
label | 740f63d7-f77e-5208-9cfa-87bad5560f63 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
label | 342851de-10b7-54c0-b7df-29fb674a65ab |  | note | Acceptance Criteria - Install as per manufacturer’s instructions
label | ea9e9b93-6d62-5fe8-a3b9-cdf5fb181c1f |  | note | WITNESS POINT
button | f5fdacc7-55f7-5d30-bb6f-6b0b15b2f3c8 |  | button | Acceptance | Yes,No,N/A
label | e6fe022f-eef2-5085-9370-b64d9b4eeb18 |  | note | Key - W
label | f04a5ee3-63c1-5b1e-930b-77013699c3f8 |  | note | UGL Key - W
label | 6b954ac5-cc90-5d89-a386-70abdbcb5a78 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.8 - Concrete Lining Construction
label | 15f52d11-a9e9-5e95-aad5-221ac80172b8 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
label | 0c7fb856-8a44-57c4-9c4f-ccfddd4af81a |  | note | Acceptance Criteria - Minimum thickness of 100mm or as per design drawings. Free of humps or irregularities
button | d462b4dc-9ce9-57b6-af64-e53a131b2ddd |  | button | Acceptance | Yes,No,N/A
label | 2cc5dad1-a9b4-50ee-bf2a-51b721896fcd |  | note | Key - W
label | f1a671bd-169c-5518-affb-da523fed4aad |  | note | UGL Key - W
label | 1803d635-5a1b-5cb5-be4f-9149796a7c64 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.9 - Concrete Lining Weepholes
label | 4dd3f88b-8c8b-5ff6-9fff-527c2caf52f0 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.2]
label | af382a64-9af7-5ce6-8d5c-3a8bc166010b |  | note | Acceptance Criteria - As per design drawings or at 2m spacing in non-horizontal elements
label | 2f03c3d9-aeef-5e92-90bf-d7941b0577d5 |  | note | WITNESS POINT
button | b89ba3d3-dd7c-50a5-8b4f-e520b55fc369 |  | button | Acceptance | Yes,No,N/A
label | 70389a67-3578-540d-9380-dc2358532fbe |  | note | Key - W
label | 1258e541-163d-5559-b609-83e011a7a458 |  | note | UGL Key - W
label | d34ab789-19c4-53ab-b1e2-9fbccad0db9f |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.10 - Concrete supply and placement
label | ef90a5ec-3c23-5a4f-b221-1c777a298a76 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
label | 78a42a42-e8b5-5bb0-9def-9be3836bc91f |  | note | Acceptance Criteria - Check docket to ensure strength and slump is as per design requirements
label | 09d18e90-7a07-5dd4-afcd-7d9d89353098 |  | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | db29c4e1-65b5-584f-9139-880908734a9e |  | note | – – – – – – – – – – – – – – – –
label | d1d6bb38-debc-53e0-ab13-4dc48c1001d2 |  | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
label | 3cba222e-57f8-571f-a0f6-6fe534497194 |  | note | – – – – – – – – – – – – – – – –
label | 36dddae3-ec22-5f8a-8cd9-28c37f78a39a |  | note | 10 - 24 ¦¦ 2.00
label | e31da2ba-ec86-5047-93c7-96dbab6eabac |  | note | 24 - 27 ¦¦ 1.50
label | 8bbe6dfa-f3a2-5218-a79a-300fb4a4b298 |  | note | 27 - 30 ¦¦ 1.00
label | e2cb0770-a07c-5a14-9685-c7d30ed978c8 |  | note | 30 - 32 ¦¦ 0.75
label | 33db4320-0fac-5aa8-9060-d51acaa50235 |  | note | – – – – – – – – – – – – – – – –
button | a2a2d937-b253-5849-a534-ac91d84abf31 |  | button | Acceptance | Yes,No,N/A
label | 4f977cdb-b95a-50e2-ad4a-fe99d17e023f |  | note | Key - S
label | d8b505b8-9016-52a7-930e-7aea313bca28 |  | note | UGL Key - S
label | 6aace5a1-e7a6-574a-aa48-7d4241e09a97 |  | note | SHL Key - S
label | fba6dafc-8587-508f-97bb-f2d7b2187e00 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | afbf4759-886e-5b8c-abfa-f8fd3225eeeb |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 2.11 - Concrete sampling
label | e4e63284-81a5-5027-ad09-43dcf9a9f88c |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | dee8856f-d3c1-535f-b885-326e8409b279 |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken as:
label | f76a399c-d92f-5663-81ed-3a22cc49cf5a |  | note | (a) Compressive strength: See table below
label | b262d1ee-1a07-5ab6-8fb9-ac430dffb779 |  | note | – – – – – – – – – – – – – – – –
label | aded2ee9-e894-5d9e-8478-369c1899cfd8 |  | note | Number of batches for each type and grade of concrete per day ¦¦ Minimum number of samples
label | 16867d9a-e97a-5a51-a7b0-ed797b968621 |  | note | – – – – – – – – – – – – – – – –
label | d894025f-7b70-5c75-a7dc-bcced2fa7be1 |  | note | 1 ¦¦ 1
label | 8e3fab72-322c-58a8-b181-fb63b62b76f3 |  | note | 2-5 ¦¦ 2
label | 7a19848f-21bb-5e09-a23f-390aa95dad79 |  | note | 6-10 ¦¦ 3
label | ab1a25b7-edfe-5638-882d-974ec3fdc9ce |  | note | 11-20 ¦¦ 4
label | f3ce4932-e9ae-532d-9d50-baf8867b7491 |  | note | each additional 10 ¦¦ 1 additional
label | e7b7c8d8-aa05-5c11-99a7-2a25ef76c225 |  | note | – – – – – – – – – – – – – – – –
label | cb9276d7-4432-5f5a-867b-70e19a4a55f4 |  | note | Slump: One per batch of concrete
button | c00ff1c1-f157-5980-b74b-79b51b8a8668 |  | button | Acceptance | Yes,No,N/A
label | 90769fbe-ee68-52ae-be12-cd72546e813e |  | note | Key - S
label | c2da4c6e-7f26-5324-a371-bbfee19dab76 |  | note | UGL Key - S
label | 2db1aa6e-5323-528b-bf13-7abce2dd1b6d |  | note | SHL Key - S
label | e4da179d-2f79-50e7-96b5-79fa27727707 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ad586d73-5d78-5dfb-bc28-f2b108725273 |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 2.12 - Concrete testing
label | 93a418a7-ea30-57a6-9f66-2407878af263 |  | note | Ref docs - Drawings
label | 3ff747eb-936e-5da3-b0f6-1e202ca67ac1 |  | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
label | 85b2be7e-64ef-5dfd-86f1-8303431a2806 |  | note | ○ Slump within tolerances specified in AS 1379
label | bc9f60ef-a480-5f83-ad08-0d7853fa1e81 |  | note | – – – – – – – – – – – – – – – –
label | cebd25fd-453f-54b1-840c-917c8bceeaaa |  | note | Table 5.1 Permissible Tolerance on Slump
label | 3b78b4a4-dc94-50bf-b156-ee5fdd849993 |  | note | – – – – – – – – – – – – – – – –
label | 18a61c8d-be18-5904-b935-e7d4f7604c51 |  | note | Specified slump, mm ¦¦ Tolerance, mm
label | c1c51386-4b3d-5f31-b68f-71e393823386 |  | note | – – – – – – – – – – – – – – – –
label | 4fa20b7b-98b7-5839-9dfc-aa37200c86ac |  | note | <60 ¦¦ ±10
label | d6f81e58-64d6-582a-b366-be1e45d67225 |  | note | ≥60 ≤80 ¦¦ ±15
label | bb5c8c7f-b789-57c8-bbcb-b10bb9546dbc |  | note | >80 ≤110 ¦¦ ±20
label | 5b4ac936-dd49-54bd-bacc-01a13b3ed015 |  | note | >110 ≤150 ¦¦ ±30
label | 844e13c0-7ca5-5410-8a6a-40a45c7378c6 |  | note | >150 ¦¦ ±40
label | a7308dda-9e35-572a-98e1-c95648f93a1e |  | note | – – – – – – – – – – – – – – – –
button | ad063fb4-d9eb-5d9c-9a61-20e95f5d9ab2 |  | button | Acceptance | Yes,No,N/A
label | 27a9add7-677a-52b0-8350-9f68369e8bab |  | note | Key - S
label | 37b2bd35-1d36-5890-8739-da8b3e7f6276 |  | note | UGL Key - S
label | 5b72b9b2-f9ba-541c-aa41-677d24223d88 |  | note | SHL Key - S
label | f9a8b9cd-02bb-5249-a0f6-ee6836cfd3c8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | faba44b9-0931-5163-a8ac-3e4eb3e3cae6 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.13 - Joints - Contraction
label | 99579e45-ba05-5c35-8c79-3750b2021a0b |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 009dd210-fe5b-50e6-92f8-6d0fa152ceff |  | note | Acceptance Criteria - Contraction joints to conform to the following:
label | 7ae65602-788d-5d6f-8266-39255e111bea |  | note | – Width: 5mm min.
label | 366425e8-351c-572b-9c63-8ea29bfd3731 |  | note | – Depth: 20mm
label | 02fd72fb-85ec-5f74-b178-980862d6652c |  | note | – Intervals: every 3m
button | 6fd6b844-5f67-5ec6-9aaa-eab71c88adf6 |  | button | Acceptance | Yes,No,N/A
label | 6420ad94-59dc-5d21-bcc2-84faecb3f042 |  | note | Key - S
label | 9855a15d-ab68-51ba-a9e8-9cea0e3294ef |  | note | UGL Key - S
label | b68260f4-d8dc-5b24-ba36-1b8208efdcdb |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.14 - Joints – Expansion
label | 2ded28ea-3428-5654-a3da-db97da144d73 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 5d95604e-d29e-59dd-9c1e-38f98f8cd3aa |  | note | Acceptance Criteria - Expansion joints to conform to the following:
label | 68766d70-8e3e-5e26-b6bd-d0003e202750 |  | note | – Width: 15mm
label | 3cbd8c56-533f-5392-8875-be11306401b8 |  | note | – Depth: Full thickness
label | 066e7660-3dd2-5eb7-ad5f-59f45d3b9ec4 |  | note | – Intervals: Max interval 15m
button | fc4d87f8-27e1-5f39-b556-b920a256ab77 |  | button | Acceptance | Yes,No,N/A
label | 2fc91c3c-1168-52d8-8226-9d3fb4514b29 |  | note | Key - S
label | f4cdeba9-c322-5d8e-a7cb-0ddb6f5c97e3 |  | note | UGL Key - S
label | 2b449869-12a1-55cd-82ae-c10bd71f52e0 |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Rock Mattresses and Gabions
checkpoint-status |  |  | checkpoint | 3.1 - Foundation
label | a4c08c9b-4d96-5edb-b9e0-288d55d4ecd4 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
label | 1e5b09b5-a8d6-5577-b9c7-d6bc96ec6d6d |  | note | Acceptance Criteria - Shape and compact foundation material to 95% standard compaction
button | 668f7ef9-5b5e-5804-85dd-fa294051e70b |  | button | Acceptance | Yes,No,N/A
label | 8cce07a3-9927-53df-aef0-e11de59af3f4 |  | note | Key - S
label | ebb23c3d-46f7-5a59-a76a-f3903cdf3ee8 |  | note | UGL Key - S
label | 0030be6d-de02-5afc-95ce-1aa97fac8ee8 |  | note | SHL Key - S
label | 70c74a33-d48b-5b89-ba87-3be0f961fce7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | b4d577d0-866f-55ed-80f4-3810023678d2 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.2 - Geotextile
label | 3710c70b-5c32-53d8-ad88-2c49173e4a4e |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
label | 8b1b96ca-81a0-500d-91cb-9da6ab8eb97d |  | note | Acceptance Criteria - Place geotextile between the foundation and any wire cages
button | af18b41b-9880-5fde-ad63-a86f01f1f1d9 |  | button | Acceptance | Yes,No,N/A
label | d0cf404b-bafa-5994-bdf4-4320e2723c75 |  | note | Key - S
label | 24ef7cfa-3420-53bc-8bd9-f8d7fabca122 |  | note | UGL Key - S
label | 1b145bac-e834-56a6-94ea-f3b05ac3329b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.3 - Assembly
label | d98c3284-3fa3-5299-89b7-6da3fb2db71c |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
label | c425f4a3-8a5e-54f9-8fb9-d48a7e477df5 |  | note | Acceptance Criteria - Assemble and lace the rock mattress or gabion cage as per manufacturer’s instructions.
label | 45a9e933-66d3-5919-aab8-1f7ab51ed598 |  | note | ○ Secure the end of a new cage to completed works or with galvanised star pickets driven in to the ground.
button | f8012629-57ea-59c2-9490-1d3155eae0d3 |  | button | Acceptance | Yes,No,N/A
label | dce0694c-0792-59f6-b40d-c0dc9afd1230 |  | note | Key - S
label | 0381c0e8-29c8-572d-8359-a3213833d3c5 |  | note | UGL Key - S
label | f584064e-3221-572f-bc58-6f55afe3c47b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.4 - Filling
label | 6fbe8148-2605-5423-8e92-445b1be2eeb4 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
label | a18a75d5-e23b-5567-b764-fb44d287a83b |  | note | Acceptance Criteria - Fill boxes whilst under tension and only release tension once fully laced. Ensure cages are fully filled and uniform.
button | d015c483-1019-59b2-8fd5-bbe80d510ef8 |  | button | Acceptance | Yes,No,N/A
label | 8147712b-477b-5350-afdc-9d5a87d4544f |  | note | Key - S
label | c33e72fb-44a2-5c97-8a55-4ad7314d933f |  | note | UGL Key - S
label | fe7764ec-0e30-5534-a00f-b36c2a430e73 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.5 - Completion
label | 470d146e-e51e-5455-bba6-86e43fea0e6d |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.5]
label | 79d85a87-a08e-5a8a-9619-faeb5f5e5fdb |  | note | Acceptance Criteria - Inspect rock filled mattresses or gabions upon completion
button | ad3c0801-f9ec-5bf2-b998-20b8e5617bbc |  | button | Acceptance | Yes,No,N/A
label | bc4086e5-10bb-5d5f-bb6c-4cd6be78388c |  | note | Key - W
label | 65255746-a61a-5c44-866a-2c81d163e113 |  | note | UGL Key - W
label | 90aea2d4-8679-5cc0-b089-5cada4d82309 |  | note | SHL Key - W
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Survey Report
label | 643d6ab1-e5bd-575e-b415-8039be7600fb |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.6]
label | f563f1b6-bed7-5eed-a4b3-ce1eea012d2a |  | note | Acceptance Criteria - Survey report verifying open drains have been constructed within tolerance:
label | 167f9eac-bf83-549c-acb3-2d2336f35a20 |  | note | ○ Finish levels of channel/gutter surface: within ± 10mm of design level.
label | c6c8c8a0-c21a-5c6a-953a-a3bb45e19bc8 |  | note | ○ Surface deviation of kerb face and channel surface: ±5 mm from edge of a 3m straight edge, except at laybacks, grade changes or curves, or at gully pits requiring channel/gutter depression.
button | 6f683276-58e1-571f-b447-caa29b89e1a2 |  | button | Acceptance | Yes,No,N/A
label | 83f5d7b1-be53-59fe-9520-2d7b434536f3 |  | note | Key - S
label | 8927fafd-175f-5f68-a4c8-091264bb2f85 |  | note | UGL Key - S
label | b5aead4e-812c-5b83-b4b9-b33b171ad8d2 |  | note | SHL Key - S
label | c1f60aef-fcf8-5d69-a5dc-9348380de1fe |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 30a9d259-efaf-5ed1-aa57-8949443f3052 |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 4.2 - Acceptance and closure of non-conforming items
label | 20b71d5d-ae83-5539-aaf0-6167d0877637 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | a679a8cb-8e00-5e3e-a7aa-43494bea5307 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | f0311737-4b34-5d44-8ec6-32eb37a2ae0b |  | note | HOLD POINT
button | c067e98e-e4e6-5b46-ae85-49f42258e8b2 |  | button | Acceptance | Yes,No,N/A
label | a968e1ad-61c7-5124-80f0-ce16d93e5b12 |  | note | Key - H
label | 8d1f0790-8f5f-59af-888b-e270521a1925 |  | note | UGL Key - H
label | 92fc4f6f-7243-5843-bc42-61508c34af67 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-023 Light & Security Pole Foundations - Rev.1 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-023 Light & Security Pole Foundations - Rev.1 | 303a72c7-1083-4aec-aec3-9d3f1592fbb0
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 1d415336-d4c2-5d9a-8db9-c229dffaa13f |  | note | Ref docs - Drawings
label | 7fa252f5-18f9-5190-82c6-1a525bc2e780 |  | note | Acceptance criteria - Check the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | da29d844-6cf2-58ca-96b7-c4e02df3ec9c |  | button | Acceptance | Yes,No,N/A
label | 5000947b-072e-5dbd-96a3-b7d497d7ff02 |  | note | Key - S
label | 3b72413a-5bca-5b17-9ecf-106ce52f4ee0 |  | note | HPP CON Key - S
label | 97e356b6-2483-56c5-97d1-b52f82e78a2f |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 4746c940-0561-5950-b3ff-71a561236e39 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | ea79c6bb-5a6a-54fe-9951-631542b1c538 |  | note | Acceptance criteria - Prepare a lot map for traceability of the work area
button | 87be46a2-1b85-5859-9c66-5a543bd51a3b |  | button | Acceptance | Yes,No,N/A
label | 294c8daf-464a-5fdf-bdb6-44b7e6a8ce88 |  | note | Key - S
label | 1ebec481-9b03-52d6-9b8f-54c83c361827 |  | note | HPP CON Key - S
label | d9b0621c-1f2c-528f-8614-4c62a69b30cc |  | note | HPP QA Key - S
label | 8ec8f48f-849e-50d3-818b-8eb14c0ce2b8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | cbdbd655-a5bf-51da-abaa-9db4f687418d |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Set out
label | a71523cc-e43b-5ef1-b6ed-332c3fbd48ae |  | note | Ref docs - Drawings
label | 8cd22edb-4f30-5bfb-92cd-eb256054f38e |  | note | Acceptance criteria - Setout to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | cd0daa09-7fa1-5b36-82cf-3b277acaee91 |  | button | Acceptance | Yes,No,N/A
label | 99e83070-a10d-510b-bed6-ac5f5d95d0f3 |  | note | Key - S
label | 9574a8f3-45e7-5b88-9d2a-9090d9776e4e |  | note | HPP CON Key - S
label | f4eb36f9-7ef8-5c2d-8525-41cb56db78a3 |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 1.4 - DCP Test
label | 0eddb9a4-e744-509d-8bcb-8de3763e905e |  | note | Ref docs - Drawings Note 8
label | 6e699730-df82-59d7-8a4d-d1020fcd67d6 |  | note | Acceptance criteria - Conduct DCP test for each pole location.
label | 494c55b8-055a-53b2-82e1-e36c7b52aec7 |  | note | ○ Allowable minimum bearing capacity =100kPA must be verified by a qualified Geotechnical Engineer.
label | bf7d3d9a-5763-56e1-b2a9-a14e0a1d4d9e |  | note | ○ Ground improvement shall be made If existing soil profile is inadequate.
label | da120a9e-9922-53e4-81cb-9e4de26bbf3e |  | note | HOLD POINT
button | b781fc9c-4324-532b-8454-d1c2b2295e48 |  | button | Acceptance | Yes,No,N/A
label | b31a2e6f-dc55-5114-b903-7ffdeddf0b58 |  | note | Key - H
label | de8aee8b-9c60-5b28-9878-d9d9fa2d8da1 |  | note | HPP CON Key - H
label | 0b8a0df2-4642-54e6-a47b-d9a5b16ea4ff |  | note | HPP QA Key - H
label | da62b3a6-935f-54b2-b578-eb2854c6c0de |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 6cf15ae3-a356-504f-b0bd-b779670a9f50 |  | tickbox | Geo report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Base Bore
checkpoint-status |  |  | checkpoint | 2.1 - Bore Excavation
label | 9bda56a5-2aa3-5a3c-a75c-49af4c90e1e6 |  | note | Ref docs - Drawings
label | 13ada146-9c4d-5c98-8b20-fe194b351c36 |  | note | Acceptance criteria - Bore to the correct diameter and depth nominated on the drawings and remove any loose material at the base.
label | 95a06011-7be1-51cb-bc3c-6cca5daa4c03 |  | note | ○ 450mm – Light Pole & Joint Use Pole
label | 96da773d-96b8-5030-aa21-be2244611acf |  | note | ○ 600mm – Security Pole
label | 11dfabba-27bc-5692-a987-e401210c2b9c |  | note | ○ Depth to be verify by qualified Geotechnical Engineer.
label | 0d7d0628-a11b-522d-bc98-d68e77baf189 |  | note | ○ Base must be clean and dry to be inspected by the Superintendent.
label | 520d6c68-d869-50c7-8046-847a267e4dd4 |  | note | HOLD POINT
button | 39d6a889-6c8b-58bc-9376-58fa53d2bc36 |  | button | Acceptance | Yes,No,N/A
label | 7a6786bd-0fa0-5d46-a287-2470230c92d3 |  | note | Key - H
label | b9c63d72-fcdb-5eef-9ecb-653cc5e68810 |  | note | HPP CON Key - H
label | 819071d9-831b-5ec0-a824-1660623d6af9 |  | note | HPP QA Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Formwork Sleeve
label | 9ae55def-3a13-505f-b668-e637449fccb7 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
label | 9ef03baa-be5d-5b01-af0a-fbe1135c4ab8 |  | note | Acceptance criteria - Formwork to be set as per drawings and adequately supported and RL checked.
label | 118cbbcd-2e8d-56fd-9752-1dcd5d31f021 |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement.
label | d81f1c02-0cc0-50a0-a94b-d41d2ebc19ba |  | note | HOLD POINT
button | 6a8c1df8-f0cb-5c08-878c-84dc945da3cd |  | button | Acceptance | Yes,No,N/A
label | a8d71608-ddfd-5db4-a036-9ffc7f91b85a |  | note | Key - H
label | 8e553e50-9021-50bc-904b-9133c915feb7 |  | note | HPP CON Key - H
label | 49ee2794-c7bc-57c2-8156-773cda4ff761 |  | note | HPP QA Key - H
label | 0556def7-1b78-5ca3-a695-58c744cf2f4e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f7a2d040-4616-56b9-911f-8e2be56705c1 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Placement of reinforcement cage, HD Bolts and Earth Lugs (Supplied by Client)
label | ff1a1f67-f426-58d1-aa64-ec39a84303bc |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5] Drawings
label | eec2e430-1c50-5733-8ca0-2a11ae6e5e3b |  | note | Acceptance criteria - Ensure that cage is clean and straight. Plunge the cage centrally to bore hole and ensure spacers are attached at correct locations.
label | 325c8632-084e-593c-aa1f-9b526780e549 |  | note | Reinforcement cages and embedment to conform with drawings and specification.
label | 03c884d3-5c54-52de-b22e-d6da0d09f753 |  | note | ○ 4-M20 HD Bolts grade 8.8/S
label | bef67c26-6f7f-5a6c-a2a9-0666690243aa |  | note | ○ 500mm min embedment
label | 01e3bbbd-0fb9-5ed3-8e89-c6015ced20c2 |  | note | ○ 130mm projection
label | 400601c8-9e62-5df4-8395-a5e7d3f69af9 |  | note | Or
label | f3a490fd-f3a2-52b4-a04a-82e825b6a510 |  | note | ○ 4-M24 Bolts grade 4.6/S
label | 52de79dc-5a0f-5d11-a6ef-81ce8f46501c |  | note | ○ 600 min embedment
label | 4ae0b679-7e56-5438-82bf-587cf790ec19 |  | note | ○ 150mm projection
label | 1471b9dc-b16a-5636-8bd7-ab0547c6dd22 |  | note | HOLD POINT
button | 806bdcc5-a02d-54f4-bf73-639402de726e |  | button | Acceptance | Yes,No,N/A
label | b9665c93-66c7-5fe6-86b6-4ace1cce8719 |  | note | Key - H
label | 6ba9be13-1ae9-5c46-b16e-c933d8c4590c |  | note | HPP CON Key - H
label | e2c255e1-6c7a-5f58-9d08-4859acf6f67c |  | note | HPP QA Key - H
label | d71c0995-106b-57a9-9c84-6c5a071207ba |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 4966b010-8987-5b87-b6a4-b5744721ba87 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 Concrete
checkpoint-status |  |  | checkpoint | 3.1 - Concrete supply and placement
label | 5998fe3e-1d89-5b39-96f7-821e5983f252 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
label | 61ef8983-c674-5021-b9f3-eaa0ceba665b |  | note | Acceptance criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
label | fefb6498-79b2-52fe-a0e0-104269bdf33a |  | note | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
label | 2336ed73-b9a2-53c5-bf7c-f4324a43ff69 |  | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | 5671376d-a708-5948-a42b-43b1a23f6a27 |  | note | – – – – – – – – – – – – – – – –
label | be560ed9-2dca-5241-8590-9c50f54058c2 |  | note | Concrete temp at discharge (°C) ¦¦ Max elapsed time (hours)
label | 89e894c0-bb55-5376-ae7a-b6bc9e62f81f |  | note | – – – – – – – – – – – – – – – –
label | 6efbc748-7c9a-5b16-8ec9-277d5035eb7b |  | note | 10-24 ¦¦ 2.00
label | 6023461f-4bf6-53dc-8334-af79147382e7 |  | note | 24-27 ¦¦ 1.50
label | 3a43a3a3-9970-52a6-b42b-b4aa47af7ac2 |  | note | 27-30 ¦¦ 1.00
label | 74c91880-db00-5339-aeff-7935226f3ec0 |  | note | 30-32 ¦¦ 0.75
label | 1ae9314c-21ee-507a-bae7-0ecffa99aabe |  | note | – – – – – – – – – – – – – – – –
label | 46ad998e-fcbb-5106-a8bc-622f5bf82ab1 |  | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
button | d5e49e5c-aaff-58c9-99a0-3a67b0cc7fbf |  | button | Acceptance | Yes,No,N/A
label | 9c985240-1a18-5791-98b9-9b2de85fe2af |  | note | Key - S
label | f1585110-1107-52d6-801c-dee7eab9e559 |  | note | HPP CON Key - S
label | 644dfbf6-a341-5eff-81c2-5958f7615578 |  | note | HPP QA Key - S
label | d870eef0-d089-51d5-a7f7-dc4217344aa8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ccb8e5cb-c65c-522b-a685-32deaa6a0715 |  | tickbox | Material dockets
checkpoint-status |  |  | checkpoint | 3.2 - Concrete sampling
label | 5b077a56-1d4a-5e3d-ada7-b7330ed3e63a |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | b4ab27ab-e9ae-5f7d-bb45-ae7185d5f4ea |  | note | Acceptance criteria - The nominal rate of sampling shall be taken:
label | 2bf9c5cc-59ca-50ce-b933-7cc103da2380 |  | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
label | dd0ab810-db9d-596e-88e5-9bf5f3796e5e |  | note | (b) Slump: One per batch of concrete
label | 809b1601-6719-5f21-bd54-408a0abd370a |  | note | ○ Average compressive strength at 28 days meets minimum design requirements. Slump within tolerances specified in AS 1379
label | 781f7182-7c67-5855-aeb6-01f902c1578b |  | note | – – – – – – – – – – – – – – – –
label | ff290c48-15cc-56af-8b18-c271caa1dda5 |  | note | Specified Slump (mm) ¦¦ Tolerance (mm)
label | 152db6dd-8973-5ba8-8a74-13d6fc702ba4 |  | note | – – – – – – – – – – – – – – – –
label | 60055e76-7d67-5805-bdfb-15fc758075e2 |  | note | <60 ¦¦ ± 10
label | 3e80c47a-e6c6-53d5-a0b2-1526fbbbd133 |  | note | ≥60 ≤80 ¦¦ ± 15
label | f12de317-4e5f-562c-87eb-cdd74e20b067 |  | note | >80 ≤110 ¦¦ ± 20
label | 38d244ac-4896-584d-9085-3e02581f4c65 |  | note | >110 ≤150 ¦¦ ± 30
label | a4895b91-e502-55ff-9d5f-275288b23877 |  | note | >150 ¦¦ ± 40
label | dcd0f942-e87b-52c6-9431-ddb5d596961f |  | note | – – – – – – – – – – – – – – – –
button | cc72dc41-ddc7-51ee-b81e-60a85a0685b8 |  | button | Acceptance | Yes,No,N/A
label | 4c8a0273-23e2-5768-990e-c38ad1de036c |  | note | Key - S
label | a5314a3f-f97e-5c62-8210-8479ae0386eb |  | note | HPP CON Key - S
label | 0e874af5-e38c-54e1-aa06-03175b43148d |  | note | HPP QA Key - S
label | a00fb00c-ab00-5f89-81b2-358b42838d76 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ab32d41e-ec99-59ed-9143-ae7937c43ee1 |  | tickbox | Material dockets
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Survey
label | 5bf021cf-6837-58ef-bb7e-2f60e495f04b |  | note | Ref docs - Spec. 0003 Piling [3.10]
label | 0e530ee7-b1da-557b-8a59-c36b9c613b33 |  | note | Acceptance criteria - All piles shall be constructed within the tolerance specified below:
label | 9615617e-80f0-523c-a624-d9dd8029ea46 |  | note | ○ The centreline at the top of the piles shall be within 50mm of the specified position
label | c3dd1123-548a-5712-be1a-e5114450b7f7 |  | note | ○ The tolerance on the level of the top of the piles shall be ± 10mm
label | 111ece0a-f8d3-57dd-9cca-cd7c860f9d73 |  | note | ○ Piles shall be constructed to the minimum diameters specified on the drawings
label | c22e7237-3a85-50f2-a7fb-b6ad50724dc8 |  | note | ○ Length of pile/pile liner shall not be less than total length shown on drawings
label | 89c85987-f7c1-59a0-89c3-79a0be672d69 |  | note | ○ Review survey as build report.
button | a34c60d6-34f4-59bb-83d4-48a2bd0c6db2 |  | button | Acceptance | Yes,No,N/A
label | 4afc44ee-2529-5e3b-89c9-61fe09904e19 |  | note | Key - S
label | 0e64909c-6e92-53b3-87bb-e55d9752055a |  | note | HPP CON Key - R
label | 39846905-212d-5584-b130-1cb998813b8c |  | note | HPP QA Key - R
label | 3c25ca0a-0439-55ae-8023-2456569008e8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c6e76896-5998-5321-b09c-562b4caffc48 |  | tickbox | As-Built Surveys
checkpoint-status |  |  | checkpoint | 4.2 - Concrete Test Results
label | e68dbd3f-38da-52e6-8ba6-5b30162311a5 |  | note | Ref docs - Spec. 0002 [Cl 8.2]
label | 7390a9f1-479f-5c29-9b73-0104f6ca3056 |  | note | Acceptance criteria - Certificates received, reviewed and conforming to requirements for each pour.
button | 43d21ece-2e4e-56d6-b559-27b580b38b68 |  | button | Acceptance | Yes,No,N/A
label | f70be150-cf06-54e3-ba94-a287eca22eed |  | note | Key - S
label | e315478f-6233-5323-9a60-1e2a7f7c5d60 |  | note | HPP CON Key - R
label | f21eb127-b727-5bf6-bbf2-fbb42b37baaf |  | note | HPP QA Key - R
label | d44f6980-a2c3-5a16-9ee9-55f421f30071 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2f33bc09-4182-5d0c-98be-4a85ba7b70e2 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 4.3 - Acceptance and closure of non-conforming items
label | 390b15b5-15f4-5c4d-9fbd-eb566756a1d0 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | c55a4c1e-b747-581f-90ae-cc570b10ab95 |  | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 0502b9e5-e49f-592b-85ad-6eb4eb305e53 |  | note | HOLD POINT
button | 1c257cef-2997-5ad0-9012-1219104976c4 |  | button | Acceptance | Yes,No,N/A
label | 27ad7400-b4e6-5a6d-844a-126ef85e7f54 |  | note | Key - H
label | 2ac740c0-9fa8-5e39-ac6c-ffd3c0ca7e85 |  | note | HPP CON Key - H
label | 9f13406c-744d-546b-8a5a-1772ca0168dc |  | note | HPP QA Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-006 Kerb and Channel & Checklist- Rev.5 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-006 Kerb and Channel & Checklist- Rev.5 | 422d5cbd-0911-401f-8a4b-6b4b5f38d37c
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Determine lot size
label | 23ea0b50-77b5-5c36-a330-9f9dec534cb7 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | bf4552b6-5f5e-547b-a658-3b91c4a12d7c |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | dbd59763-1149-51b8-874e-d93885ac1474 |  | button | Acceptance | Yes,No,N/A
label | 6d112e99-e523-57bf-a1de-fc365598b2bf |  | note | Key - S
label | 8ab1b5a5-23ba-551c-9936-7df42f7d5c26 |  | note | UGL Key - S
label | 21be28a7-26f7-5a0d-bafb-6a360373a43c |  | note | SHL Key - S
label | 3326b6ce-6937-53c6-afa1-accc83a7260b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 83fa7cff-54c5-57a8-86d1-ede15aab5be2 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.2 - Concrete Mix Design
label | 83b8110f-5c7b-5050-94be-ec03f1917cf7 |  | note | Ref docs - Spec. 1121 Open Drains [Cl 3.1]
label | 2407ff25-909a-5c2f-b194-52226b4d21b6 |  | note | Acceptance Criteria - Submission of Mix Design and compliance certificates for concrete constituents
label | 818245e8-c747-5c13-a510-6da7ddac521d |  | note | HOLD POINT
button | d81e9743-cf6a-57c8-8b12-d61629348187 |  | button | Acceptance | Yes,No,N/A
label | 92113e45-14b9-5e16-a026-c0d9b2c79594 |  | note | Key - H
label | 0ca1712e-4eb4-5496-a250-a08433e010e5 |  | note | UGL Key - H
label | aa0597ba-42c4-58fa-b461-e688a0c71495 |  | note | SHL Key - H
label | 7cbb6f73-13fd-5f54-a663-c305ddb6f748 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ae6978c0-77fd-54f9-bd59-fea3718ba871 |  | tickbox | Material conformance certificate
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.3 - Joint Fillers & Sealants
label | cd06b79e-8038-5bd3-8131-ee241899aa34 |  | note | Ref docs - Spec. 1121 Open Drains [Cl 3.2]
label | 8e307295-83e9-5cfe-8786-c616626b4831 |  | note | Acceptance Criteria - Submission of Compliance Certificate for joint fillers and sealants
label | ac5b3ce6-91a4-5686-9011-1dc3f9e4d24c |  | note | HOLD POINT
button | 8ed8321a-6c06-5db1-bfae-bb2b4eb35423 |  | button | Acceptance | Yes,No,N/A
label | 2e89feb4-5321-5f04-b6bc-a48bb51e203c |  | note | Key - H
label | e329f753-b3e0-582c-999b-b5b90a9021d7 |  | note | UGL Key - H
label | 61b370bd-a1a6-51fe-ae98-120ab2a2519d |  | note | SHL Key - H
label | 70d4d324-4b50-5e5d-88f0-9e1ab4c87c49 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c56c580d-2afe-52b4-9425-1a92cb21c1ba |  | tickbox | Material conformance certificate
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.4 - Kerb & Gutter Methodology
label | 2caa9e64-6524-55c7-a3fb-ab4bfc7baa50 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 50b36497-e570-5cfb-92de-1eaad8091b85 |  | note | Acceptance Criteria - Construct kerb and channel in fixed forms, by extrusion or by slip forming to AS2876.
label | a1f8ba27-9b5a-5e11-a201-6aa67f5de930 |  | note | ○ Submit details of method proposed including type of extrusion or slipform, concrete properties, equipment and finish.
label | 7d7f5dbb-7663-52c0-9ba3-13ba692f576b |  | note | HOLD POINT
label | 6e727449-e18f-5e1d-8d3f-6e7da7f1ebc8 |  | note | Notice: 14 working days prior to commencement on site
button | be09df0c-e116-53c8-b8b1-281bc50260ab |  | button | Acceptance | Yes,No,N/A
label | a6c811dd-1474-5e19-944c-ed6788968865 |  | note | Key - H
label | 48676d81-2510-5a0d-bf2f-0fe2013a9c75 |  | note | UGL Key - H
label | 6f1e5d4d-2cf0-55c3-ad92-e768a75b997a |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | f4fea250-d06c-5167-b81c-f9c3f216097f |  | note | Ref docs - Underlying Lot ITP
label | 646f62ea-e06a-5445-9fd2-ee3f45685908 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | 42d23c79-4e3a-5767-83c8-16ba1185a139 |  | note | ○ Refer underlying lot ITP(s)
button | 6c5b9bdd-eaeb-5239-9759-8e62da0a3a13 |  | button | Acceptance | Yes,No,N/A
label | 04480635-2f43-578e-a13f-baefdb86d8be |  | note | Key - S
label | 0a3971e7-272f-5ba6-b924-2ed25d73e1d9 |  | note | UGL Key - S
label | dee5b9b7-2191-5e48-96c8-e3c88b13331b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Survey set out
label | 77abcd3a-40c7-57c9-99ae-38ffe3f200fe |  | note | Ref docs - Drawings
label | 90edc993-5b78-5c9c-a17a-53d22f3a31bf |  | note | Acceptance Criteria - Set out the alignment and level of the kerb
button | d0ea18b2-a1a5-511d-974a-6b0e92e94d48 |  | button | Acceptance | Yes,No,N/A
label | a52b960c-fb88-5c40-9cd0-17707e89b74c |  | note | Key - S
label | 102abc9c-d4d1-57ab-99fc-d5c4746cbb8f |  | note | UGL Key - S
label | 53dcbdbe-1de7-5ecd-8dc6-2f4d1fcf43c8 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Kerb and channel placement
checkpoint-status |  |  | checkpoint | 2.1 - Foundation
label | 33a63628-28fb-5d3a-b586-1b620df210bc |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 63d2795c-dac3-5061-a292-f561326173bf |  | note | Acceptance Criteria - Shape and compact foundation material to the requirements of the respective pavement course
label | 719cb626-5cd5-53b3-8107-f6124dcaa2c3 |  | note | HOLD POINT
label | c653fc30-322b-593a-97c8-c5800c785a76 |  | note | Notice: 1 working day before forming
button | f1a849c0-6749-5a9f-823e-27e3cf2c2d00 |  | button | Acceptance | Yes,No,N/A
label | 14fd45c0-8818-5a48-8966-1c98f18df920 |  | note | Key - H
label | 05d45c9a-9802-5ee2-a3eb-44978f7d3539 |  | note | UGL Key - H
label | 7c25a614-81d5-5116-bf78-b618f771c6f7 |  | note | SHL Key - H
label | 33306e45-55b3-58aa-984b-b08a7b8bcbc0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 65d5c97a-b9a2-590a-9f22-d8fb5e7b060e |  | tickbox | Test reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Trial section
label | 1ada370d-8446-589a-80e8-cc102a3d0302 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 26b8b368-3bcb-5f64-9516-f48d5912c317 |  | note | Acceptance Criteria - Construct trial section to demonstrate the Contractors capability of forming equipment.
label | 48d6fd31-c229-530b-b2b1-922fda532728 |  | note | HOLD POINT
label | 23b2e091-ac36-58ed-9611-ace02f7c8327 |  | note | Notice: To be completed on 1st section of kerb,
label | 451548e3-dde0-50bc-b639-c2f03e1361a8 |  | note | 3 days prior to commencing next section
button | 1ad99bfb-a3e6-5705-a95f-026a1a8f181f |  | button | Acceptance | Yes,No,N/A
label | f4f87e73-c47e-5dac-8cb2-dc49b5316c19 |  | note | Key - H
label | 4e275058-8f0d-52c2-857e-52cfd89ecc2f |  | note | UGL Key - H
label | 298ef5c2-2ae3-598c-afd0-172f7e06424f |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Concrete supply and placement
label | 6099a512-0efc-5168-8916-ee9a0d5929f1 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11] Drawings
label | a98a0acf-5d60-554e-b419-bc3872a869de |  | note | Acceptance Criteria - Check docket to ensure strength and slump is as per design requirements
label | 384f623e-a70f-5ecc-81f9-c278296ab75e |  | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | ef6f7f8f-c3e3-52ee-906e-634d257f68ee |  | note | – – – – – – – – – – – – – – – –
label | aa951040-7ab7-53f8-a06a-e7ee4c9c0d63 |  | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
label | e2561c21-9663-51d1-8d85-dcfddb52003f |  | note | – – – – – – – – – – – – – – – –
label | de080aa2-af0b-58a3-a9fe-96f42be61153 |  | note | 10 - 24 ¦¦ 2.00
label | dfef807b-df7a-59c1-864f-1f704815d66d |  | note | 24 - 27 ¦¦ 1.50
label | 4987f7aa-d964-57f1-bc4d-afebd4958fe6 |  | note | 27 - 30 ¦¦ 1.00
label | dbeb0c66-b74d-5843-b3c8-00752defc128 |  | note | 30 - 32 ¦¦ 0.75
label | ad708570-4d65-5318-ae09-3366756a11d3 |  | note | – – – – – – – – – – – – – – – –
button | d07fc7e4-6d9a-50df-8a73-642d62790c71 |  | button | Acceptance | Yes,No,N/A
label | 8212656c-6b1c-59d1-91e6-95bbb88dbdc2 |  | note | Key - S
label | 501f781a-e86b-5f99-978d-954a171793f8 |  | note | UGL Key - S
label | ba9306c7-f1c3-58ed-b74b-356d9af40ebf |  | note | SHL Key - S
label | 71d3fffe-840a-5970-b76e-7666239b443b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 30fa5370-6220-5269-9957-9a72678f54d7 |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 2.4 - Concrete sampling
label | 972a3878-27b4-5bed-a96b-df9d32dc3db9 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | 7f65886a-c3fb-5eba-8232-ad3306f53766 |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken as:
label | 322636c0-f9c7-5d85-bf7b-2cb26efdd3d0 |  | note | (a) Compressive strength: See table below
label | cb5f28b8-0172-54c6-bf9d-ac0f341f8acc |  | note | – – – – – – – – – – – – – – – –
label | fe1e0e03-44a4-58b8-a0ec-a1f1c3b3f367 |  | note | Number of batches for each type and grade of concrete per day ¦¦ Minimum number of samples
label | 92b1f8a1-fb27-5323-a047-80e7019f702c |  | note | – – – – – – – – – – – – – – – –
label | 05869597-a5fa-5696-ba3f-4d6cbf0971f4 |  | note | 1 ¦¦ 1
label | 75030b7a-9d53-5292-a2c9-4a6243e750fc |  | note | 2-5 ¦¦ 2
label | 55d680fc-aa4b-572e-a1ec-31cabd965549 |  | note | 6-10 ¦¦ 3
label | 7d4f0c7d-8997-5f92-afad-c005916ebd34 |  | note | 11-20 ¦¦ 4
label | 5982802d-e046-5ed2-ad97-02f0189088ac |  | note | each additional 10 ¦¦ 1 additional
label | 956dfb24-9854-531d-8dba-f3ee36d2ee93 |  | note | – – – – – – – – – – – – – – – –
label | 973d37ca-2095-5887-9ef5-67ef14bf2ed3 |  | note | (b) Slump: One per batch of concrete
button | f9f7e46c-cd14-5ce9-bae9-7e0a8af4866e |  | button | Acceptance | Yes,No,N/A
label | cceb2992-5576-5235-bcc1-03f9f903bc1a |  | note | Key - S
label | 78c9a28e-9975-548b-a28c-525b5cfc0022 |  | note | UGL Key - S
label | e8aefd4f-2b15-582a-bdde-00511421a5e1 |  | note | SHL Key - S
label | a8edbf9e-95bc-52b0-9291-698633c6768b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 834f1182-e975-5e9a-b66b-5971c9c845d6 |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 2.5 - Concrete testing
label | 428d0f33-aa8a-5907-b56c-79e0e04fd683 |  | note | Ref docs - Drawings
label | d1402de4-d388-5599-951c-7873d7992be3 |  | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
label | b850ce4b-9651-5978-8cab-23f51615a807 |  | note | Slump within tolerances specified in AS 1379
label | 3d940112-e77d-5dc0-a06a-b0c6c60fddde |  | note | – – – – – – – – – – – – – – – –
label | 4ff66f1c-2ed8-5051-a179-3053a58cb4f7 |  | note | Table 5.1 Permissible Tolerance on Slump
label | f863eea6-6d3b-59b3-b626-a3c5beb984ab |  | note | – – – – – – – – – – – – – – – –
label | c618414e-37d4-52f1-aa88-30676b33c984 |  | note | Specified slump, mm ¦¦ Tolerance, mm
label | 9eb0fc28-06a6-5504-8d15-d01775ad831b |  | note | – – – – – – – – – – – – – – – –
label | c7bec765-8f13-5b3f-a9a7-28c3a2b4c800 |  | note | <60 ¦¦ ±10
label | 28739fc6-3010-564b-88a0-f585e8fda8f1 |  | note | ≥60 ≤80 ¦¦ ±15
label | 34fea913-774b-5538-9f18-35b511af98cc |  | note | >80 ≤110 ¦¦ ±20
label | d41cf3ff-b8ed-52cc-b56b-adc1b30ee0ec |  | note | >110 ≤150 ¦¦ ±30
label | fbd562ee-e237-550c-b6a5-ae0417ab9f39 |  | note | >150 ¦¦ ±40
label | cf123a84-6859-5ddd-91e4-e0e9eafe6cf3 |  | note | – – – – – – – – – – – – – – – –
button | e702f67d-19a4-5923-9f4f-f4f145b1e0dd |  | button | Acceptance | Yes,No,N/A
label | b8e24fc4-fa96-559f-a38f-f9ebfa7da4bc |  | note | Key - S
label | 23125f5d-20b2-51a1-a638-04064a4d5ee6 |  | note | UGL Key - S
label | 09ee832b-4b01-59e4-8a6d-55bece884774 |  | note | SHL Key - S
label | 6ae1fe41-188a-52af-abe0-14c133f04590 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 60c7433d-ca22-5502-8b4b-f38df2e02df7 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.6 - Finish
label | 1a5490d7-2b7b-5385-a990-3eae7076d974 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 9d6a7ef6-e9a8-53c5-bbc8-d1fcd9594a0d |  | note | Acceptance Criteria - Finish true to line: The top and face of the finished kerb and channel.
label | 98a60b8d-4142-51e8-b7c2-65a2ae91751f |  | note | Top surface: Uniform width, free from humps, sags and other irregularities.
label | 2acf4b50-70aa-5e5b-b803-d070e8c3b8cc |  | note | Type: Steel float finish or as otherwise shown on drawings.
button | e80b9b2e-f2ee-5922-95bb-aec9497f0f64 |  | button | Acceptance | Yes,No,N/A
label | f6bfd661-ce00-5e7a-8ebd-1e40ef0db7ed |  | note | Key - S
label | ff3a4aae-8342-5efe-82f4-0d004e635c21 |  | note | UGL Key - S
label | 016019c4-e03a-5532-918a-b792782454c4 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.7 - Joints - Contraction
label | 42a7eb96-0708-5a6a-9a5c-e3cf5447fbb3 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | 11fc12f5-8533-5525-9431-33d4d7422409 |  | note | Acceptance Criteria - Contraction joints to conform to the following:
label | ab3d3907-a593-5d7b-adfe-68e768f75193 |  | note | – Width: 5mm min.
label | 715edca4-25f0-593f-9ca8-421eb49089d3 |  | note | – Depth: 20mm
label | 120ccc2c-145d-55f2-8e9c-a2430583acbb |  | note | – Intervals: every 3m for a min of 50% cross sectional area
label | 268bb8d4-26bc-51ab-a19c-a6b592156839 |  | note | – Tooling: 20mm depth / 5mm width
button | 873644a5-a92a-58b2-abb3-05dea1eadad6 |  | button | Acceptance | Yes,No,N/A
label | f1dca3d3-92fc-56e4-be6a-ea3326108d2c |  | note | Key - S
label | 94d86eef-9fdd-5c84-bd18-bc1074729ffd |  | note | UGL Key - S
label | c4fde604-3358-5359-97fb-d2c429a664f7 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.8 - Joints – Expansion
label | 0c3397c9-8d12-5753-9c18-e55a3fe26141 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.3]
label | f4ff86c5-9a5a-58d0-a6aa-9c899089f40e |  | note | Acceptance Criteria - Expansion joints to conform to the following:
label | 9932a94e-1dac-5a21-a84e-6e51b341d9dc |  | note | – Width: 15mm
label | c2f9b354-145e-5c04-97a1-07e306d5d330 |  | note | – Depth: Full depth of kerb/channel
label | c223ced1-75d5-5f32-a097-50f9090271a9 |  | note | – Intervals: Max interval 15m
label | f97a127d-fb17-5347-9704-cd5110dd9f5e |  | note | ○ To be provided where channel/gutter abuts against pits, retaining walls, overbridges and both sides of kerb laybacks unless otherwise shown on drawings.
button | 52bcbef1-51fc-51b1-a634-4a5eed97ade6 |  | button | Acceptance | Yes,No,N/A
label | cdc9e428-849a-5573-b646-7fc23e91929c |  | note | Key - S
label | 3ce33a93-4232-5811-9164-9bb2428d833a |  | note | UGL Key - S
label | d8f4eaf9-4bd4-5c67-99ab-dd684d9b8da7 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.9 - Backfill
label | 4b7ba6dd-4e1a-5507-9e83-098203af3eff |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
label | 1fd07d26-dfc0-5c9e-baf2-2a8c393e5290 |  | note | Acceptance Criteria - Timing: Backfill behind kerb no earlier than 3 days after concreting.
label | 3f1f73a1-2efc-52e0-876d-dbe5ba141443 |  | note | Material: Granular material, free of organic material, clay and rock in excess of 50mm or approval material
label | d2e72fb4-7004-5849-8815-0b87f9beca82 |  | note | Layers: Compact in layers not greater than150mm
label | ddc25e45-bd59-50f4-97c0-ccd4b3eedb74 |  | note | WITNESS POINT
label | ea8fe023-fe9b-5080-b8a6-c8c301503618 |  | note | ○ 1 Working days before backfilling behind kerb
label | 7ebb9358-7d59-59f2-947f-bc285dc89217 |  | note | ○ 3 Working days before to backfilling gutter pavement
button | 12b37733-ba2c-5e82-85e4-a590b0bd82a4 |  | button | Acceptance | Yes,No,N/A
label | c95924a7-c561-5766-8cb6-f610974f6857 |  | note | Key - W
label | 0f1a0b01-f7a0-5b27-b0f7-30b8e13b7832 |  | note | UGL Key - W
label | ad44044b-31ac-5fd6-9ea6-8874d9b436f2 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.10 - Backfill Compaction
label | 83ca36ff-91bc-5538-a776-cad6dd424233 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
label | 544b48e9-56de-51f7-9f79-25836937bc74 |  | note | Acceptance Criteria - Compaction: As per pavement design drawings or otherwise 95% relative compaction in conformance with AS 1289.5.4.1
button | 3e1d5c0f-099c-5484-b940-5b2cdbb99958 |  | button | Acceptance | Yes,No,N/A
label | 21e47768-75db-5dd5-bca1-b7985b78d7d4 |  | note | Key - S
label | e0319f1e-b7a3-525e-9fff-0a7e048d3bac |  | note | UGL Key - S
label | 5480c889-45e6-53cd-8607-4df0a1354fd6 |  | note | SHL Key - S
label | c8be9ec4-593b-5f9d-951c-c6b6e2aab6d1 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e26cf7c4-b0f4-5b1d-a8a1-14c324b510a7 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.11 - Gully Pit Tie Ins
label | 34d95e1c-73b3-5282-bec1-d03600cd298c |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.4]
label | 1a0c9023-6245-5810-a98b-d37c3627d426 |  | note | Acceptance Criteria - Adjust gully pits or precast units to suit the new kerb and gutter profile without reducing hydraulic capacity of the pit.
button | 3e09c2fa-858f-5336-8346-d7c6d623b99d |  | button | Acceptance | Yes,No,N/A
label | 17c6f77c-4254-5ed5-bae0-1ae7cc99b6d9 |  | note | Key - S
label | 69cc825d-b3b7-5487-95af-59df96935f84 |  | note | UGL Key - S
label | 10049363-7b77-50d5-82d5-a6d45129828c |  | note | SHL Key - S
label | b9db0955-8138-5b5e-a908-4c3d1311abc1 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 6ae6be90-fbe0-5310-8cd1-ec09d7ccb77a |  | tickbox | Test reports
checkpoint-group |  |  | section | 3.0 Conformance Check
checkpoint-status |  |  | checkpoint | 3.1 - Survey Report
label | 2c44dc5e-4c60-5e7d-906a-cd85c4197521 |  | note | Ref docs - Spec. 1121 Open drain including K&C [Cl 4.0]
label | e947a803-ddef-560e-9d8f-12b24c1d3847 |  | note | Acceptance Criteria - Survey report verifying kerb and gutter has been constructed within tolerance:
label | 039c677e-702e-592d-adc3-752b837a86fa |  | note | ○ Finish levels of channel/gutter surface: within ± 10mm of design level
label | f879bd76-5645-58dd-ac58-fb6d5579e7d8 |  | note | ○ Surface deviation of kerb face and channel surface: ±5 mm from edge of a 3m straight edge, except at laybacks, grade changes or curves, or at gully pits requiring channel/gutter depression.
button | 84b05d44-9cc4-5b55-a76b-b6148b1ce9a0 |  | button | Acceptance | Yes,No,N/A
label | ec81a7c3-3ba1-5972-b0a1-a61086d9b06c |  | note | Key - S
label | 5c0b86e3-6e80-5663-a5da-d90d5ddb717f |  | note | UGL Key - S
label | 4dabb84d-be00-51ef-bd18-9cc0f76fa965 |  | note | SHL Key - S
label | 905d8661-4faf-559b-8585-3110f3e8019d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e47a40db-8119-52cc-9fa6-a87b7729543e |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 3.2 - Acceptance and closure of non-conforming items
label | c22eca06-6982-55a5-97e6-9b384a1a062d |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 3a2a7c71-416a-5c7f-b493-d815302c9f58 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | ef584c52-1766-51c0-99a9-d72bebfa7bca |  | note | HOLD POINT
button | f79b3de3-7f39-59bf-bd4f-410617543579 |  | button | Acceptance | Yes,No,N/A
label | 0520858a-01cb-508c-a6e7-0eb5b7004b77 |  | note | Key - H
label | 182a516b-46d4-53e0-a3cc-b88e707ba279 |  | note | UGL Key - H
label | 3a0fb9b8-ca02-5e42-8704-96d5b6bc772a |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-008 Conduit and Pit Installation & Checklist - Rev.5 | 473bd0bf-a46e-4e88-bb8d-8d19f9a5445d
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 7d430a6f-2ca3-56de-b8fd-79cec8d4de87 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 059f6269-66e9-53f2-bc66-f362e7da08e8 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | ebc1b194-60e9-5b26-aca4-f2dec5a9ef86 |  | button | Acceptance | Yes,No,N/A
label | c0ee44d2-facc-5d38-b4a4-48c943157346 |  | note | Key - S
label | b3baaea6-0642-5888-a75a-9efbf1be5ea4 |  | note | UGL Key - S
label | a590d0d6-f468-51c3-9dd7-dbc88e2523bf |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 92feb3f5-a4c1-507a-8b1b-d9ad88352147 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | 4e28a19b-8d63-51cf-ac93-abb32269243d |  | button | Acceptance | Yes,No,N/A
label | 86ec8f9d-e1ce-5d7b-85e7-f2070a5bc1b2 |  | note | Key - S
label | 85a65a63-cd3c-5866-81cd-c3ca119daa32 |  | note | UGL Key - S
label | 70d09dc7-cba0-5204-b551-fa546710fa16 |  | note | SHL Key - S
label | fbbbd502-4279-512a-81cc-7d6c3bc94640 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 02d27176-fe56-5c83-94f5-fa4f750a0cf5 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Underlying Lot Conformance
label | 5a11f012-608e-58bf-9665-7a74364258a1 |  | note | Ref docs - Underlying Lot ITP
label | f4a5b1d4-559f-52b5-b1b4-74b0a052c1be |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | 96a6f65d-93c1-589b-8f08-16c1574b8e5d |  | note | ○ Refer underlying lot ITP(s)
button | f54821da-8ff8-5130-b42b-e0aa2886aef2 |  | button | Acceptance | Yes,No,N/A
label | ba6987d2-8994-5b88-8068-9dbad17723e5 |  | note | Key - S
label | 65be1dea-4cb9-5f56-a851-9a30671bc192 |  | note | UGL Key - S
label | e64a4717-a8fc-5dee-ad0a-d5a210845295 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Set Out
label | 1abc94a0-14a5-55c4-8768-46317993bbbe |  | note | Ref docs - Drawings
label | f0525d99-6a04-592f-9fd7-03589c11a104 |  | note | Acceptance Criteria - Peg location of proposed underground services with levels from pit to pit. Peg property boundaries
button | 43935b5b-ffb0-5be1-8308-ca317487c195 |  | button | Acceptance | Yes,No,N/A
label | 54bd7d20-a341-56c1-a18b-6a4ffe615be4 |  | note | Key - S
label | aa3bbcaa-f7b9-5277-9fc4-500b9f7c86f1 |  | note | UGL Key - S
label | 2f1ff0a4-d1c8-5cd7-9215-9f8ba90936a1 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Material Conformance
checkpoint-status |  |  | checkpoint | 2.1 - Conduit Supply
label | 16147b78-2330-525f-9c65-545f8ab36bcd |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
label | b2c556aa-71ae-5e10-b1bc-da0dabba971f |  | note | Acceptance Criteria - Conduit system shall be a Category A wiring enclosure for an underground wiring system to AS/NZS3000 and AS/NZS 3013.
label | b3fdfe6c-fb91-59c7-b924-676275e72563 |  | note | ○ No corrugated conduit or similar shall be used under any circumstances.
label | 62c9206d-dc6d-5400-b355-6322e2210e78 |  | note | ○ HV & LV Conduits: Shall be orange heavy-duty uPVC, sizes as per drawings otherwise min 150mm (HV) and 100mm (LV) to be used.
label | 786b8562-aa30-57ab-b348-5d78deb2c340 |  | note | ○ Comms Conduits: Shall be white heavy-duty uPVC, sizes as per drawings otherwise min 100mm to be used.
button | 34e9d706-1a20-55c5-8603-75f54fd13ae2 |  | button | Acceptance | Yes,No,N/A
label | 41d038b3-c53b-55ee-83d7-bb8bddbb68f9 |  | note | Key - S
label | bc9e6b36-f57b-5271-84e4-09f9f15848f0 |  | note | UGL Key - S
label | df982772-33df-5549-892f-8b7dd2f761a9 |  | note | SHL Key - S
label | 6b198f2f-5dff-5ed1-9d88-c841bbdce317 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7412b1cf-55f8-5992-8b49-a9805b48bd58 |  | tickbox | Material certification
checkpoint-status |  |  | checkpoint | 2.2 - Pit Supply
label | 1289a539-c38a-5d98-877e-edcdf3c2fc8b |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11]
label | 7e58a724-3b8d-5ade-bc7e-0666a6c66aa2 |  | note | Acceptance Criteria - All pits are to be reinforced concrete complete with concrete lids. All lids shall be gatic with min load classification of Class D in accordance with AS 3996.
label | 731a5e9f-4a9b-5b0f-b20b-5241cbc53006 |  | note | ○ Pits lids shall be fixed to prevent unauthorised access.
button | d539c4d7-f83d-52f9-9384-b52175a3dd3f |  | button | Acceptance | Yes,No,N/A
label | e914ea11-b83e-5499-b59f-54bc3e81f833 |  | note | Key - S
label | 49f0769c-34f3-5841-bc24-9c5d22e1b296 |  | note | UGL Key - S
label | 5ce04435-10b9-51ef-910d-3c628ab130bb |  | note | SHL Key - S
label | f51fa354-3672-5952-89f9-867716a5b685 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e23588e0-4039-56bb-917e-d5ef4fd88375 |  | tickbox | Material certification
checkpoint-status |  |  | checkpoint | 2.3 - Embedment material
label | cbae44da-45ab-518f-bca7-e2374dd7d3a5 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6, 6.11]
label | e1b14b72-098b-5496-abc3-0c5e47805b7d |  | note | Acceptance Criteria - All conduits shall be surrounded by a min of 100mm compacted sand unless shown otherwise on the drawings. For power conduits, this compacted sand must have a min thermal rating of 1.2°C.m/W.
button | 668a40c2-2fc7-58a6-9b7a-af1336ab4b0c |  | button | Acceptance | Yes,No,N/A
label | 37dab6f5-ece6-5908-8bd2-bb1c0444628e |  | note | Key - S
label | 1fe021c0-14ae-5ad4-9c30-05c8abfcfe64 |  | note | UGL Key - S
label | 70909ef9-f931-5d0f-a027-b2a35ea26ba1 |  | note | SHL Key - S
label | 459ec7eb-6050-58ec-8461-1ba61188a28d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 191aa402-7284-58cd-bd01-fde69a648477 |  | tickbox | Material certifications
checkpoint-group |  |  | section | 3.0 Excavation, Installation and Backfill - Conduits
checkpoint-status |  |  | checkpoint | 3.1 - Excavation
label | bed79d57-6067-5493-9412-4efa24a9b0ae |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | ce606fb7-b226-5f48-a2ee-4d75d1be7d93 |  | note | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
button | 66f76344-c1b2-5d60-9fca-8e545d82a56e |  | button | Acceptance | Yes,No,N/A
label | 43119d15-4a7c-5123-bec2-f0ad250a4453 |  | note | Key - S
label | e8692ce6-582f-568e-9f0a-51e51b5d6a0f |  | note | UGL Key - S
label | 92e5255a-9252-5a53-ac97-ee2764b6f5cc |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Place Bedding
label | 8bd52178-c5c7-560f-a79c-27ae647f01eb |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | e9648bfe-ebd0-5270-8382-79772878f540 |  | note | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
label | f8314024-4da0-59ce-b0a5-2307ace2ebdf |  | note | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
button | 821a90ed-8707-5d23-a4c3-09c36817c76c |  | button | Acceptance | Yes,No,N/A
label | a53b5118-cc90-589f-a719-c7715e0a7fe9 |  | note | Key - S
label | 75d18ce6-6f05-5c5f-8986-552d16a63d47 |  | note | UGL Key - S
label | 6432f6d0-a674-539e-b78d-d78d6ca25c12 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.3 - Conduit Installation
label | cd98c5a5-017e-5d83-b1ed-115c71e60489 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11, Cl.17.1], Drawings
label | 0aa726f4-4c4f-5be2-8e8d-928b344733a1 |  | note | Acceptance Criteria - Conduits to be installed as per the drawings in a straight line where possible and with no changes in diameter between pits. Joints to be sealed with a solvent cement or glue as per manufacturer recommendations.
label | c303aa32-6be4-582b-90a3-07beb8b3c8bd |  | note | Minimum separation to be 150mm for DN150 conduits and 100mm for all other sizes unless shown otherwise on the drawings
label | fcaac8d9-a4cb-5cb8-94e2-ba3b7b58fb0b |  | note | Minimum depth of cover to conduits to be:
label | 9928cb2f-eaf4-5b24-bcd7-bd8f9e6a5d48 |  | note | – 300mm for COMMS
label | c38a3967-76f6-50f8-92d5-6ddd886c3c79 |  | note | – 500mm for LV
label | 47688c84-8db3-50bf-bebb-92e3aa9d4414 |  | note | – 900mm for MV
label | e6ffa39a-8341-5a14-b0aa-0a23e0d2227c |  | note | WITNESS POINT – Prior to Backfilling
button | 0298276d-1f0b-550a-add7-7d6bafa22dc3 |  | button | Acceptance | Yes,No,N/A
label | fe0f87ab-6c3d-5c37-9d50-06275d6a58d9 |  | note | Key - H
label | fe174e6d-ee72-5a24-a3ff-2ef50f96f6d8 |  | note | UGL Key - W
label | ac25e264-d4a3-571d-a513-3eab21496f79 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 3.4 - Conduit bends
label | eb286f2c-aaf9-59da-93a1-2e60ef4bec51 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7]
label | 832ed589-f863-545c-8602-28b7bb8ba020 |  | note | Acceptance Criteria - All conduit bends shall be long sweep bends with a maximum 90-degree angle.
label | 90d95227-d893-54a8-b12f-a61e5a93682a |  | note | Min bend radius shall suit the min cable bending radius of the largest cable in the conduit and generally not be less than 1000mm.
button | 2e1cbf9e-dbf2-537a-b6b3-47784ded7453 |  | button | Acceptance | Yes,No,N/A
label | 439e708e-13b4-5b12-a2e9-2b398b9c8a5f |  | note | Key - S
label | 88d26208-5e03-5822-8574-332bb19be397 |  | note | UGL Key - S
label | 94f560f4-ade5-55b2-9ed6-2966fb7ea552 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.5 - Marker tape
label | 835b1b95-de99-5b7a-a011-41409f50d662 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.9]
label | c62a70cc-2447-5912-97ab-6790cdc19480 |  | note | Acceptance Criteria - Orange Polyethylene marker tapes, 150mm wide and 0.1mm deep, shall be laid in the trench directly over all underground conduits at approximately 50% of the depth of cover. The tape shall be marked with the warning:
label | e55aa324-2f54-59ee-81a2-78d86cb9e05d |  | note | “WARNING BURIED POWER CABLES”
label | d7fb8d2f-4b31-5db2-909f-eaad490547c6 |  | note | or similar in black letters that will not fade.
button | a709e204-90d6-5e81-8920-1d8a74d97e04 |  | button | Acceptance | Yes,No,N/A
label | cdb2f9cb-4ecb-55ae-b13d-e0d30234fc46 |  | note | Key - S
label | 473a51ed-3f9c-59d4-b311-a83b3d9fe3f4 |  | note | UGL Key - S
label | e6ae85b0-aedb-5ae1-85d1-5d653e8d83be |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.6 - Backfill - Conduits
label | 81278cda-0962-505d-80ed-3517d8f49588 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
label | 75a67e55-2db8-51f9-a03b-342430d7d62a |  | note | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
label | c405819e-9ce6-5900-88bf-0d0f4bba6a93 |  | note | ○ Layers not to exceed 150mm compacted thickness.
label | a6c82b98-b1c1-5ee7-903b-75e3ee462d2a |  | note | Key - S
label | 80f7812b-8a29-5cf5-8a9a-b969cefa28f5 |  | note | UGL Key - S
label | ce990f00-50ea-5b2d-afbe-9bc0fa408fad |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.7 - Compaction
label | c0bf998c-5026-5256-8c75-9ddf24d8e05f |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | 75057d40-e99e-5561-8f19-c7a996449f30 |  | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | 0f0cd3d7-38cc-5060-be9f-9fc5f21e8743 |  | note | – 95% for foundations
label | e1300c7b-d0ee-5db1-8a07-b2723c510033 |  | note | – 70% for conduit encasement
label | f2868c86-9443-5ec1-8746-dc47472782aa |  | note | – 97% for select fill areas
label | 71be7640-0baa-5bee-b77e-53b6cb6c3e95 |  | note | – 92% for general fill areas
button | c5b2d35e-22b5-5c3a-9f18-f8d9ef122dc6 |  | button | Acceptance | Yes,No,N/A
label | 89dd4925-520f-5af2-bd7d-48587975c7f3 |  | note | Key - S
label | ab0172e0-1f56-576d-9b0c-3455acb29ba7 |  | note | UGL Key - S
label | 43af223b-ba38-54c1-9421-5621f26e3355 |  | note | SHL Key - S
label | 2a3527a3-1990-5d4c-b05d-631d5ff6d780 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bed4de77-e7cd-5819-95e1-1a14248f88e3 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.8 - Cable Markers
label | f11380c1-0b15-52b5-94e5-81816ef230ab |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.10]
label | 9c6f56ad-e928-5df2-b3f5-b2a5337d0251 |  | note | Acceptance Criteria - Install Concrete Cable markers on the surface of all underground cable joints, at every change in direction, and on straight runs at least every 30m.
label | 9c9d63b0-a7ca-5b3e-a2fb-add0755d2b52 |  | note | ○ Markers to be a 400mm square and 100mm deep concrete block with a brass label attached. Label to identify conduit type and direction.
button | 24d0e565-7955-543b-afe5-69c4b32bc75e |  | button | Acceptance | Yes,No,N/A
label | 8f115051-aeb0-531c-b762-796695018241 |  | note | Key - S
label | 3df851a6-e636-5661-859a-a7c8421a3c18 |  | note | UGL Key - S
label | a0abeba3-c463-5578-b032-418744d25831 |  | note | SHL Key - S
checkpoint-group |  |  | section | 4.0 Excavation, Installation and Backfill - Pits
checkpoint-status |  |  | checkpoint | 4.1 - Excavation
label | 2de300ac-42b4-5d8a-a9c7-cab37ae38691 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | 2fdc59ef-440c-56cd-8d9a-cc9d68bcc2f0 |  | note | Acceptance Criteria - All trenches unless otherwise directed by Snowy Hydro shall be excavated as per Drawings.
button | 9b946bdf-4279-50fb-827d-ed2bc6ca2786 |  | button | Acceptance | Yes,No,N/A
label | 94db1377-1160-52ed-ba77-0982ab20af68 |  | note | Key - S
label | 018a0ecb-8aba-5713-aa16-b5f9b630e8c4 |  | note | UGL Key - S
label | 20259e89-42ba-53e1-b13c-fcbf03d9025b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.2 - Place Bedding
label | dbcf26d5-140c-59e2-8061-e214fc88e208 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Drawings
label | b75b1195-4f20-566a-9253-ee848935841b |  | note | Acceptance Criteria - Pits shall be installed on a compacted sand base of not less than 100mm.
label | cc3fc3f5-252c-5cbd-bfcc-126af905c18c |  | note | ○ Bedding layer to be compacted for the full width of the trench to a depth of 100mm for Comms & 150mm for Power Conduits.
button | 7218d8ca-fc1e-5fa2-9ede-e87a8509d0bc |  | button | Acceptance | Yes,No,N/A
label | e79a8dc7-cab7-5900-884f-224c0385752a |  | note | Key - S
label | 90242fb2-1616-5258-8544-d1945344e27a |  | note | UGL Key - S
label | 44c2b3d8-9270-5001-af5f-5cc00a1d40b8 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.3 - Pit Installation
label | ad2a4141-fd2d-50d8-9cbf-1d9e44700b5d |  | note | Ref docs - Drawings
label | eeee6359-8934-5c5d-9c26-a7eda004377e |  | note | Acceptance Criteria - Pits to be installed as per drawings and manufacturers specifications.
label | c3771c3e-a71a-5029-95a7-85c2262fa45c |  | note | ○ All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall.
label | 655222b2-dbfa-5576-be40-1f3236df6a7a |  | note | ○ All pit joints and bell-mouths are to be mastic sealed or glued as per manufacturer recommendations.
label | b18f2a3b-eee3-5fec-bc74-42b32bcd8579 |  | note | WITNESS POINT – Prior to Backfilling
button | 5393e6bb-5dee-5c5a-9f7a-9f4a63c7552b |  | button | Acceptance | Yes,No,N/A
label | b77782a1-c967-5ddc-8354-29dbc4ed5a45 |  | note | Key - H
label | 6c4e54e4-f35f-5a6b-b515-85e4c46247e2 |  | note | UGL Key - W
label | 935dd72f-959a-5146-a6a7-06ea4a42505f |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 4.4 - Pit Drainage
label | 1d832f44-769e-5196-af0b-f41fbae18216 |  | note | Ref docs - Drawings
label | c291b9d6-344e-546b-8dd7-4e63a0b1884b |  | note | Acceptance Criteria - Pits to be installed with a drainage system as per the drawings to prevent pooling of water
button | 3863c267-e66f-5fc5-a163-ebec5e7665f0 |  | button | Acceptance | Yes,No,N/A
label | 54fc5548-1e4c-52ea-894f-36247b533460 |  | note | Key - S
label | 0980740c-f1e3-5c13-98b2-d71a78da8d5f |  | note | UGL Key - S
label | 0d3aeee4-b766-53e1-a5c7-2b7d428b926a |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.5 - Step Irons
label | ea66fe06-2643-503c-969d-597fe4c7f0ee |  | note | Ref docs - Drawings
label | d0728c1d-bc98-5523-a7dc-45357b31e67e |  | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | 11427d63-49cf-52d6-9b66-fa814c4225bc |  | button | Acceptance | Yes,No,N/A
label | a7b987a0-410f-529b-a186-d07692bcc412 |  | note | Key - S
label | f5b768ac-11c8-515c-be77-c2ce9452baf0 |  | note | UGL Key - S
label | 27f98708-d0bd-5209-9ed2-989156743aa0 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.6 - Access Covers
label | cbefda3f-ba82-5d50-80c4-a09c8431e48e |  | note | Ref docs - Drawings
label | db688475-2924-5d7a-b615-a1fbaf41952b |  | note | Acceptance Criteria - Pits to be fitted with Class D Concrete Infill Gatic Lids to AS 3996.
button | ef21cea4-440c-5c93-9004-736f87268b10 |  | button | Acceptance | Yes,No,N/A
label | 21d76149-1da3-5779-9a44-8b11ea9ce3cf |  | note | Key - S
label | 87e66778-ec5f-5ab0-b3f7-a9e7409d6387 |  | note | UGL Key - S
label | 3c237bd9-1940-527d-9df9-85bdbcb2d5b9 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.7 - Brass Marker Plates
label | 0c088bb1-3009-55fe-bbeb-65398ca3b63c |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
label | da43766c-a59c-5bbf-8112-a9d19a48dd24 |  | note | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
button | a1d14a4c-c9a8-5a5f-86e1-ad4653ac5683 |  | button | Acceptance | Yes,No,N/A
label | b652b5c6-b62e-503e-bdb6-951ef6822506 |  | note | Key - S
label | d8293475-6968-56f0-8814-12650fcc3064 |  | note | UGL Key - S
label | 56a521c2-eeb3-5719-acae-6336f1089753 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.8 - Backfill - Pits
label | 84fd2348-ca56-5607-924e-e5b9804d7abb |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6]
label | 7737919a-8946-5729-9cb3-8259db9bc831 |  | note | Acceptance Criteria - Backfill the full width of trench with compacted sand to above the level specified for compacted sand, back to natural surface level.
label | d2eee582-9b80-5417-b831-0011c0744cce |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 6d69e21d-489e-5d27-a0cb-0dfbb1a6b575 |  | button | Acceptance | Yes,No,N/A
label | 07a7861e-58de-53a4-bfdc-e5aa04ffc8de |  | note | Key - S
label | 0d0ef195-98d1-58fb-9698-fccb77b67c63 |  | note | UGL Key - S
label | 149a03eb-0fcf-53e0-9c69-3cf0467bf042 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.9 - Compaction
label | 0be40808-bbe0-57d2-ad79-7414bc5e37cc |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | 04900907-d585-515b-a487-57165d16f9a4 |  | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | 893efe38-083a-5825-86c7-4a02170b5c25 |  | note | – 95% for pit and conduit bedding
label | e2f4f3fc-748f-5072-b836-6bd05ecaa286 |  | note | – 97% for select fill areas
label | bcda238a-f31c-5943-9443-5628d440958c |  | note | – 92% for general fill areas
button | 0e5cc0f6-951f-51cb-842c-17c94cdec072 |  | button | Acceptance | Yes,No,N/A
label | 048c5ecb-9eb0-56b3-a66a-f6e40bb3678a |  | note | Key - S
label | f0bdcfdc-f1d6-50fa-8602-489c2f5ea4ba |  | note | UGL Key - S
label | a35bb144-49b9-5194-b1f6-e553b36d8c18 |  | note | SHL Key - S
label | 0cffa7b6-d642-57c9-8e46-6bf400e2d41a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 90779270-c252-5be0-b862-60d875e92e53 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 4.10 - Rope and Mandrel
label | 4c8af62a-cada-5c4b-8bc4-62efef1849ab |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.7.5]
label | 774ff7ed-a9e4-593b-be24-1ce2654eee31 |  | note | Acceptance Criteria - Draw ropes or wires to be installed in all conduits that will require further cabling.
label | 7a2cb33b-6a9c-5c5c-a3b2-1dae4c2afe7c |  | note | ○ All conduits to be mandrel inspected prior to cabling to check for blockages.
label | 459a8f82-bacb-5162-a4ac-0239b64a5dc7 |  | note | WITNESS POINT – Prior to Cabling
button | dac4c2bb-5447-5acb-ab50-24cc2e6b747e |  | button | Acceptance | Yes,No,N/A
label | 6df40e9d-85a5-59a3-aaab-c5cce396839e |  | note | Key - H
label | f3e0e90c-d7fd-516d-abe0-d379d13a6df9 |  | note | UGL Key - W
label | 3877ced6-2f91-581c-8a25-9f72fc267b0a |  | note | SHL Key - W
checkpoint-group |  |  | section | 5.0 Conformance Check
checkpoint-status |  |  | checkpoint | 5.1 - Survey Report
label | 839c2651-c6c1-5444-ba1d-14796f923f25 |  | note | Acceptance Criteria - An as-built survey of the conduit and pit system has been completed to ensure all structures are within construction tolerances.
button | 6dfaa406-2121-50b8-bb0b-f5f87dbb6150 |  | button | Acceptance | Yes,No,N/A
label | cb9efa2d-24f6-5f64-a66d-4281c1977217 |  | note | Key - R
label | f36390bd-a6ba-535b-be62-891d747cf2a9 |  | note | UGL Key - R
label | 75754d84-52d5-54be-bda9-a55229b398c2 |  | note | SHL Key - R
label | eba7ff6e-f052-5ce7-b3e2-6aab3c3ef649 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d55a88d3-997f-5ddb-9c23-1f50bcf9c879 |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | 2e6c91e2-360a-5df7-995b-d9d0b19e19b6 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 8f57ed3a-204d-5d87-adca-3cb7e1774bff |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | d6a13e52-c085-5168-b333-83c5189b9b1e |  | note | HOLD POINT
button | 04fc6eb8-a3d3-5183-8276-1bc9f8ce5954 |  | button | Acceptance | Yes,No,N/A
label | 8ee7234b-63dc-5529-ae32-2f80fbc19f95 |  | note | Key - H
label | 988850ca-276b-5f1d-884b-caff378a6518 |  | note | UGL Key - H
label | 6a9302b3-3700-5f95-adad-6e0bfabfb773 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-004 Oily Water (Pipe Laying) & Checklist - Rev.6 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-004 Oily Water (Pipe Laying) & Checklist - Rev.6 | 481449af-ca36-4750-8c6d-0c8883bd46a2
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 08adb2bb-bd96-5772-8f0c-b610d85d9d07 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 8da6c70f-e6e6-5c26-a41a-0e5e1ae205fd |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 8229c34a-2772-56fd-9d18-0bdea1a92ed6 |  | button | Acceptance | Yes,No,N/A
label | 422c9e75-f3a9-5767-bcab-0c07bf85c600 |  | note | Key - S
label | 0ce6c43a-77ff-556d-a3a0-f52b8fcfd4c2 |  | note | UGL Key - S
label | d4dfc06b-a5f5-52fc-b78f-3c1e188f13a4 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 0209090a-73a8-51b2-93d0-28939fe49d8e |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | 608ea41e-3cc7-549b-8d73-adcb01876fe8 |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
button | 1b28a4ee-dae1-57af-8274-b8c745377788 |  | button | Acceptance | Yes,No,N/A
label | ca81eb9b-f676-5c47-a033-9652a6b1ab25 |  | note | Key - S
label | 722fd0b4-2f2c-51fd-9613-1a3937d4ade8 |  | note | UGL Key - S
label | cef15c17-0966-5e3b-a932-11c67a73f20a |  | note | SHL Key - S
label | b63a0c77-5c46-5979-a2c2-81dd3b143f8a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 70a9f32d-1b87-5807-b98f-ef3f1171ce9b |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Drainage Pipe Material
label | d22add74-1c33-55d1-be7e-be7379823ba7 |  | note | Ref docs - Drawings
label | e9cdd879-47f1-5820-bc9d-77a86242b089 |  | note | Acceptance Criteria - Has the correct class & type of drainage structure been supplied and free of defects?
button | 7b473a95-5ad4-5ca8-9a6e-b65e6e3c986e |  | button | Acceptance | Yes,No,N/A
label | 57bce863-f437-58a5-9777-7af208dc6c8f |  | note | Key - S
label | a040e73b-8084-5e01-af6b-feb75e2197ba |  | note | UGL Key - S
label | 5a2f54f7-889d-57d5-b509-73667f8b80a2 |  | note | SHL Key - S
label | e794aa3f-b88c-5988-a697-3c3f0a782cd5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1881211f-4b56-538f-930b-96c260698cf0 |  | tickbox | Material conformance certificate
checkpoint-status |  |  | checkpoint | 1.4 - Embedment material
label | 7b1c6d6d-c832-59e3-af50-7f986164c5e9 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | d67df3b6-f12a-5f6e-a0d4-e85e683dc3fb |  | note | Acceptance Criteria - Material has plasticity index less than 6.
label | b07e9a41-7b9d-5137-98d5-d939ab24da0e |  | note | – – – – – – – – – – – – – – – –
label | 124e5f64-47a5-5007-9858-4435a2331d59 |  | note | Table 5.1 Embedment material grading
label | a7cba0e6-b1b2-5ed8-ad57-06409ee00e50 |  | note | – – – – – – – – – – – – – – – –
label | bfbe11cc-ffdd-5d0d-ae99-5315aa6eb582 |  | note | Sieve size (mm) ¦¦ Weight passing (%)
label | 7bdb831e-cf7a-5da4-8ad0-93d0876021e7 |  | note | – – – – – – – – – – – – – – – –
label | 269b9187-b469-51dc-923a-d1748bef622e |  | note | 19.0 ¦¦ 100
label | 8b3086e4-6423-56dd-9d92-b6a6fd451bc4 |  | note | 2.36 ¦¦ 50-100
label | dfb8d022-b0a4-5f51-88ce-1eef83f2e701 |  | note | 0.6 ¦¦ 20-90
label | fb5db0e0-71b2-536d-a2af-e2f5c6d269f2 |  | note | 0.3 ¦¦ 10-60
label | 7b88f4a8-c5ad-5aa8-8a78-65c37ca25f51 |  | note | 0.15 ¦¦ 0-25
label | 6003c99a-6e07-546b-82ad-a823ae6a8517 |  | note | 0.075 ¦¦ 0-10
label | 6d9c18bd-3cc2-5433-b6cf-8ba1db29f1a1 |  | note | (Table taken from AS/NZS 2566.2, Table 5.5)
label | 9fc2738f-55f2-572b-8d85-92616db43052 |  | note | – – – – – – – – – – – – – – – –
button | 97356fd8-b2d8-5fcc-9255-088399bc3963 |  | button | Acceptance | Yes,No,N/A
label | eabb70cb-7961-5799-a443-b99da595e4ea |  | note | Key - S
label | 61f92623-a574-510d-b75e-95a73d6ba854 |  | note | UGL Key - S
label | 53fd27f4-09d1-51d7-b097-81ff6a069c5a |  | note | SHL Key - S
label | 359388ef-23fd-5739-9f68-80a256550c55 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f3072f19-56c7-5a96-bd3c-895887f50264 |  | tickbox | Delivery dockets
boolean | 8241ad2d-5feb-5543-8a70-005771f498a2 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | 49474a7c-7ee0-5a76-8d55-0a4545be2697 |  | note | Ref docs - Underlying Lot ITP
label | ee991f2b-b84a-51f9-9edc-b12674fc5a0e |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | 4194d93f-d98d-5814-9c51-de39a517671f |  | note | ○ Refer underlying lot ITP(s)
button | a02d96c9-3467-5933-88af-2edefbe32bb6 |  | button | Acceptance | Yes,No,N/A
label | fbde8ad3-3039-5d14-a8fb-5954241d285d |  | note | Key - S
label | ec03a385-567f-536a-968d-8ea627e6aabd |  | note | UGL Key - S
label | f01cf819-1686-5746-bbef-0dd50b0cc521 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Temp. drainage during construction
label | 9c788c72-1052-5ba7-92b1-c557e34ccba2 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
label | 4675008c-dbf6-5472-8ef8-bdf51040aca3 |  | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair.
button | 0eda91f9-0e68-57d1-92eb-cd8a3595dc16 |  | button | Acceptance | Yes,No,N/A
label | 468c3db3-e061-5028-940f-69bf6c425f81 |  | note | Key - S
label | 1b39ffeb-ffc6-5428-93f9-8b708e630068 |  | note | UGL Key - S
label | 49cf9a2b-c490-531c-84c3-aa5b282bec87 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.7 - Set out
label | d7e6767a-aaa7-5810-bf44-e0f82bb081fd |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2], Drawings
label | 8515ce22-fc7c-5908-ad94-4df2400c8409 |  | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | c3f732b6-2561-544b-a8e9-9d105b311af4 |  | button | Acceptance | Yes,No,N/A
label | 0312fcb2-8ea1-563e-b03c-15743e5c3732 |  | note | Key - S
label | 7bcfb41e-e8d6-5338-b9f1-d0197803795a |  | note | UGL Key - S
label | 0e23872a-4242-51e6-9c29-2a0a19ebb4e0 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and Pipe Laying
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | f2550fc4-6a5f-5912-80bf-dab454790cee |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
label | b50fe8ee-bfdb-5eb9-8f8e-db0aeb42a36f |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 5759149b-cf42-5dda-99c9-b4d08ff613b0 |  | note | – – – – – – – – – – – – – – – –
label | cbfb67bf-5476-5861-89fd-75e00893631e |  | note | Table 5.2 Trench and embedment dimensions
label | 71d6dd6b-8a57-57ff-beb5-9abc2b4fcf4c |  | note | – – – – – – – – – – – – – – – –
label | 36f70226-8b45-5752-9044-9d88e29157aa |  | note | Extreme external ¦¦ Minimum dimensions (mm)
label | b3436101-e3c2-5d61-9e58-b521f1b19bdb |  | note | Dia (De)mm ¦¦ x : s : o : y
label | ff08e84f-9e4c-52e7-98c8-b069fd446a4c |  | note | – – – – – – – – – – – – – – – –
label | 67b3601d-acef-504e-9fb2-364a9d590118 |  | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
label | 0c4c9f59-cfb5-537d-be97-1f2e984ffb16 |  | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 3706cb86-fc09-5f53-9ec3-15947121c07e |  | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
label | f278d67b-0b46-515d-8942-63d674421a89 |  | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
label | 9a2aa3e6-55e7-5788-adaf-c4ec30b27f47 |  | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
label | 75544a86-ec49-519d-9d49-45d177ec0457 |  | note | – – – – – – – – – – – – – – – –
button | 5742858f-1fcb-5d4b-b549-1649a22dfe33 |  | button | Acceptance | Yes,No,N/A
label | cc3712a3-6041-5c57-a847-59ea1cbefcfa |  | note | Key - S
label | 3e01d7a2-9724-56ff-874d-5e3669a3e094 |  | note | UGL Key - S
label | f7a692ec-d76f-50f9-9bba-d2127a2482a2 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable Material
label | e70855ab-10dc-512f-9d52-6c9201bf79af |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | cce4ce2f-5ad9-50a7-8205-30a20670b56a |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | cc30e38b-81d3-586f-a94c-37aedbc7f03e |  | note | Notice: Prior to Placing Bedding
label | cc4425f8-78bf-5cbb-8798-f32962fd1ffc |  | note | HOLD POINT
button | f5a188a8-9b11-5d5a-842c-4312de4a1751 |  | button | Acceptance | Yes,No,N/A
label | bb637bbd-ef7e-5619-b127-a70684dc101b |  | note | Key - H
label | 06b09e4a-efb0-5807-8dac-c0395ea7b43b |  | note | UGL Key - H
label | 89c2f39a-96db-5dbd-b701-4daeea8e7a02 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Compaction – Foundation
label | 2d8bc8ed-7e2b-5b0d-b8f8-4227ef4a9a4b |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | dc6196af-05f4-544b-9479-8f3f023a7578 |  | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
button | dfad7e5d-0260-575b-a120-415027517f6d |  | button | Acceptance | Yes,No,N/A
label | 097cd713-cfc5-534b-96f2-3a738bddb5ec |  | note | Key - S
label | 4ca9b456-1e8c-569c-8c3c-3949d5eff4e5 |  | note | UGL Key - S
label | dcddcac9-0677-5401-bdc8-8b7efa989849 |  | note | SHL Key - S
label | de5b14a4-5314-5dff-8fcc-932c397a1737 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ccd3df89-d283-50cc-93b8-e48dec9de0e0 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Compaction – Embedment material
label | 0ae1c6f8-8298-516b-aad3-192b0fd4c698 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | 27aee5eb-e0ad-5f89-9701-c07f9a95f3ad |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | d41f43d9-d0d2-5914-a1d9-ecd16a1ce8ee |  | note | Bedding:
label | ce3d0b62-9def-53da-9fd7-df3e80a484a0 |  | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
label | ec4871ad-f500-5ea0-bff3-b2a948d38e55 |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | ee256f17-0dcb-59cd-adfc-35be5e08831a |  | button | Acceptance | Yes,No,N/A
label | 5e22af0b-4ff9-5999-9278-db7cbb88fc8d |  | note | Key - S
label | afdb65be-ce8b-57fb-b72d-c316b74ea503 |  | note | UGL Key - S
label | ccbcb957-da00-5024-a849-36b8a1faa684 |  | note | SHL Key - S
label | 2f6672f1-705b-535b-be01-d46072e6ad21 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2238d18f-fe77-52ca-bba6-b874795f87b6 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Pipe Laying, Pipe Joints and Protective Coating
label | 9ffae909-fa2a-5b2e-aa3f-f650da0b7c33 |  | note | Ref docs - Drawings, Manufacturer Specifications
label | a9f4e913-9ff1-55dd-a735-5e428625c4cb |  | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
label | 65a5ea4f-da25-59d6-bac6-99b1b8964f93 |  | note | ○ Pipe joints installed and torqued as per drawings and manufacturers specifications.
label | 2f2bd4e2-ae26-561c-989e-a2b15ed18a7a |  | note | ○ Protective coating on pipes applied as per manufacturers specifications.
label | dab4cebe-d326-521e-b20c-e01750412116 |  | note | HOLD POINT
button | 265cec24-9489-540d-a1e5-11b1adb6e4e1 |  | button | Acceptance | Yes,No,N/A
label | 1870c7f8-f93f-5d51-8992-0ec486ea1ca9 |  | note | Key - H
label | 3b8ac0f1-5bb5-5960-8112-4923a8bc5560 |  | note | UGL Key - W
label | fcc6bff3-c35a-5f5a-b68e-be5c5fc8a729 |  | note | SHL Key - W
label | 35583ac5-cc4e-5bf9-870e-b41d295636a1 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 993ae244-b113-5169-bc56-beffc847921c |  | tickbox | Flange connection and protective coating check sheets
checkpoint-group |  |  | section | 3.0 Filling and Compaction
checkpoint-status |  |  | checkpoint | 3.1 - Compaction – Embedment material
label | 3713ec8b-8d9f-5885-89b6-4a2d131c4150 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | d6d15c49-65d4-533d-b222-952c3e6d51aa |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 2947a3c3-4c18-5aad-9cee-b8c1899c5137 |  | note | Side and Overlay:
label | 024f7a8c-d30e-58cd-8841-de3d73a86f85 |  | note | ○ Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
label | e383961f-bdd4-5914-83aa-c27678311e95 |  | note | – – – – – – – – – – – – – – – –
label | 1feda0ea-377a-5d74-921d-07c297275fed |  | note | Table 5.3 Minimum relative compaction
label | 90445425-b450-5283-beed-dbad9371e98a |  | note | – – – – – – – – – – – – – – – –
label | 2dad8a3c-5d4f-50ac-8f76-cd2324050dea |  | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
label | b5d51674-972f-5568-ba47-fd4a9afc2846 |  | note | – – – – – – – – – – – – – – – –
label | 7ade0b8f-1abe-5f11-a320-6f24c8d3a48e |  | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
label | 2e570b21-7bbc-5e5b-95bb-3c75c5fee453 |  | note | – – – – – – – – – – – – – – – –
label | 561cd108-d249-56fc-9588-5d05f2244a52 |  | note | Layers not to exceed 150mm compacted thickness.
button | 5f108bfe-c7bb-52e9-8831-0c581e31f978 |  | button | Acceptance | Yes,No,N/A
label | 89becd64-43f3-51a7-954c-f640ae452016 |  | note | Key - S
label | cd57602d-8c6c-57a4-b2da-844b05bf924d |  | note | UGL Key - S
label | 671cca38-2d89-55d3-9e09-93db1c51a6fb |  | note | SHL Key - S
label | 6a408a4d-a68f-590f-94b0-e767bcc8757f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e8163bcc-1ea3-5fdc-ab55-7517abc666dc |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.2 - Compaction – General Fill
label | 3641b63d-4a32-5cb8-90c4-35a3003a9a40 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | b387c5ff-0720-59e7-915e-cc38315c851a |  | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
label | d764eba3-9d02-5368-81db-a5ccbd2b009c |  | note | ○ Minimum relative compaction to be 92%
button | 58163e41-4322-56c9-9188-4bd29a2cd967 |  | button | Acceptance | Yes,No,N/A
label | e8d82ec0-45fd-535f-be59-6e857ccb3860 |  | note | Key - S
label | 538e6e1d-5b74-5221-aa28-db3d61aa3bc6 |  | note | UGL Key - S
label | 033039cc-659e-51b0-a24c-688ca447edf4 |  | note | SHL Key - S
label | 2b5f4592-c14e-5ed4-8bc1-07aaaad8cd74 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1a5a2f14-e4ea-5459-8df8-f50cb67d11da |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.3 - Compaction – Select Fill
label | c6bdbf5d-991a-557c-a093-489404aa3cc0 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | c1d156d2-8773-554d-929c-a40fc829ec53 |  | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
label | e8c8be93-956f-5232-b1c9-e9bba6331665 |  | note | ○ Minimum relative compaction to be 97%
label | e1db8c4e-e33c-592a-b88a-5f1c294c68f5 |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 81f4569c-e8f7-50eb-95e4-4fc7421d7a81 |  | button | Acceptance | Yes,No,N/A
label | d6fc8b17-e7ba-5bc9-8d61-40ad9e57fe6b |  | note | Key - S
label | 83a975ba-26dc-5772-b17e-cf511b70a698 |  | note | UGL Key - S
label | 2dc1df7e-41da-581e-8b3e-bbba2716dcfc |  | note | SHL Key - S
label | 69b0c61c-8722-5da7-9289-5c94a4981953 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7f913d44-9d56-520b-b5ce-59de25ec05ef |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.4 - Moisture Content
label | 446ca5e0-ba5f-5f46-a823-6cf6212aefcd |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 647f5f4a-1842-56dd-b401-2ef80b22ea8c |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | d31ecb59-1d95-55f7-8bbc-2ccc3f11a382 |  | button | Acceptance | Yes,No,N/A
label | a65a60f2-0ccc-598e-bf93-7699d5473681 |  | note | Key - S
label | 8fbbf796-3242-501b-a370-1ad0dd34fcd4 |  | note | UGL Key - S
label | 976e1f2d-122e-54ed-a5f0-ea4eabfb7328 |  | note | SHL Key - S
label | 0536ac45-32ae-5f5b-93be-9ae4969b6fd8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7f36196e-05c1-5d15-80dd-bb419eaa8a94 |  | tickbox | Test reports
checkpoint-group |  |  | section | 4.0 Conformance Check
checkpoint-status |  |  | checkpoint | 4.1 - Survey Report
label | 51d273bd-7b24-592b-bc30-f3590539523c |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
label | e0bd05ec-4bb2-5cda-81a4-9dab541af18a |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | a6835ab4-3abb-52ad-ab6c-640671bb2071 |  | note | Plan: +/- 200mm
label | cb43bf8b-71f5-500b-951e-6b7adff5d9a3 |  | note | Level: +/- 20mm
label | 6775ba81-e3a1-5794-ab44-636778e88499 |  | note | HOLD POINT
button | febdd185-15a9-5d95-ae6e-a3f1bf1ccdbf |  | button | Acceptance | Yes,No,N/A
label | 7606c9ec-adce-525d-9ed6-f277f1cbdd9b |  | note | Key - H
label | 6de49d22-786c-5bd1-b6a1-698b88cbbe86 |  | note | UGL Key - W
label | d30497b1-135c-56ee-aac5-65ea9aad9943 |  | note | SHL Key - W
label | 86e113b8-99cf-58d3-9f24-6e201ae0367d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2fb6d66c-e755-57ea-9993-58c0cac4c020 |  | tickbox | Survey Report
checkpoint-status |  |  | checkpoint | 4.2 - Acceptance and closure of non-conforming items
label | e4ce0638-d949-5ec1-8634-64c1e624738d |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 0fc03dc0-861d-599d-b104-451d09a833f4 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 3e7c628f-f6ba-5182-8847-580223bba8b7 |  | note | HOLD POINT
button | f4026d98-b4a6-5f1e-a1de-31e574b2d40a |  | button | Acceptance | Yes,No,N/A
label | c2cb9002-5524-599b-9513-65d5f629a9d3 |  | note | Key - H
label | fb446174-6f8b-5eb0-9f34-8b9ba4a3b6ea |  | note | UGL Key - H
label | b4770109-7f33-5506-b832-e07ecd4c6135 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-021 Screw Piling. REV 2 | 4fa6e1a6-3a25-45d3-9b9f-d8a7fc96d3eb
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | ad18b816-4ed8-5979-8bb9-24711442b6d6 |  | note | Ref docs - Issued drawings / Site copy drawings
label | d6bafaf7-b31b-5e72-a04b-a66a9cb55304 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
button | 9c420586-452b-5520-868d-ef34b217598b |  | button | Acceptance | Yes,No,N/A
label | a0694a4c-9271-53e5-bcf3-0538ef0a963b |  | note | Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | 6b233749-75ac-51cc-839d-ee418bf30fb3 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | 133e9b54-c6bc-5d32-8973-551e047d9417 |  | button | Acceptance | Yes,No,N/A
label | aab8e36f-a3dd-5f10-bbb0-7aad69cbedfb |  | note | Key - S
label | 5b1e8239-54df-5772-9409-6225241dfbe2 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 9038ae4f-be08-575b-88ca-b7855b419575 |  | tickbox | Lot map
boolean | 54df3821-85e3-5429-a407-e6487891fe3d |  | tickbox | Piling Schedule
checkpoint-status |  |  | checkpoint | 1.3 - Material Certification
label | 445f84c4-769c-5470-8f6c-a3319d8a2304 |  | note | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
button | a17fbd5e-c194-51e2-803b-dbc3e80e1e83 |  | button | Acceptance | Yes,No,N/A
label | 12e99b27-4f7d-5c76-a447-616f79328c52 |  | note | Key - S
label | ac2702ea-3e17-52f3-8e90-53493a3e2806 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | b0f28937-02dd-5cf5-bbbe-7ff8361aa7f9 |  | tickbox | Material Certification
checkpoint-status |  |  | checkpoint | 1.4 - Geotechnical Engineer
label | 0fb93aaa-ec61-5140-9aad-e2147918f63b |  | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
button | 2d80147e-8a06-5f31-adee-a3e136933c42 |  | button | Acceptance | Yes,No,N/A
label | a25d93aa-c5a3-51db-b843-6ba7bbe1dbd9 |  | note | Key - S
label | 5d5098f3-3d9a-5bbc-96f2-6b08420e2aa6 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | c867717e-4202-5c1d-a227-13c2686c251f |  | tickbox | Bore Hole Log
checkpoint-group |  |  | section | 2.0 Materials & Equipment
checkpoint-status |  |  | checkpoint | 2.1 - Screw Piles Shop Drawing
label | adec23e4-0d8f-5119-a54a-f8b11d85db7b |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | 72325818-6399-5d47-8962-b4f6b9eb632b |  | note | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
label | fc6ae8be-2068-5f38-b21f-8f3a4dc7f217 |  | note | Shop Drawings to include.
label | a38e1b46-2f95-5898-a632-437533b33484 |  | note | – Dimensional Requirement including tolerances if applicable.
label | b5f53bb7-48b0-5552-aca3-3b76b2e38144 |  | note | – Sections designation and material grade
label | ab21d4f9-81bc-557d-8f34-a484187db8ca |  | note | – All Welds and weld procedure
label | ccea1a5c-9e19-5dc0-8d64-744ef961c164 |  | note | – Corrosion protection requirements
button | 3518e232-58ee-5479-bd55-f41715f3a7c1 |  | button | Acceptance | Yes,No,N/A
label | 05dbef10-0922-528f-940a-b4538e723368 |  | note | Key - H
label | ebe2575f-a6e5-5cf3-978d-cf8b39a34b52 |  | note | UGL Key - H
label | c50be11e-146e-5719-a6fc-f635014901fe |  | note | SHL Key - H
label | 7eeac7e1-56fc-5a17-8e33-0b952c226da6 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 033d1ef7-aea5-5b16-b3fb-b67e71274ca7 |  | tickbox | Shop Drawings
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Manufacturing of Steel Screw.
label | 65bda2f6-ba83-506e-8413-e1aa43658871 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | 5e4e9c13-cace-50a1-8636-afdbd3278042 |  | note | Acceptance Criteria - Fabrications
label | b16fd25e-fd0b-5d0f-8523-960b7d8a7361 |  | note | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
label | e36b9b90-dbc5-5e09-9de3-89382581fe35 |  | note | Welding
label | 0c2d7994-33e7-5213-b92c-28723951fc76 |  | note | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
label | d220f89d-5841-5ffd-a3b1-95c65a4bc555 |  | note | Helices.
label | 5fb04e66-33a4-58bc-8ebf-abb0d84b651e |  | note | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
button | 7165bf54-0f3c-5c45-a272-ce86cb5c1acf |  | button | Acceptance | Yes,No,N/A
label | dfd05cce-0cad-5619-b9dc-f7f46e261d93 |  | note | Key - H
label | a455d09f-27ff-515a-b60d-d1377d122f9f |  | note | UGL Key - H
label | 15ad9620-939d-52db-9dd0-34b710353537 |  | note | SHL Key - H
label | d56dd816-fef6-5574-9d4a-c1899df8c254 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 69e46334-1c27-5945-88ee-ac11480320de |  | tickbox | Material Certification
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Piling Machine
label | 84ebdd4f-439a-5371-a9a7-104369f595ab |  | note | Ref docs - Drawings
label | 8ecb3f3c-a670-5810-a345-792459614b7d |  | note | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
label | 0819ee95-2b3e-5bac-ad57-5c0d356b8c21 |  | note | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
button | 1db5c4b1-1dd7-57c9-acbd-06dcb31a9e6c |  | button | Acceptance | Yes,No,N/A
label | f0674c92-2694-587d-b1ca-02614db5b94d |  | note | Key - R
label | 8cdd7263-bbdf-51d5-910d-549eda653bda |  | note | UGL Key - S
label | 369b7e8a-c56a-5bcf-b64b-6439fbbaa81a |  | note | SHL Key - W
label | bce8124a-f6b4-5572-99b5-f88f1a68d66a |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 324b72dd-7885-5de0-8c2b-0bc223a24ac5 |  | tickbox | Calibration records
checkpoint-group |  |  | section | 3.0 Piling
checkpoint-status |  |  | checkpoint | 3.1 - Survey Setout
label | 7eb6d4f0-2b35-5a96-af43-dd1a395de55a |  | note | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications
label | b665ea15-b6d1-5e59-bbd7-17becb634a75 |  | note | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
button | 3b6f3e53-5594-5ac6-b1b8-c2e2ffa595ba |  | button | Acceptance | Yes,No,N/A
label | 0b0d946c-4713-5b0e-9c40-a4338db4c1ec |  | note | Key - H
label | e7b50fc5-76e8-52d1-94ac-2d8545ed92a1 |  | note | UGL Key - H
label | ae185911-4d69-51bf-8087-091320a15d00 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | e5eaf2e1-8dcc-5d73-b142-d45b900a9ec4 |  | tickbox | Survey Report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Screw Pile Installation
label | d2794989-02d0-5c09-9bf7-28e303858b2a |  | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
label | af0ec9b2-280b-591a-a94f-d9a315090d83 |  | note | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
label | 0dc523f8-03e1-51b3-82b0-03d59ac5663d |  | note | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
label | 006593b3-9d87-58b1-bd9e-5fb52bc00e51 |  | note | ○ Screw piles installed as per design and required machine torque.
label | 074e4d47-642c-5d0e-8af1-f575788d6f3b |  | note | ○ Rate of penetration and torque vs depth to be recorded.
label | 230e35bd-2faa-5717-a793-25fa5395a5e8 |  | note | ○ Each piles finish height is to be checked.
label | ca7d3dd2-01b2-5c2f-9a72-8c65054c7420 |  | note | Notice: 3 working days prior to excavation of test pile
button | 7068b210-2450-57be-b41b-57ed5c8837b4 |  | button | Acceptance | Yes,No,N/A
label | b798d336-e5b5-5607-9377-e759aa8bcd50 |  | note | Key - H
label | f64ba602-30c5-5ce2-bf61-9fba424107a0 |  | note | UGL Key - H
label | 722f8f4e-9f81-5bef-bf16-f769ce7a62ca |  | note | SHL Key - H
label | 3d9ff63e-124e-5e30-9a16-3e94cb5cb30a |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | bdffd828-faff-5cba-b432-2cf981c9d7a4 |  | tickbox | Geotechnical Engineer Sign Off Sheet
boolean | 396a305e-c8f2-52e2-bbb4-32f1da643a1a |  | tickbox | Pile Log Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Concrete supply
label | 2b0e7585-7f66-51d8-a9f7-1f103a3b59f2 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | 197e49c0-792f-507c-aa73-bca08e0163d3 |  | note | Acceptance Criteria - Verify:
label | 921ba7c2-27d5-5656-b474-f668c768247d |  | note | – Concrete mix
label | f5e68cb8-cd24-5568-b97c-316e3d5a84a7 |  | note | ○ A concrete delivery docket to be supplied with each batch delivered.
label | 5db562e5-6365-504a-af69-1bb6cc0e5e4a |  | note | ○ Concrete work shall be in accordance with the technical specification for concrete supply, construction and grouting and any other notes on drawings.
button | c519f2a3-7b20-5d55-99b1-25d0add7fc0a |  | button | Acceptance | Yes,No,N/A
label | 95210026-8586-5115-81ce-3bb3571dbf2f |  | note | Key - S
label | 50d0d9e4-43ab-5261-a760-eca74aefe467 |  | note | UGL Key - W
label | 137b186a-418a-5808-afd0-098cf1881407 |  | note | SHL Key -
label | b95115dd-0f84-5969-8dee-16636b2cad7d |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | d881d1e1-5040-5171-828b-6ac5095ef505 |  | tickbox | Material dockets
boolean | 4d23a1b6-574f-5eb5-bc35-c77997bb0fb8 |  | tickbox | Concrete Pour Record
boolean | 9f089f5c-458c-53c6-b21c-64a2a89079bf |  | tickbox | Pile Log Sheet
checkpoint-status |  |  | checkpoint | 3.4 - Concrete Placement
label | 8233d1f6-03df-5ec2-9de4-d888ea44c8eb |  | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | 82d3ba68-d203-51ec-bcf9-0d62255d105f |  | note | Acceptance Criteria - Concrete to be placed as per the construction drawings in accordance with AS3600.
label | 182ee511-9c65-59ed-9a1b-00ed09c22022 |  | note | ○ Prior to the pour ensure there is no water or debris at the base of the pile shaft.
label | fe08bf6f-a23c-5ae1-afdc-4aa52d48d145 |  | note | Notice: 1 working day prior to placing concrete for test pile
button | 6f9c75eb-8b60-5bf3-9f4e-605f8e092d21 |  | button | Acceptance | Yes,No,N/A
label | 15e9be40-6e3b-55a1-bea1-0f1599bbf3ed |  | note | Key - S
label | b11c6700-df90-5b5a-966b-0bd0e06ed7be |  | note | UGL Key - W
checkpoint-status |  |  | checkpoint | 3.5 - Pile Cap Installation.
label | dba40be3-900d-5c4e-9a31-ef9234646436 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.9]
label | f124edf3-e756-5dc9-a561-76d977d56130 |  | note | Acceptance Criteria - Reinforcement for pile cap to conform with drawings and specification. Reinforcement grade to be either 250N or 500N.
label | a6e48486-728e-58d2-bdbc-d5dc70be0753 |  | note | ○ Formwork to conform with drawings and specification.
label | 0fc57c87-a6ac-54ef-a13c-0875478b6cdb |  | note | ○ Concrete to be vibrated adequately during placement to ensure there are no voids or segregation.
label | f20ff353-8f2f-5e0e-9608-e40d23a2b946 |  | note | Notice: 1 working day prior to placing concrete for test pile
button | a10e1135-f247-5e5f-a302-d27b59538000 |  | button | Acceptance | Yes,No,N/A
label | 9ba8e4b0-cf1f-5ee5-a35a-ebe451c14544 |  | note | Key - S
label | b8b90135-6b37-56b7-8f4a-745efca166f4 |  | note | UGL Key - W
label | ff1eeebb-c050-52fd-82c8-fbcd918f25f7 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | f01e2917-c486-5c02-bc15-a9b9022e9c92 |  | tickbox | Concrete Pour Record & Pile Log Sheet
checkpoint-status |  |  | checkpoint | 3.6 - Concrete sampling
label | 096b6fae-cbb4-5e33-a515-35d29288340f |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
label | 3d163fbe-7fed-53d5-9230-f1dfb82e7946 |  | note | (a) Compressive strength: One set per pour or as otherwise directed by Superintendent;
label | 0a1b04df-3b16-598c-9bce-25620f84e67f |  | note | (b) Slump: One per batch of concrete (xxx mm)
label | cf421fdc-50df-5c9d-b568-17212bcdbd57 |  | note | Acceptance Testing shall be done at a NATA registered laboratory
button | 2a26c838-0f9a-5aba-aff7-c837685f5df2 |  | button | Acceptance | Yes,No,N/A
label | 64681501-0e55-50fb-a0ae-b8df81dcf376 |  | note | Key - S
label | 579ac796-bad9-5ef3-b3b9-305d0288928e |  | note | UGL Key - W
label | 7a396fef-ae75-5c83-ad1d-7b2dd0f9c5a8 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 581021bb-a734-579f-9dd6-788756ee7a4b |  | tickbox | Test report
checkpoint-status |  |  | checkpoint | 3.7 - Concrete RL and depth
label | d8e5e81b-415b-5477-879d-3f4977074cf2 |  | note | Ref docs - Drawings
label | 5f48697a-82bf-568a-b3e1-06ee7677ce2d |  | note | Acceptance Criteria - Screw Piles depth, size, position, and concrete RL as per the Piling Pile Log Sheet and Drawings.
button | 44c72ca7-eca8-52fc-88e5-cf9e9ff4465c |  | button | Acceptance | Yes,No,N/A
label | ba98f98e-05d5-5fce-9c3e-d6827d558ccc |  | note | Key - S
label | 40ba2de4-71bf-5974-938c-c0a9481a4c16 |  | note | UGL Key - S
label | 605d6737-7026-5fcf-a065-98bd591306f4 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | f0648d8f-ea74-51e2-b241-abe72102a174 |  | tickbox | Pile Log Sheet
checkpoint-group |  |  | section | 4.0 Conformance
checkpoint-status |  |  | checkpoint | 4.1 - Survey
label | d6421578-4688-5bed-844e-9e3ca2e0ceab |  | note | Ref docs - Spec. 0003 Piling [Cl 3.10]
label | 5b82d3be-b8db-522e-9453-ecebb53ca3cd |  | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
label | 25ad7c1d-dbe2-531d-a07f-83cd8f074498 |  | note | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
label | f3089c20-003e-5653-8b43-e6f6bf3c97ce |  | note | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
label | ab48c377-924d-5e88-ab72-fa66364f3d2e |  | note | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
button | 44f1fc08-50a4-5142-be4f-0c608234925b |  | button | Acceptance | Yes,No,N/A
label | 914955db-8d04-5561-8725-be2fd2ca98f4 |  | note | Key - H
label | c9219129-f29c-5105-a896-761a670c7d7b |  | note | UGL Key - H
label | 7c261ade-d19d-5763-9600-4a51497ad7cb |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 33cef580-b118-5b3c-9f4f-345889cb59c4 |  | tickbox | As-Built Survey Conformance
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-002 Drainage (Pipe Laying) & Checklist - Rev.6 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-002 Drainage (Pipe Laying) & Checklist - Rev.6 | 5e2e0e6e-b5b5-4814-aea7-79d0188b0453
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | c0b03e59-3ade-572f-b4ac-40efecd556fa |  | note | Ref docs - Issued drawings / Site copy drawings
label | 795cc7f9-f2dc-5a76-982b-2ce6c1884756 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 66464ad7-2abf-535d-b933-bc40ee9c5418 |  | button | Acceptance | Yes,No,N/A
label | 3dba44fd-eba0-5979-83ae-c66f1b2bc207 |  | note | Key - S
label | 9ad1c210-04a2-59ef-9fca-c471d6848b04 |  | note | UGL Key - S
label | 69b9d476-6ac6-57f9-8a71-d0cf72fd57cc |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 32d9968c-e8e3-5274-8bce-e6f698354ac8 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | a95913d7-e725-5f72-93c2-96c466fb7552 |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | 9466f2c9-978f-59fb-9cb4-728858ec1071 |  | button | Acceptance | Yes,No,N/A
label | 6ae598eb-5c88-5a21-b52b-65b2a14d501f |  | note | Key - S
label | 25a00ce7-de14-5e68-a348-bb35a508eb7a |  | note | UGL Key - S
label | 2d1c0898-806b-5015-83c8-27364b4e167b |  | note | SHL Key - S
label | 2655338b-fb95-57e4-bad9-0bbeee35ffe3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 143842ce-cd4f-5943-b23f-529fc75ff432 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Drainage Pipe Material
label | 1ad3d5cb-3de2-5fb2-b056-2142e42e45db |  | note | Ref docs - Drawings
label | 10ab4a3e-4cfd-54a4-8981-eebc7ff1b270 |  | note | Acceptance Criteria - Has the correct class & type of drainage pipe been supplied and free of defects?
button | f5844f64-3780-569f-8da8-97dadda2a931 |  | button | Acceptance | Yes,No,N/A
label | 0f849e77-ada7-55ef-9703-a8cdab50c030 |  | note | Key - S
label | 3cfd7d22-98ee-5d11-a1f3-b85f03f77eef |  | note | UGL Key - S
label | cdf3f0cb-cfa7-5e35-af20-95417e709b25 |  | note | SHL Key - S
label | 138cb1db-5cf6-5794-b597-76aa9c96f35d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 3037230e-11a0-5c91-bcc9-6eb318cd5489 |  | tickbox | Material conformance certificate
checkpoint-status |  |  | checkpoint | 1.4 - Embedment material
label | 4939f515-60a9-54f3-83c5-13717ed7c65b |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | eff0a2ae-2390-5b57-ad44-1ea574a660b7 |  | note | Acceptance Criteria - Material has plasticity index less than 6.
label | 62923b07-04b0-5186-92a4-e6da1d09f8c9 |  | note | – – – – – – – – – – – – – – – –
label | ecb2f58f-5835-596e-906a-20bb16a3a588 |  | note | Table 5.1 Embedment material grading
label | 08408dde-93e1-57cf-a9e8-8fe68f2e906a |  | note | – – – – – – – – – – – – – – – –
label | 4a393e40-fb1e-5692-8f56-91c625c71371 |  | note | Sieve size (mm) ¦¦ Weight passing (%)
label | c1c29013-0e6d-5d20-a6db-e621baaa6828 |  | note | – – – – – – – – – – – – – – – –
label | 7ded47f0-3fda-55b3-bb95-964cb936e78b |  | note | 19.0 ¦¦ 100
label | 3d00cf67-8fcb-5f6e-8f6e-fa1aaf574e23 |  | note | 2.36 ¦¦ 50-100
label | 6140fc8a-8969-5c09-b290-0faa2c23d173 |  | note | 0.6 ¦¦ 20-90
label | 2105ebe5-1a51-5e16-9151-4b0c7e75f2a4 |  | note | 0.3 ¦¦ 10-60
label | d7919e1e-d249-5c43-afb6-f5dcc893087b |  | note | 0.15 ¦¦ 0-25
label | ff20db25-28f0-5bb4-bd9f-a747d21a909a |  | note | 0.075 ¦¦ 0-10
label | b203d5a8-f832-50ad-8e5e-f766d81e7fde |  | note | (Table taken from AS/NZS 2566.2, Table 5.5)
label | 23851731-9cac-5b44-b077-d069409993d0 |  | note | – – – – – – – – – – – – – – – –
button | 165acb89-2669-5330-8ca0-af6964e2ae57 |  | button | Acceptance | Yes,No,N/A
label | fc7562d5-4d9a-5f62-8e62-b6bc99644392 |  | note | Key - S
label | 6f0571ac-0dd9-50da-81e6-77b7205be27b |  | note | UGL Key - S
label | ec996d9e-7e78-588b-ab3b-9ef525aa266f |  | note | SHL Key - S
label | 6b15abfe-a6ab-5e66-8404-7ee9e7cb7fc5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | fd939fea-b01b-5dc9-b214-6d8a62a25593 |  | tickbox | Delivery dockets
boolean | 0ac25300-f833-5173-b31e-7537095fefac |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | 5f0642d1-a205-56bd-94f4-0c081649a51f |  | note | Ref docs - Underlying Lot ITP
label | 7e4f3173-3e55-553d-b01a-664db5039a61 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | 43105d82-1668-5bf8-80f0-abf2f3cf2c31 |  | note | ○ Refer underlying lot ITP(s)
button | 436be88a-d038-51e1-898d-633adfa9ede9 |  | button | Acceptance | Yes,No,N/A
label | 90259a46-8bd2-5da7-8e21-b3282b33965f |  | note | Key - S
label | d7cda47c-68ad-522a-974d-4d90d1b72200 |  | note | UGL Key - S
label | 6bc4c028-63df-5628-99ba-7ec2666539a1 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Temp. drainage during construction
label | a164fdb5-820b-5593-86c0-4357dfc8ef2f |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
label | 91673264-b644-5ec8-b427-92817dfb0167 |  | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair
button | f75f2c25-2e72-58a2-b8a9-c63351a5ea18 |  | button | Acceptance | Yes,No,N/A
label | ec0ce591-a193-549a-9a4d-5e33ff4819b4 |  | note | Key - S
label | 0d081c0f-844a-5d73-8c9a-c36822eac5d3 |  | note | UGL Key - S
label | 5a6c995a-66c8-5e79-b7a4-a49f86c5206a |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.7 - Set out
label | 7c185ffe-c14a-54e2-be09-75e6a80cccdc |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2] Drawings
label | 7ac8f825-7419-5f69-9b6d-3a2d2fb83d6f |  | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | 9700f6b3-774d-5af3-9ff2-b01969fe37f1 |  | button | Acceptance | Yes,No,N/A
label | 81a90d5e-1506-5170-a054-5c1fe830c0bd |  | note | Key - S
label | 08c8aadc-e89b-59dd-9b64-545f59ce3614 |  | note | UGL Key - S
label | 84c5cd8d-283d-534e-8cb5-415462f7bfaf |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and Pipe Laying
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | d82095df-0f73-5737-8ba2-dd1cb1321ced |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
label | 0e23f42a-4535-5200-aabb-e64a5e1ff2b4 |  | note | Acceptance Criteria - DICL & Flexible Pipes:
label | c3858a5f-5a97-56d0-bc5f-b1082e2c27f0 |  | note | – – – – – – – – – – – – – – – –
label | 7b8339f9-79a7-5bbc-b0f2-851151bfeae9 |  | note | Table 5.2 Trench and embedment dimensions
label | 216fb083-5320-5f6a-bc05-0ddda4fa4d9b |  | note | – – – – – – – – – – – – – – – –
label | adf2002e-8aee-5ff9-9df1-f3bf1dac4d38 |  | note | Extreme external ¦¦ Minimum dimensions (mm)
label | 57028ebe-01e9-53ce-9198-446161bb975e |  | note | Dia (De)mm ¦¦ x : s : o : y
label | d0952fed-a6ba-5662-a02e-07fd5d7e7575 |  | note | – – – – – – – – – – – – – – – –
label | da3677dd-89ad-5469-a9c0-a4631d502c0b |  | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
label | 1956efa6-a89a-598e-99bb-18dc49c61695 |  | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 8cab0ff9-8638-5fea-8fa8-5ea528e453f3 |  | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 57a501a9-9593-5956-b1be-01062a14c4dc |  | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
label | 04b752b6-f811-5f93-aec8-4bb065a72f06 |  | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
label | 08c9b9ae-d0c0-57ea-86b2-297e27a76e2c |  | note | – – – – – – – – – – – – – – – –
button | f2788d90-98a1-5197-b101-5a1d990cef58 |  | button | Acceptance | Yes,No,N/A
label | 1b4f5e96-9f5b-5869-9c78-953e817c56a7 |  | note | Key - S
label | f1c55896-b7c6-5ebe-839b-6ec2076f3ae9 |  | note | UGL Key - S
label | 32366fcf-e84e-5ca1-817b-373ab4979420 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable Material
label | 3a0d0be3-5b66-58b3-a142-f15ade574468 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | 92d969f2-de12-56c5-89c0-e69fa6b3909a |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | 5f772ed4-e1e7-563c-a2ad-3b9074d9a46e |  | note | Notice: Prior to Placing Bedding
label | c75c4a4b-075f-599f-bce0-e3bd93b23fa7 |  | note | HOLD POINT
button | c5c276f3-f56f-55b3-9907-7dfa47f047b0 |  | button | Acceptance | Yes,No,N/A
label | 771cd60f-b89c-5707-a3a1-f262a4eaef47 |  | note | Key - H
label | 0cf1c771-3575-5a11-ac02-d3f797970361 |  | note | UGL Key - H
label | f77068ea-71d9-5677-9139-ebd076fea80d |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Compaction – Foundation
label | e0665098-64a9-5c97-9f8a-683ad85544a6 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | ce70c461-1ed1-5be6-a34c-3ab1ce58db65 |  | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
button | d49a5b63-84a2-5bb2-a535-5cb49aa5ef68 |  | button | Acceptance | Yes,No,N/A
label | 76ef7931-c865-53ff-a5ba-249d6d313556 |  | note | Key - S
label | 01c8a8e8-ed9f-59f8-af8c-ab3fb1a19832 |  | note | UGL Key - S
label | 05ed141a-701d-5ffa-a931-1dfd18341747 |  | note | SHL Key - S
label | 64c9e87b-9901-585d-afe3-dfbb972e62a3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 611d9d96-afc3-52ce-8673-cfe7865e740b |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Compaction – Embedment material
label | c1bf9871-f12d-5d43-9c37-623887ea8000 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | 46bc4fbb-a440-5064-b8bd-f93bdf3ec582 |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | ce9c7172-709a-5a8c-ae33-74cd654b9d98 |  | note | Bedding:
label | 83e9f72f-49b1-5a31-b516-6f2bc1de6446 |  | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
button | 927e7f7f-9b9f-5466-9fe8-055933633bff |  | button | Acceptance | Yes,No,N/A
label | d8546833-6430-55c0-9621-d5133f2967d7 |  | note | Key - S
label | 5f2f26ef-32a4-56f6-ae66-f3f9e8976df1 |  | note | UGL Key - S
label | 20116a2c-ab80-5e06-96a2-9138532da621 |  | note | SHL Key - S
label | eded2e61-628a-5c4f-84f0-32f8d44ec404 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 377cdbd3-e1fc-51b4-af8b-76a613cbd3d9 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Pipe Laying
label | fdee4d95-7cdd-5993-b5c4-a7cbb6abfaed |  | note | Ref docs - Drawings, Manufacturer Specifications
label | 6e62ad88-dce1-57a2-a28c-1e6846c17520 |  | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
boolean | 122fb2bb-d650-587d-a2ef-d82b33de74b0 |  | tickbox | Stormpro
boolean | dac8923d-d7d9-5161-a853-438a700a139d |  | tickbox | GRP
boolean | 6bb43f92-9a7d-5eb7-88bf-b2f3330bae7c |  | tickbox | PVC
label | 363ca5cc-8e45-5a3c-adc9-9dc854ba903b |  | note | HOLD POINT
button | 4f4e8670-537d-5f0a-bcde-b7397dd1bde9 |  | button | Acceptance | Yes,No,N/A
label | a065e0d6-e8ad-5145-9d73-cbb9fec24c2e |  | note | Key - H
label | cb29232c-d917-58d5-965e-dca76086a3c3 |  | note | UGL Key - W
label | 369d36f2-cce4-5725-ba59-7e71bd36e3ff |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.6 - Steel reinforcement
label | b11ad209-f01c-5a3b-90df-27fec2c034f0 |  | note | Ref docs - Drawings
label | 6db5a4af-b1aa-5c9b-b268-4603d9dbbe82 |  | note | Acceptance Criteria - Reinforcement installed as per drawings.
label | da12caef-b5e3-5566-bcc7-4014aae463ae |  | note | ○ Concrete pre-pour inspection complete.
label | 563ff45f-3397-57a3-8858-d2f29bce485a |  | note | HOLD POINT
button | 9a33fdbf-14db-5985-9135-cea1bf23e9dc |  | button | Acceptance | Yes,No,N/A
label | 524e01c0-bb4e-58f8-8150-63a68e2ca42f |  | note | Key - H
label | 7b05f702-c6b8-57e3-9c90-3fe2e77c6ee5 |  | note | UGL Key - H
label | 1d936174-ac4d-5a0a-aa77-3a60953cbabd |  | note | SHL Key - H
label | c751101d-e711-5412-a650-55d3ca11dcaf |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 64d54f43-89e4-5e75-a1d5-e3efbc8eeaac |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.7 - Concrete supply and placement
label | 2944bf2c-a7dc-5a07-841c-c3cc5ba6cb70 |  | note | Ref docs - Drawings
label | 9cef04ca-c3e5-5872-ac98-464bcd0ba8f4 |  | note | Acceptance Criteria - Check concrete docket to ensure strength is as specified on the drawings.
label | 4c78f463-78aa-55d7-82a9-6e2139f4efa4 |  | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated
label | 75f029b0-e6fa-5c17-a427-65129454569a |  | note | ○ Ensure pipe is adequately supported to prevent sinking or flotation. A minimum of 300mm encasement is achieved around all sides.
button | 9012d024-fe6e-5662-a839-f2203ffeae4a |  | button | Acceptance | Yes,No,N/A
label | ed8c6df6-761d-54af-8138-7017f9ef2beb |  | note | Key - S
label | 63ec70f9-5318-56c1-914a-1fda2b9c92b3 |  | note | UGL Key - S
label | ea9cd216-fe79-5fb3-a1bb-ce25178479fd |  | note | SHL Key - S
label | 59959fee-249c-5956-acc1-820b1cf3cf09 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c09035d5-fa41-5a90-bff0-bedd579ea0b0 |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 2.8 - Compressive strength
label | f3b7c4ba-7710-5b08-ac17-5888181f13e6 |  | note | Ref docs - Drawings
label | 2ba20c5e-427e-539d-bff6-b138ec60e9dc |  | note | Acceptance Criteria - Average compressive strength at 28 days meets the minimum requirement specified on the drawings.
button | e6c093ef-b636-5e77-92dc-f2992207fef9 |  | button | Acceptance | Yes,No,N/A
label | 987c48d9-0008-57ad-8652-edd926a893ee |  | note | Key - S
label | c3dc39cc-8a69-5f99-a222-327347f973fc |  | note | UGL Key - S
label | 43f5cf5c-3433-520b-a5fe-76c696013fdf |  | note | SHL Key - S
label | ecf770e4-b53a-5b87-a886-7802e550e768 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c539b126-9d4f-5409-a0e4-df0ddc4eea1c |  | tickbox | Test reports
checkpoint-group |  |  | section | 3.0 Filling and Compaction
checkpoint-status |  |  | checkpoint | 3.1 - Compaction – Embedment material
label | ebf90d80-6903-5695-a2c3-8a30dd9fa6cf |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | 9bbdf193-8cde-5291-b4da-99956af7c94a |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 91ed0797-01f0-5909-bc9b-e34db24f331a |  | note | Side and Overlay:
label | e7aeeb2b-d055-51e0-80aa-884c620e01c7 |  | note | ○ Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
label | 17b0995b-0ee6-5676-b9c0-fcdcf6057a39 |  | note | – – – – – – – – – – – – – – – –
label | 2b257259-e1d5-5691-8c10-e708fb1e7e5a |  | note | Table 5.3 Minimum relative compaction
label | 79397e50-2f64-5a91-b0a2-3813397cc084 |  | note | – – – – – – – – – – – – – – – –
label | 5f147c21-4df0-5f27-b27a-e99c00dff167 |  | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
label | 33bc1fc3-2258-5d36-9631-bf32aa2b4fd6 |  | note | – – – – – – – – – – – – – – – –
label | 541d52f1-330f-518e-b253-4bbccddb304a |  | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
label | 66a52626-edf3-524f-8126-74a81516b0e3 |  | note | – – – – – – – – – – – – – – – –
label | d009c06d-0371-5860-b569-644ae2694342 |  | note | Layers not to exceed 150mm compacted thickness.
button | 1decd1dd-390f-597c-962c-c72a548fa306 |  | button | Acceptance | Yes,No,N/A
label | 8be99407-8a18-5136-b8d9-c90de11821f0 |  | note | Key - S
label | 1f2b0f13-75ef-5e0f-bf0d-e546a39e2bd7 |  | note | UGL Key - S
label | 5ebe63db-31e9-5176-ab30-c582dcda7289 |  | note | SHL Key - S
label | 74c88909-41b4-550e-bff1-0d8ab4afc536 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 60db9358-c8db-5aa3-b6e3-0887d3db9793 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.2 - Compaction – General Fill
label | a2233e6d-16ad-5760-a197-b62ef4622020 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | b8394a5e-d778-558d-96c4-307996ba3c1e |  | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
label | acfad297-d893-581c-ab23-1917126ccb37 |  | note | ○ Minimum relative compaction to be 92%
button | 3ad4eb05-d210-57f5-bae5-1491a9eda897 |  | button | Acceptance | Yes,No,N/A
label | 3e4b0238-dcdb-5faf-b2be-0d8b428db2f1 |  | note | Key - S
label | 76d69608-f443-5766-b129-2973970c47e0 |  | note | UGL Key - S
label | 2816ce6e-e71a-5af0-827d-833042096627 |  | note | SHL Key - S
label | 87cbb96f-a388-5bac-ad91-53db8e77f445 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 82c47731-23e5-53c2-9cc3-8762934a54eb |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.3 - Compaction – Select Fill
label | 75cbc901-74ba-5953-8095-5dce76b15123 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 3b839a17-e66c-59cd-9400-c29d6daf3e97 |  | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
label | 102549d3-4e40-56fa-a4fe-85f509e08d7d |  | note | ○ Minimum relative compaction to be 97%
label | 3bb2c9fc-9026-5458-9b11-3f47f6a8f7ae |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | cab7c735-738e-546f-abbd-c1aa2e21d6f1 |  | button | Acceptance | Yes,No,N/A
label | a453d585-01b5-54ba-b133-0c42b54ff0b1 |  | note | Key - S
label | dbb646f1-9bb8-5dcc-b88c-6e12c8063e4f |  | note | UGL Key - S
label | e5633a44-e8e8-5a41-847e-ee887dbbad25 |  | note | SHL Key - S
label | 6661ddd1-2feb-5df2-8b80-449028b222da |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 70cee02c-2549-5bee-8fe9-2c4392310356 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.4 - Moisture Content
label | c3064a2f-924f-557c-ba5c-5c31352b7c64 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 7e4b2a87-51a7-5acf-ad09-685695117853 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | 27659e2b-28c4-5cf3-963e-783e990a4b2b |  | button | Acceptance | Yes,No,N/A
label | ab7ddd76-6ace-5a13-932d-66ce5d15b70a |  | note | Key - S
label | fc2b5e11-40db-5992-956f-e56de5d19909 |  | note | UGL Key - S
label | 98457612-9b9e-5157-8a1c-9bc0af3f91cb |  | note | SHL Key - S
label | 81646af7-0d3c-5143-8d7e-470cf9653c21 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 75acbd05-b79a-5b71-ab98-8bbd5f28b2c6 |  | tickbox | Test reports
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Survey Report
label | 1fb1c047-a355-5afa-8103-3d64d8dd29db |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
label | be8d28a1-ba43-5074-a0ca-edd25b5e34f2 |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all pipes are within construction tolerances.
label | 9d42a401-3fd0-590e-a8c3-00e82c3425e0 |  | note | Plan: +/- 200mm
label | f7934e9d-f72f-5ad5-95ce-b974fe729c14 |  | note | Level: +/- 20mm
label | 32498b40-928e-5dac-9f6b-7237ec562fe3 |  | note | HOLD POINT
button | 96292278-3c61-5d65-80c4-e26987ae07f9 |  | button | Acceptance | Yes,No,N/A
label | a8b64548-e1d7-5cab-b9b5-54f095ab8863 |  | note | Key - H
label | 3cdc08db-5ab9-5233-9ad8-bfe22c06e1ea |  | note | UGL Key - H
label | 089ba4df-c3f9-573d-b134-5533b3d94c03 |  | note | SHL Key - H
label | 95a6f357-d86c-5c9c-9d80-d9748cb51622 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 21221b8a-db7d-5f10-bbc6-023067e3b560 |  | tickbox | Survey report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Acceptance and closure of non-conforming items
label | 8bf5e939-d36e-5af8-996a-3cec789129c2 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 6e8347ee-1342-5191-be20-5339b7e0bf0a |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 0722076d-cbe4-5909-b62d-c1a7010ed834 |  | note | HOLD POINT
button | 78c117eb-7d33-552c-aea2-60106fe48ab5 |  | button | Acceptance | Yes,No,N/A
label | eb9a2844-2c0e-58c1-bc48-c3b5e9d7c13b |  | note | Key - H
label | 3817d5f4-b816-575a-ba4d-7396476c92bb |  | note | UGL Key - H
label | f6220109-82c9-5d47-8b28-79a439492982 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-003 Drainage (Pre-cast Structures) & Checklist - Rev.7 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-003 Drainage (Pre-cast Structures) & Checklist - Rev.7 | 6b5caf84-daab-4d89-86de-0f928db5685b
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 09b8a9c7-bd5e-5a97-bfd6-c2f3ebc6f163 |  | note | Ref docs - Issued drawings / Site copy drawings
label | e095affc-9552-5418-9199-87ec6a996f48 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 037aa174-7300-5b22-801b-55e5895c9cc3 |  | button | Acceptance | Yes,No,N/A
label | e299607e-8bd8-5273-896a-dec71c5c91c3 |  | note | Key - S
label | d5b70182-3cb3-540e-8555-aa2f6bf6359e |  | note | UGL Key - S
label | 1850ecf0-66eb-56b5-8b7f-3b7bc2203e26 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | a285d34c-134b-5ccd-8970-8b2770602d38 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | e069c0f6-6173-5a19-bb7c-38367103b5ba |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | b6039fce-c00f-59ad-b922-2545d53cdc3c |  | button | Acceptance | Yes,No,N/A
label | c0505d40-bb65-5234-b2af-1d70e7b8d78a |  | note | Key - S
label | 269ad51f-4500-5636-aa41-fc143c84f4be |  | note | UGL Key - S
label | 4c5e2cb2-4e4f-547b-8ac8-2ba6ef319df0 |  | note | SHL Key - S
label | f860cc80-46d4-5520-8da2-d71e82eacf80 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7b142569-fe03-5b59-b6a1-c4ab1820e0d2 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Precast Pit Approval
label | c9791dbe-e21a-5eb2-848b-57396446a61a |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 2.2]
label | 89b05457-47b4-5fe1-a772-b61e6430ab9e |  | note | Acceptance Criteria - Submit Drawings and Installation Procedures for Precast Pits to the Superintendent for Review prior to delivery of the first pit to site
label | ac3a94d8-9551-5e6d-9018-db446bc993fc |  | note | HOLD POINT
button | a3cf02e3-ac64-5ff4-a351-0eb49a1a0ed6 |  | button | Acceptance | Yes,No,N/A
label | c4455a31-4d34-5893-8ce4-46eb6a65b701 |  | note | Key - H
label | 363ce85b-2a18-5bf2-8db8-25e3bc7a2baa |  | note | UGL Key - H
label | 96589c07-c7c4-5d7e-a79a-eff2f9bad370 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.4 - Precast Supply
label | 1671607d-7acc-5c4f-959c-1fe25c8ef6dd |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 2.2]
label | 6732c613-9ff2-59a4-a894-9aef40f49308 |  | note | Acceptance Criteria - Does the supplied pit, slab, culvert or headwall meet all requirements of the specification and the drawings
button | ef24aecc-7b79-55f8-84d2-e861f238b388 |  | button | Acceptance | Yes,No,N/A
label | 1275aa33-f83e-54e6-b473-f7fdc8325d3d |  | note | Key - S
label | 7073a6aa-b420-5c1e-9f07-2ace8de23f72 |  | note | UGL Key - S
label | 1a75c5af-8257-5ec4-ae2e-5fec7c9775f1 |  | note | SHL Key - S
label | ee923638-01af-571d-8e77-9279665d9b5e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e7be3b7d-27b6-5be4-a756-e3455818aa0c |  | tickbox | Material conformance certificates
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | 58fa1030-3ad2-53f0-b29f-78e5807a412f |  | note | Ref docs - Underlying Lot ITP
label | 00459470-c080-5a22-be9e-7b0fb43b0070 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | e42760e3-4b21-525f-8dc7-81d786bd5ab5 |  | note | ○ Refer underlying lot ITP(s)
button | daaed654-31dd-5d13-89a1-6b4119afb8a3 |  | button | Acceptance | Yes,No,N/A
label | 7c5c4720-e88a-5885-ab54-cbb0f673023e |  | note | Key - S
label | fe8a4177-e5c5-5603-bc4f-f820a05ee797 |  | note | UGL Key - S
label | ede3dfbf-7a8b-5fa0-a343-dbdd8a678702 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Set out
label | d969608d-ab56-5034-b7ee-01712f96d405 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2]
label | 6ccb9e00-e6df-5aa4-b759-6df6df22c399 |  | note | Acceptance Criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | 04487a72-976d-5230-a869-307f6007d8b0 |  | button | Acceptance | Yes,No,N/A
label | 68fbfb69-1a88-58f5-b137-9a14021a5f65 |  | note | Key - S
label | 3e6ea099-8048-51de-be2b-0ec55c94db35 |  | note | UGL Key - S
label | f3d93ab3-3ff9-5e56-9852-14062ea64e28 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Construction
checkpoint-status |  |  | checkpoint | 2.1 - Unsuitable Material
label | 783021d4-fb7a-57de-bbe5-98dbb998835d |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | cb4ecffa-57bb-50ae-b2f5-cd99315a1a5d |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | 57dccf4c-ca4a-5d29-8150-0d47d35a357c |  | note | Notice: Prior to Placing Bedding
label | dcab14e6-3e6a-5a8c-ab4e-97558018df20 |  | note | HOLD POINT
button | 89236ff0-e6c3-5df9-9c02-b56a5aee3f36 |  | button | Acceptance | Yes,No,N/A
label | 0fca9dfc-8873-5a5f-9913-b23d33ee86af |  | note | Key - H
label | 7277d5ac-ddb5-5da3-a0a3-885b5751c0da |  | note | UGL Key - H
label | 686d5a43-213b-5887-979b-151973877923 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Compaction - Foundation
label | 001b4bdc-72d3-5121-b4cf-11eb07bc1f03 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | 14bb71e1-d171-5955-a941-b4cbee565c4c |  | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
button | eda071c6-a128-5065-abad-f35ef27f933a |  | button | Acceptance | Yes,No,N/A
label | 18fc7d56-4e28-5fd0-843e-8495ca2e4213 |  | note | Key - S
label | 813c429f-ce54-576e-abd8-67ab9e905764 |  | note | UGL Key - S
label | a0880baf-f8ba-5cee-bdff-c0cb526ab5b1 |  | note | SHL Key - S
label | ac40d5c2-0512-5381-9f0f-9730b03e2e14 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 31b07e80-ace1-5ba8-8855-dc3515202dca |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.3 - Compaction - Bedding
label | 32810833-5c09-5400-9677-f2b9e2c25fa1 |  | note | Ref docs - Spec. 1353 Stormwater Box Culverts [Cl 3.4], Spec. 1351 Stormwater Drainage [Cl 2.5]
label | 5443e9bd-7cff-5489-b303-5549cc9de6f8 |  | note | Acceptance Criteria - Precast Structures to be installed on bed of Select Fill with a minimum thickness of 150mm
label | beb2b625-2aaa-5865-8295-1ad776ef51b6 |  | note | ○ Bedding layer to be compacted to a relative compaction of 95%
button | 01546156-b39b-5345-bfac-ea904146ae97 |  | button | Acceptance | Yes,No,N/A
label | e095e192-3bff-5a62-a051-ef8e91c32074 |  | note | Key - S
label | 8d5f77a4-a3d9-5896-b9d0-f4c993f0855a |  | note | UGL Key - S
label | 58a36643-dbf0-5193-9393-e28b7ddd6705 |  | note | SHL Key - S
label | 433d818f-7016-54a1-96d7-1ab5c934480d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bd8bc4ca-eaf6-5617-a809-0b6ae4efd08c |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Pit Buoyancy Slabs
label | 2af57b9b-e29d-5a79-8ad6-42eba3a0a7ba |  | note | Ref docs - Design Drawings
label | 7576850d-1b4c-5eef-8b64-a59795b0b1bc |  | note | Acceptance Criteria - Pit Buoyancy Slabs to be installed and bolted to precast pits as per the design drawings.
button | 5157bbf6-317d-5e25-95c1-bebb50a45806 |  | button | Acceptance | Yes,No,N/A
label | 5b817281-db46-5290-b3b4-c54ae23a09e8 |  | note | Key - S
label | bab89831-d80c-577b-a4b8-a73008c05e3a |  | note | UGL Key - S
label | 3a1241bb-e14e-5e2f-a805-e83b2f2e0795 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.5 - Pit Installation
label | cc3eba54-c5a7-57d2-81a1-e29ce8f66f3a |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.1, 3.3]
label | a723a0ef-6f25-502f-9e00-83f7fe5f041c |  | note | Acceptance Criteria - Pits to be installed as per drawings and manufacturers specifications utilising certified lifting points.
button | a0cda77d-6e1a-5845-8fed-2d0fd498fc7c |  | button | Acceptance | Yes,No,N/A
label | fcfb0229-b37f-56c7-9420-d8184b6deab0 |  | note | Key - S
label | a9fd114d-f031-5edd-b93f-0dcb6b0e5c42 |  | note | UGL Key - S
label | b9c6b0b3-0f08-5fa2-ac2b-a8c0f235bde2 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.6 - Access Covers & Grates
label | 5634f71e-c163-58d3-b724-2922e6b31f71 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 51fcbc42-c5d0-50eb-bb42-035be3cdb41a |  | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
button | 031c3b6c-16e3-5f3a-9c19-d10b9d6346a4 |  | button | Acceptance | Yes,No,N/A
label | 8f8bc47a-2fc3-56f2-9962-658e4b3109b6 |  | note | Key - S
label | 3f2c275b-2ee7-578f-8d55-7c9d01653443 |  | note | UGL Key - S
label | 1d7f1829-fefc-505a-a48d-f35aefe8aa80 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.7 - Step Irons
label | 780205a8-3917-5c1d-9861-33f876b4c4d4 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 6708a13d-98a6-58e1-8fea-de8e95e8d35b |  | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | cf459b44-ad59-5d5f-bc39-7e4f932e4cce |  | button | Acceptance | Yes,No,N/A
label | bc4f1b74-a8ba-5121-b3a7-a0135b374d83 |  | note | Key - S
label | 6c99a675-9dfe-50be-8cfd-6c19bc429f36 |  | note | UGL Key - S
label | 24b294d3-9575-54c4-8fcf-1a1018a8beac |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.8 - Pit & Pipe Connections
label | 0065ceec-f66a-5376-8ea5-31b972f9032f |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | b4351cd8-e1ed-57e9-bafd-d98d4c65ce2f |  | note | Acceptance Criteria - Inlet and outlet pipes to be connected into precast pit walls as per design drawings & manufacturer specifications
button | 41003606-9b7f-55bf-9495-0b40a328e367 |  | button | Acceptance | Yes,No,N/A
label | 5bce9afd-c6b5-563d-b372-bec10b50d241 |  | note | Key - S
label | 055ac5be-3ff0-51fc-aafe-08d948447bbd |  | note | UGL Key - S
label | e7672e2f-fc78-5a41-8c23-6aef47b44c1e |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.9 - Pit Jointing
label | 9f0e2c5e-5557-586a-979a-440cbfdd9f62 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
label | 42fa34db-c0e5-5b49-bf88-ca3922bf34fd |  | note | Acceptance Criteria - Internal joints between precast pits and riser units to be waterproofed as per Symal RFI-037 & manufacturer recommendations.
label | 1cf53b10-7fbb-54d1-b5b9-7947a714bd8f |  | note | ○ External Joints between pits and abutting concrete pavement, kerb or structures to be a 10mm isolation joint.
button | 85ba263e-48c3-5496-b31f-3c772501c4d4 |  | button | Acceptance | Yes,No,N/A
label | 6a950e9f-fa3d-5bff-860f-698859afd216 |  | note | Key - S
label | beefe677-b113-5737-80fd-68ab68a04c01 |  | note | UGL Key - S
label | b03e38a4-80a4-54af-a9b5-096f332fd20f |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.10 - Backfill
label | 145218d1-774f-5bd6-9a9f-d4eac6780867 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.7], Spec. 1112 Earthworks [Cl 4.10]
label | 5507f336-b1b6-5acc-b633-dc671531d8e4 |  | note | Acceptance Criteria - Precast Structures to be backfilled & compacted in 150mm thick layers.
label | aa0283a6-79d5-5d46-a649-46768f4e89fe |  | note | ○ Backfill to be Select fill for material within 1.5m of pavement surface and General Fill below 1.5m deep.
label | 9a7b5597-8af8-5cc1-8b21-71276db59c9d |  | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
label | f590f1a5-9aae-5559-8d01-52f8a1834087 |  | note | HOLD POINT Prior to Backfill
button | cf59e2f3-bbeb-5d13-8b6e-87eb001b760f |  | button | Acceptance | Yes,No,N/A
label | add46eb2-ddcf-5893-84bb-6f008774802a |  | note | Key - H
label | 716c6a36-488f-553b-ab3a-1b23fd03442b |  | note | UGL Key - W
label | 1fae0abf-5357-5b43-b0f0-ec368b95cbd1 |  | note | SHL Key - S
label | 9745a92b-448e-5844-962a-7e4be953dc72 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 8ee2e93d-f704-50af-91b0-72a26612b1d9 |  | tickbox | Material Test Report
checkpoint-status |  |  | checkpoint | 2.11 - Compaction - Backfill
label | 864cdf3d-fb9b-551b-b80b-a8bf0695fc0f |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13
label | 13dabe6e-2a02-56af-8946-d3875c3311ca |  | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against pits to be:
label | 952aad7e-6def-5a26-b65f-9753d0fdaf8c |  | note | – 92% for general fill
label | 2ae4234b-a16b-57e6-89c4-5d09b286695c |  | note | – 97% for select fill
button | 3d8f2ddb-c18a-5531-987f-2ea68dc99f5f |  | button | Acceptance | Yes,No,N/A
label | 750a5747-01b5-5e59-bac5-a3986c92624f |  | note | Key - S
label | 8d4ec2a9-07d1-5c76-b62e-f65d4e538f5e |  | note | UGL Key - S
label | 188a774f-dfa9-5a82-9246-4262f8868a89 |  | note | SHL Key - S
label | 869c41c6-19c1-5afa-a07e-46089b735e45 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bfceecf9-17f3-5ab4-a5a1-d89a9265e705 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.12 - Moisture Content
label | 6913c316-9a96-5078-8a62-609e895a070b |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | dbd3197c-30fa-52b6-a14a-40630ae9aeb2 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | fcad517f-7306-5768-a7f7-757913a3d3b6 |  | button | Acceptance | Yes,No,N/A
label | 31870570-6bfb-5a29-9193-dbf009a7f200 |  | note | Key - S
label | f7e6395c-cb5a-53cd-b76a-f9815bff85fb |  | note | UGL Key - S
label | bee9959a-3f82-5afd-b9bd-d3a524257ba2 |  | note | SHL Key - S
label | 6489ad58-de2f-59df-bffb-48bbac32d4ea |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d8cee89b-9bfc-529b-97e1-e16437060afb |  | tickbox | Test reports
checkpoint-group |  |  | section | 3.0 Conformance Check
checkpoint-status |  |  | checkpoint | 3.1 - Survey Report
label | 1fcea21b-5be9-5952-ad02-7403e5c1b57f |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
label | d9e24de4-46d6-5ecd-b5ea-cc3312b132c4 |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | 53a98e96-7a25-5770-a0c4-eaa5640ee586 |  | note | Plan: +/- 200mm
label | db7ae03a-431c-58ce-ab91-f8794dd9425e |  | note | Level: +/- 20mm
label | 548b2d94-2bad-5b69-b0de-f5249586322c |  | note | HOLD POINT
button | 1a278e96-8bb1-5b32-ac5a-7b874767b24c |  | button | Acceptance | Yes,No,N/A
label | f04dc712-22b5-5aea-b957-2b59f13477df |  | note | Key - H
label | d70dae81-5293-5bab-adb4-eaad3d60c215 |  | note | UGL Key - W
label | f0ba6bcc-ea80-575e-8d53-065358d2b98a |  | note | SHL Key - S
label | e4616bd3-0aae-5a34-83ea-1dcdc5538593 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2736db49-398e-593a-a1ce-dae7eeab9abc |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 3.2 - Acceptance and closure of non-conforming items
label | fc7be392-28ec-5057-89a0-a89570c70192 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 094b92ea-21bd-5d2d-8c27-9cd1b700ab0e |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 27a3f015-27a2-57e3-812c-46d88185c42e |  | note | HOLD POINT
button | 3b87b8af-f3f2-5be5-8162-fa4f245ff443 |  | button | Acceptance | Yes,No,N/A
label | c0184e28-07e6-540b-9afc-034d6a3ffd88 |  | note | Key - H
label | 5c53803e-e059-51bf-b9cc-14336b4661d8 |  | note | UGL Key - H
label | 93db51dc-7be1-55cf-87a8-4336e217b1db |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-009 Unbound Flexible Pavement & Checklist- Rev.5 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-009 Unbound Flexible Pavement & Checklist- Rev.5 | 6ccde3b1-383b-4d54-87c8-72ede1e37663
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 8a057f01-850b-5c26-8fc4-63d79c5d41fd |  | note | Ref docs - Drawings
label | bb28ac68-4d40-50fd-9c36-6db19c321a4c |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | c97c5970-47bb-54cd-af9e-b4a1d5094617 |  | button | Acceptance | Yes,No,N/A
label | da47f3cb-7da6-5f7b-925a-4a96e38e7cc2 |  | note | Key - S
label | 29be0142-ac5f-5b74-94af-09d53084e164 |  | note | UGL Key - S
label | e9640473-d615-5edb-b85d-996491db979b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | aefd6173-5b7c-547e-8d42-e33b60a826df |  | note | Ref docs - Spec. 0161 Quality (Construction) [Cl 7.6]
label | 50c0de5c-a050-5cb2-88af-bec3ee915e6b |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | 4c0381e9-e98d-5048-9d5d-2689ed964302 |  | button | Acceptance | Yes,No,N/A
label | c93ab9ca-d662-5193-9c91-78109cedd892 |  | note | Key - S
label | f007ec21-2358-5968-a076-95c240829e2f |  | note | UGL Key - S
label | 140e5389-5975-5304-a868-d8d98a733dd1 |  | note | SHL Key - S
label | 1c36246c-f577-575c-a769-bd1517a3b341 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 5cf598fa-9b05-5bf8-90d9-ae8248d6ad17 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Material Classification and Source
label | 72e6d435-1907-5b11-81e3-d42641cf6bec |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 2.3, 3.0]
label | 26a81325-134e-59ad-912e-b7c77a51dbfc |  | note | Acceptance Criteria - Is the correct material being used?
label | 51a2cf90-2949-5c23-bedb-dc9d5a934c5e |  | note | ○ Has the material to be used been approved by UGL (Material certificates to be provided)?
label | 2ea5b7c6-3888-54e0-a2e1-bf18d347d309 |  | note | HOLD POINT
label | 3a564a03-8083-513b-92e2-228e3e9ad5c6 |  | note | Notice: 14 days before commencing
button | 5ae90004-2432-5be8-beb7-1668dcaac2e1 |  | button | Acceptance | Yes,No,N/A
label | 80960097-4a10-57f9-bc19-eddeffdfb5f8 |  | note | Please tick the appropriate box:
boolean | 81348a95-56ec-5eca-90e5-846283d3e0e2 |  | tickbox | DGB20
boolean | f358d177-2ae3-5035-a801-39d4b8fabb12 |  | tickbox | DGS20
boolean | 30b93fae-b3d9-5a1c-a251-db7d206308c3 |  | tickbox | _________
text | 939482c8-20ca-533e-ad22-2f4ecbf66d95 |  | textbox
label | bb75851c-e636-545c-b868-18f5402ee48a |  | note | Key - H
label | 1061b288-54ed-573d-802b-b14fd36b9ab8 |  | note | UGL Key - H
label | 7659d112-e6a4-5789-a57d-6a80015f5e77 |  | note | SHL Key - H
label | 7d8566d0-52f7-5a2e-b05c-7363233d5d79 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 8364ed1b-7292-564b-a36d-e87f35463ae5 |  | tickbox | Material test certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.4 - Set Out
label | 5b640af7-da0f-5674-b12f-a29d3b39884e |  | note | Acceptance Criteria - Is the work area clearly pegged out for line and level?
button | 2188346c-b86f-57fe-8efe-06dcad2d8a1f |  | button | Acceptance | Yes,No,N/A
label | 1eec752b-4f77-5517-a6ee-4666446ac683 |  | note | Key - S
label | 31d4fe20-cf57-5760-802f-cc73a950b57d |  | note | UGL Key - S
label | c8b3591f-e72f-521b-83e5-a9dfe40470dd |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Pavement construction
checkpoint-status |  |  | checkpoint | 2.1 - Delivery of Material
label | f8436422-0e98-5f34-8449-ae9af83ed3da |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.2]
label | ec74fa6c-98c3-52cf-acc1-56af92472c13 |  | note | Acceptance Criteria - Inspection of delivered materials for approval
label | 2a032ae0-53df-5ca3-b278-16a0c9e788a0 |  | note | WITNESS POINT
label | 432befe5-fdc9-5466-815b-16af97275278 |  | note | Notice: Before placing
button | 0063de23-bed9-5525-a69d-6fe04e7911eb |  | button | Acceptance | Yes,No,N/A
label | fe41e074-4ca6-545a-956e-8384efcb23fc |  | note | Key - W
label | c2c74132-0e2b-53b1-b515-301ff09858ab |  | note | UGL Key - W
label | 97fa13fc-f4d4-5e12-b86b-26de2b3d74ed |  | note | SHL Key - W
label | 72a0e4f7-d3d7-52a4-8185-edfd8c65bc76 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 552710d9-ed21-54e9-a638-f63987b30204 |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 2.2 - Stockpiling of Materials (if required)
label | f8d2a80c-d3f5-529c-8c48-5660aa491153 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.2]
label | 445b78bb-ecef-59f9-98b2-ad507863b640 |  | note | Acceptance Criteria - Is the material being stored in an approved stockpile location?
label | 5bf48f82-7ace-51c1-b501-651165fc5e03 |  | note | ○ Stockpile foundation to be clear of vegetation and extraneous matter and shaped to form a crown to drain freely.
label | 142a78ae-f781-592e-ae98-2632c690384d |  | note | ○ Stockpile total height < 4m
label | 6b5f54bd-ad79-5ee4-b031-cd039585979d |  | note | ○ Shape of batter: Side slopes not greater than 1.5H:1.0V or less than 3.0H:1.0V
label | b5084cb1-eb27-519a-a4f1-1b4bcfe8a2e8 |  | note | WITNESS POINT: Ongoing
button | 5ce8fab3-83fe-56cf-b96e-61af4bc6522f |  | button | Acceptance | Yes,No,N/A
label | bed15e81-f8e0-5b6d-baba-7c53d638a03c |  | note | Key - W
label | 5ced5dda-a571-5f39-be21-7e8aaf49d60f |  | note | UGL Key - W
label | 8f0ecfed-a35d-5786-a605-c79c8488c80a |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.3 - Spreading Material
label | 7d165d30-fd25-5dd9-b702-7b4fc2adff91 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.3]
label | 3f7ca4ee-553a-5787-9476-dc18857fee69 |  | note | Acceptance Criteria - Prior to spreading, previous layer to be inspected by the Superintendent for approval.
label | c9bd8177-b3c7-5ba0-9967-d96f2cb5d35a |  | note | ○ Refer to ITP of previous Layer.
label | 35f83acc-023f-59d0-a29e-7c6264f52422 |  | note | HOLD POINT
label | 49a29732-3d22-55cc-b368-d5d5ab596027 |  | note | Notice: Prior to spreading material
button | c942c98e-8b10-552f-9d3f-44e835a75796 |  | button | Acceptance | Yes,No,N/A
label | d72ef7d1-e141-579a-bf93-0dc917070454 |  | note | Key - H
label | 0ff3b186-b846-5572-b165-4b201484f414 |  | note | UGL Key - H
label | 6f4f86f5-158c-542c-8756-f0e8dd5b6893 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Moisture
label | b13a1a5b-e5c2-5768-b69d-d5379eefcb37 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.3]
label | a8f20e05-99d2-5a81-8a63-b463f46eb57a |  | note | Acceptance Criteria - Has the material maintained at optimum moisture content (60 to 90% OMC), with additional water being added if required during compaction?
button | 8b14c15b-9f07-53f4-8596-d862a9b42146 |  | button | Acceptance | Yes,No,N/A
label | 5c9dde09-0af6-5803-82cc-ad6aff550694 |  | note | Key - S
label | de02fc0b-3a1c-50c8-8b9e-41799bddc4f9 |  | note | UGL Key - S
label | 598f39cb-4c00-5669-9f4e-eadb09eac9e6 |  | note | SHL Key - S
label | f9777d6a-094c-5c8f-8169-6a130e007414 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1b889c1b-347b-5896-9381-8d59105fd6e6 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Compaction
label | ea2f0c91-58fb-56e9-8d30-d0102b3820d4 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.4]
label | f2e76ab9-4791-5efb-8d2b-e844dbc28954 |  | note | Acceptance Criteria - Is compacted layer thickness between 100-150mm?
label | fffdf57b-e9c3-5ba2-9bf4-8662643f60e9 |  | note | ○ Has the layer been adequately compacted to a minimum relative compaction of 97%?
label | b5119c4e-9aaf-5ad8-96d0-f2453100a77c |  | note | HOLD POINT
label | 454ceaaf-c90a-5a8b-88fd-ba67f5cdd487 |  | note | Notice: 1 working days after getting results
button | 03342863-9e87-5aa2-ae09-9bd025a097a4 |  | button | Acceptance | Yes,No,N/A
label | f4b3ece8-aa72-5acc-b64f-fd0bcb607509 |  | note | Key - H
label | b8f42153-1320-5de8-ad8b-45e9dd5a19d7 |  | note | UGL Key - H
label | 65c4de17-8b74-54de-ac55-be2f752a9a36 |  | note | SHL Key - H
label | 7abf514a-68f6-59e5-8060-feec59033655 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 12ce8c47-8fbd-5c37-9cb3-7183c72087c3 |  | tickbox | Test reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Removal & Replacement
label | 5c423068-c40d-5299-aece-a0038a9482a3 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.7]
label | 568b6f2c-3a90-5027-ba28-09744ab2c6a1 |  | note | Acceptance Criteria - Superintendent to determine the extent of any rejected pavement to be removed. Before replacing the material, area to be reinspected by the superintendent
label | 9998ecec-ebb7-5935-a508-ca367256a22e |  | note | HOLD POINT
label | aa10fa51-1b72-59ad-bfc7-221226501a1b |  | note | Notice: 1 working day before next activity
button | c903c59c-64ca-56c8-b8e9-b4a0254a84e0 |  | button | Acceptance | Yes,No,N/A
label | 118b04fb-3727-501d-b8c8-670672f67258 |  | note | Key - H
label | c4ba6664-2c0d-5b57-ac4e-2840dbacb572 |  | note | UGL Key - H
label | 15c8c085-077a-5db8-83ac-09aff43dce81 |  | note | SHL Key - H
label | 4bf5bc9f-104e-578a-ae04-38c8337ad1c3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1bc61ece-3d9b-590c-bf1b-f7ccab6277fb |  | tickbox | As built reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.7 - Maintenance of Base
label | 3e33cf93-fe8e-5863-8f25-042cfe084d22 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.8]
label | 220354cd-e992-5960-9198-224a52dff90d |  | note | Acceptance Criteria - Finished surface of the base course must be maintained and appropriately drained until the wearing course is completed.
label | 29a09df0-ad90-5335-af5d-38f147433600 |  | note | ○ Cover base course with primerseal within 7 days of acceptance unless agreed otherwise with the superintendent (see 1143 Sprayed Bituminous Surfacing)
label | d0ae8caf-1ffc-5bcd-8f02-d5ea528a5a0a |  | note | ○ Non-essential plant to be restricted from using the pavement until primerseal is applied unless otherwise approved.
label | f779cb51-e260-5e5e-82f0-5259f55419f2 |  | note | WITNESS POINT
label | d14c8a4b-8b36-570b-8a01-2da7a2ebff1e |  | note | Notice: within 7 days of acceptance
button | 99f8124b-7c07-5b56-b2b4-80bb49488beb |  | button | Acceptance | Yes,No,N/A
label | 41530e2f-e992-5c0e-bab9-bf1fd60ec11e |  | note | Key - W
label | 96a04ce8-11d6-56b2-aa13-5a1acb3f40bc |  | note | UGL Key - W
label | ccd3fc3b-6a21-5ae9-b03c-008e29a06b28 |  | note | SHL Key - W
checkpoint-group |  |  | section | 3.0 Conformance check
checkpoint-status |  |  | checkpoint | 3.1 - Pavement finish
label | f02ad8b9-32ba-5989-ab7e-593199e6c95e |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
label | 9cfb4893-7494-5247-a560-6f25e889fbd1 |  | note | Acceptance Criteria - Has the pavement course been finished to a smooth and uniform surface parallel with proposed finished wearing surface?
button | f66f2f7e-b739-572d-95af-1494ac86d9ca |  | button | Acceptance | Yes,No,N/A
label | bda17945-e23a-5e0e-9ee4-1b8c57084688 |  | note | Key - S
label | 97a0255c-8b9e-5970-9b5e-d9d77924d771 |  | note | UGL Key - S
label | b2cbf1ee-2a6c-552a-b202-af473333d572 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Width and alignment
label | 59f6ebcd-3924-5d4e-a430-f9706f9e7452 |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
label | fa6f8655-1abc-552d-ba12-b64ae92af41c |  | note | Acceptance Criteria - Is the pavement width and alignment within tolerance: 0mm to +100mm measured from the design centreline (limited to 50mm per side)
label | 61702b5f-e80b-50c3-aa21-0b4eb8fd6712 |  | note | HOLD POINT
label | 103865dd-780e-5442-9e42-7e91686f63eb |  | note | Notice: 1 working day before next activity
button | a50b2a0d-1b73-502f-a0c0-3db9be8d607a |  | button | Acceptance | Yes,No,N/A
label | 28b6040c-f03a-5437-aa5a-4130f172234e |  | note | Key - H
label | 3a67f88c-d18a-5ecc-9d05-07704a0a69e4 |  | note | UGL Key - H
label | 44cbd6da-8a86-576b-a816-39b0580ecffe |  | note | SHL Key - H
label | 62a35657-05e6-5bb1-be01-41a295abf105 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 88f1f926-e1d6-54e3-aa30-deee655a95a2 |  | tickbox | As built reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Surface level of pavement courses
label | 24e584b5-2931-5928-9721-ecddd8652d0c |  | note | Ref docs - Spec. 1141 Flexible Pavements [Cl 4.6]
label | fa3005a3-4915-53fb-8c51-c226f5c7b767 |  | note | Acceptance Criteria - Is the pavement surface level within the following tolerances:
label | 79a35f1e-6e4b-5e34-badb-9d69a62bfce8 |  | note | ○ Layer Surface: 0mm to +10mm
label | a2c92769-0325-54e6-ab4c-624932d6fc51 |  | note | ○ Top Base Layer adjacent to Kerb and gutter: ± 5mm from lip level of gutter less thickness of wearing course
label | bf4cc4c4-38e8-5194-991f-4d4716fdeb5d |  | note | ○ Surface deviation: ± 5mm from 3m straightedge laid in any direction, after trimming and immediately prior to seal
label | 16fd1967-a0ec-55a7-aa72-da47310a6617 |  | note | HOLD POINT
label | 759f62e8-7c82-5b8b-af31-8106358ce237 |  | note | Notice: 1 working day before next activity
button | 7a3febc8-c442-56e3-989a-7951b4f0875f |  | button | Acceptance | Yes,No,N/A
label | 7ba5dff9-e126-5013-a85d-a683274bf802 |  | note | Key - H
label | 2c8d26b8-9759-5b91-b121-85a9db7efee3 |  | note | UGL Key - H
label | 9e05373e-829c-51de-a8b1-f1777d1605c0 |  | note | SHL Key - H
label | 638a7427-4e09-5f8d-b428-74235a214b7e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | be3de7e0-6aee-529f-9355-eded121fb66d |  | tickbox | As built reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Acceptance and closure of non-conforming items
label | 7395eb40-ed2d-5c02-b423-e1233bec44cf |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | d003d2d0-cd1d-51c1-9a20-3b547640119f |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 68b8cd7a-c02d-569d-9f03-94b0f995f111 |  | note | HOLD POINT
button | 864c4de3-0c9a-5c5c-9b49-6f9fa1834dca |  | button | Acceptance | Yes,No,N/A
label | 36671fdd-0573-513a-923f-3f706ed378cc |  | note | Key - H
label | e5843071-9e9f-5615-9a07-e9b20ad6c713 |  | note | UGL Key - H
label | 24acb938-f609-54d0-a1b5-eae9b2bbe10c |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-019 HDPE Pipe Installation - Rev.2 | 6feef3ec-0967-4646-a752-ab56a2049173
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 5f9bc9b5-d5db-5ef0-b595-037afe8eff14 |  | note | Ref docs - Issued drawings / Site copy drawings
label | c1e7cc8f-35c6-5d27-8a94-1e3662a05fba |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | b5e632d1-814b-50fd-a07c-d8efcd277a73 |  | button | Acceptance | Yes,No,N/A
label | 06195079-55e5-5fa9-9b97-650ca108be2d |  | note | Key - S
label | aade9b51-61b8-5167-b53e-eff747da2f95 |  | note | UGL Key - S
label | 2b0951b1-348e-5cd8-9e82-89fadf14265f |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 145223af-4c44-54ec-a9d0-f28523d5df3a |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | e758bfc9-d774-5504-a230-c67da6a488b7 |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | 07b8484a-2503-58b1-a01e-34f72ea7246a |  | button | Acceptance | Yes,No,N/A
label | 65282d10-cca2-52af-8c75-cd67fcb54c85 |  | note | Key - S
label | ae068240-1674-5411-b79f-b745910c7eed |  | note | UGL Key - S
label | 7f36be76-9a82-53a3-b280-3626bc946ec6 |  | note | SHL Key - S
label | c6b28620-28f5-5d7a-bd4c-9ddf201dca99 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | abb3d71b-43f8-53bc-8931-1e9c60ab8286 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Pipe Material
label | b12442f9-6921-5be3-bf94-7b7ac1423f49 |  | note | Ref docs - Drawings
label | f2c85ee1-27ff-570e-bee0-cb54eedb6b0e |  | note | Acceptance Criteria - Has the correct class & type of drainage pipe been supplied. Has the pipe been inspected to be clean and free of defects?
button | 60341232-cfd0-5562-b171-b9cf2adb7eb6 |  | button | Acceptance | Yes,No,N/A
label | 56e30506-1668-5d6b-8ccb-9785876915be |  | note | Key - S
label | e9982474-c855-5575-9768-e296f975736d |  | note | UGL Key - S
label | 61ce001c-df7a-54b8-bdf8-fd789a68fd31 |  | note | SHL Key - S
label | 62181d57-1fd6-5ad4-b7c4-d32eef2cf3ec |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 4a127dcc-5d88-5607-a608-6fc96fbe1735 |  | tickbox | Material conformance certificate
checkpoint-status |  |  | checkpoint | 1.4 - Embedment material
label | 00caa399-3309-5a0c-a1a9-79c0dc8fa9a8 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | c0851e04-caa5-558c-ae80-4ce5a0fdbbe9 |  | note | Acceptance Criteria - Embedment Material to be a cohesionless material with a plasticity index less than 6.
label | c7f46c78-06c8-5a1c-85d0-737cbd4ab0a4 |  | note | – – – – – – – – – – – – – – – –
label | 0306a507-2503-5ed5-a4df-8f03befa9827 |  | note | Table 5.1 Embedment material grading
label | ce1aa27c-1db7-5505-a5d9-2d2616841e48 |  | note | – – – – – – – – – – – – – – – –
label | 95671961-9362-5582-a44d-add7797f2af1 |  | note | Sieve size (mm) ¦¦ Weight passing (%)
label | 938ba9f8-9b0a-5ccb-b25e-8b6e32bed171 |  | note | – – – – – – – – – – – – – – – –
label | 5b28306d-e17a-5b39-87e2-dcf280a4919c |  | note | 19.0 ¦¦ 100
label | feff010d-5f45-5263-8401-f8a332abeb92 |  | note | 2.36 ¦¦ 50-100
label | 22e3e629-fbee-5908-a7ba-0a2a31c32871 |  | note | 0.6 ¦¦ 20-90
label | 278423dc-7046-5c20-a80b-687c8c857f19 |  | note | 0.3 ¦¦ 10-60
label | 151a365a-479b-5715-9bbc-cf05e181bc9e |  | note | 0.15 ¦¦ 0-25
label | 22d741f3-159e-543f-9c51-fdc1ade6e6ce |  | note | 0.075 ¦¦ 0-10
label | 006f0267-7c64-5725-9770-27f97c6218b0 |  | note | (Table taken from AS/NZS 2566.2, Table 5.5)
label | 95916354-9686-52d9-9313-ddb1b364d8e2 |  | note | – – – – – – – – – – – – – – – –
label | 86dbc983-6ed0-5967-9e0e-e892ef74dd0f |  | note | Alternatively, embedment material may be a drainage aggregate (10,14 or 20mm) as specified in AS/NZS 2566.2
button | ceb16d52-a9a0-59cc-8901-0f7c786bc1da |  | button | Acceptance | Yes,No,N/A
label | 383c2aeb-db5d-5dac-bcc9-34b153d80658 |  | note | Key - S
label | a30e5025-88a7-57d6-ba94-f7613367f6df |  | note | UGL Key - S
label | 2db87cfd-47ae-5267-b48b-c2eef986c911 |  | note | SHL Key - S
label | 2801482e-2630-5c92-87dd-2277cd9d814a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c82cd359-0cff-52a7-ae30-f9a89f8a3ad0 |  | tickbox | Delivery dockets
boolean | addb1478-3089-5d27-bca5-2a9883f2e471 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 1.5 - Welder Qualifications
label | bc329a6e-2ce9-5fdd-8120-0b094cff3f27 |  | note | Ref docs - PIPA TP003
label | f41d3ad6-3f60-5d73-8b18-d2b0ca610856 |  | note | Acceptance Criteria - Have the workers involved in welding of HDPE pipes been trained by a Registered Training Organisation?
button | 4e33fa17-46c4-5d80-a002-d9a37168195c |  | button | Acceptance | Yes,No,N/A
label | f1dcca82-c6b9-5d43-b0f3-8e3fb8ed039c |  | note | Key - S
label | 0e250ecc-9ad6-5dff-b5bc-b034a5e3ce44 |  | note | UGL Key - S
label | 870f7508-3b47-5ce5-9f28-24b3a8488fcb |  | note | SHL Key - S
label | e0bd5b88-1552-5b3f-9363-31ed84a8205d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c564d570-fbfc-50ba-81fb-3b421dc3853b |  | tickbox | Welders Qualifications
checkpoint-status |  |  | checkpoint | 1.6 - Underlying Lot Conformance
label | 87fe5c03-9c60-5636-bb3b-d92de4c53818 |  | note | Ref docs - Underlying Lot ITP
label | e54f2921-e1dd-5e95-a6e3-b85dee0c3c87 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
button | 53454913-17a3-5e8f-a215-57c00c20261a |  | button | Acceptance | Yes,No,N/A
label | 72de314a-0fa8-5a02-bd60-9c0b3d264efc |  | note | Key - S
label | b9853345-6af3-5957-b032-dd637b1ad8a3 |  | note | UGL Key - S
label | ed00f5ac-a4fb-5f71-9909-5fe2993db940 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.7 - Set out
label | 3b5a40c3-8834-5503-94e6-c75c24d9114a |  | note | Ref docs - Drawings
label | 54a5780b-ac6e-5a6a-b70f-e3b007112c1a |  | note | Acceptance Criteria - Setout of water line alignment and level. This shall be presented for inspection by the superintendent, if requested.
button | 378ab40f-b37a-53bb-9a93-6517a8962a99 |  | button | Acceptance | Yes,No,N/A
label | b450fbca-6d39-5e68-acfe-2aeb4182708c |  | note | Key - S
label | 9ce642c8-aca7-5b6a-ac26-284240a07bf7 |  | note | UGL Key - S
label | eb6ec6ef-6bf0-584f-be4f-5a41b9dc71ba |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation & Backfill
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | 1eab5661-7c76-509c-bc70-c675da9fc9e4 |  | note | Ref docs - Spec. 1352. Pipe Drainage [Cl 5.1], Drawings
label | f7ad6795-293e-5649-8ab0-ea317a0ce132 |  | note | Acceptance Criteria - Has the Trench been excavated to the correct width and depth to allow for the pipe size being installed?
label | fa5775be-fb50-537b-bb8f-51dcfb024642 |  | note | PE Pipes:
label | 37229b60-0da3-5f70-bb45-35c2b79aa506 |  | note | – – – – – – – – – – – – – – – –
label | 25888670-1fef-52cd-a220-28e17d9d21ca |  | note | Table 5.2 Trench and embedment dimensions
label | 72f9f5c4-ef4c-527e-8c60-2a242b748dec |  | note | – – – – – – – – – – – – – – – –
label | 202193bf-5c81-5fae-b81e-f53a398d1389 |  | note | Extreme external ¦¦ Minimum dimensions (mm)
label | d448357a-40d2-5c20-8442-00fa538366be |  | note | Dia (De)mm ¦¦ x : s : o : y
label | 9fe82829-02f2-539b-9eca-b9e2c3027c74 |  | note | – – – – – – – – – – – – – – – –
label | 903d002b-829f-5800-9595-3b6a3c876a93 |  | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
label | 7c9d83a4-7c78-5b49-a6ca-fa0c74c6b4c6 |  | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 76d558a3-1a6e-51b9-a68c-280bc66ba9df |  | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 57eae33f-96ce-52c1-a677-d6e127549c4e |  | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
label | 1cbd7d16-7678-5dd6-9a88-2e774859aa1c |  | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
label | 48b9057d-eed6-56ba-8a6f-9aea163dfde6 |  | note | – – – – – – – – – – – – – – – –
button | 954bb56d-c52f-5c46-85a2-3c2967d6ac93 |  | button | Acceptance | Yes,No,N/A
label | ca1f2180-a9a6-504b-84c0-aec6cf2a9c22 |  | note | Key - S
label | ac375b45-267e-5287-bb62-ab52ed2aacdc |  | note | UGL Key - S
label | 1eb7696c-7423-5cef-851d-f6b919d881db |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Compaction –Bedding
label | f0886642-d801-5004-8b95-b658b5d914d1 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | a5a55146-8d81-56ae-8fd6-4856f053e69c |  | note | Acceptance Criteria - Bedding:
label | 1a322db3-8ca6-5c9f-b49c-0e62ab6cd3f4 |  | note | ○ Has the correct thickness nominal of bedding been placed and adequately compacted below the pipe to achieve 70% Standard Compaction? (Compaction test N/A if drainage aggregate is used as bedding)
button | 56356b91-a9d4-530c-af84-354c4dadc433 |  | button | Acceptance | Yes,No,N/A
label | 25d1e664-9f07-5521-8384-b11fa29874d7 |  | note | Key - S
label | bdb7e4c5-4008-5efb-8693-298e8909c152 |  | note | UGL Key - S
label | 1973cb46-5308-5afb-9d23-ca421c641fa4 |  | note | SHL Key - S
label | 5ffc2803-1955-5a81-897e-4e25e3cc33d0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1c19fb82-298a-51a4-ac91-c99bddc36a58 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.3 - Pipe & Fittings Installation
label | 5150a476-4680-57d7-8ad9-fe4dac814793 |  | note | Ref docs - Drawings Manufacturer Specifications Spec. 1352 Pipe Drainage
label | dc8930a0-a533-53d0-a078-c377ff3d74e3 |  | note | Acceptance Criteria - Have correct pipes (size and type), bends, risers, valves & junctions been welded and installed as per manufacturer specifications? All weld records to be recorded daily on the HDPE butt fusion checklist
label | 18fca3c8-7fd9-5f6d-b9b1-20bb7a024390 |  | note | HOLD POINT
button | 2024f886-79cf-5025-a40f-2c7b0b3c05ff |  | button | Acceptance | Yes,No,N/A
label | f2ff35e0-28d9-5026-9545-bfaf773fa14e |  | note | Key - H
label | 1d48796c-c6a8-575e-a44c-0ae6c816bf51 |  | note | UGL Key - W
label | 73b8b6f6-98cd-5be4-a690-f04aacab53c8 |  | note | SHL Key - W
label | 971fa8a3-c58b-5c2f-b8e7-f38727c8bde9 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7abaff21-2289-5c93-9da9-402982ff8c01 |  | tickbox | HDPE Butt Welding Checklist
checkpoint-status |  |  | checkpoint | 2.4 - Destructive Testing
label | bfddd6b0-96fc-5af6-8406-926df39c74d7 |  | note | Ref docs - PIPA TP003, PIPA POP014
label | f9693f6b-3f19-59f7-8b86-35a2485168cf |  | note | Acceptance Criteria - Destructive Testing to be carried out as per PIPA guidelines using the Tensile Test Method at a NATA accredited laboratory. Frequency of testing will be one test every 100 welds. If a test fails the frequency to be dropped to one test every 10 welds until at least 5 consecutive conforming tests are received.
label | 0134f1c7-f7c0-5a7a-83d6-631dd02e3cc1 |  | note | WITNESS POINT
button | bac096e0-58fc-5c3b-b7e6-d0bfd901a434 |  | button | Acceptance | Yes,No,N/A
label | 916d7fc6-87b7-55df-81c1-92c69a4930b9 |  | note | Key - W
label | 4469eeb0-ef75-5e26-a898-40b57cbef9e1 |  | note | UGL Key - W
label | 0167fbfd-9cff-5ef8-adae-d9ba87253691 |  | note | SHL Key - W
label | 25903c26-b7b3-5453-bdfe-771fe560a73c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 1dfe9285-3444-59cc-a339-9a1c8165d96d |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Flanged Joint Installation
label | 281ff1de-701e-54e9-a3b0-5d7f102a999d |  | note | Ref docs - AS/NZS 2033 Cl 4.5
label | f39c93b8-1eb5-5208-b01e-d6e5fcbe406f |  | note | Acceptance Criteria - Flanged joints to be installed as per the drawings and manufacturer specifications. All flange joints to have a gasket or backing ring as nominated in the drawings.
button | 7bb240ed-6d44-5524-8a52-8338ee546252 |  | button | Acceptance | Yes,No,N/A
label | efade449-8cf9-56e3-9ac2-973805d38aee |  | note | Key - S
label | 10f65459-87b0-501c-b869-aee311b99333 |  | note | UGL Key - S
label | 88cdaa07-b9e7-540d-9783-fd8abb6c1d8f |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.6 - Backfill
label | a7425dab-5c78-5d01-bb69-2877015f1d26 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | 3a359970-c275-5ab6-b2f7-fbc0306260e4 |  | note | Acceptance Criteria - The pipe must be backfilled with the correct material and nominal thickness as per the project drawings and specifications
button | 6b8281e4-c82c-54e7-a7ae-e2894f2ffb2e |  | button | Acceptance | Yes,No,N/A
label | a12b872c-2688-5d05-bfc7-dd5213d7de36 |  | note | Key - S
label | 5e24ff7d-8e44-50f1-9be3-8b1b8721f06f |  | note | UGL Key - S
label | 950297f3-c848-5951-b27b-8332449c0e84 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.7 - Compaction – Embedment material
label | 7357cf0d-9afe-513d-ba86-46c1cd2615c6 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | 204df642-2600-58c5-b56d-df23e311c129 |  | note | Acceptance Criteria - PE Pipe:
label | fd151d90-e88f-5be6-8c04-cd6e915cce32 |  | note | ○ Side and Overlay: Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
label | d584643e-ffb2-5942-ba35-b114af8b4e4b |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 87763ebb-403b-59f6-9496-b10d7b4dedd4 |  | button | Acceptance | Yes,No,N/A
label | d55874de-7ea3-546a-b33c-576b1f75eb88 |  | note | Key - S
label | f5adde79-4660-5745-901f-9ba00463f4e7 |  | note | UGL Key - S
label | 31175873-73d6-54c4-b918-3174d3f4efd1 |  | note | SHL Key - S
label | 0a72f2ea-57af-5667-a4a6-06307ba777c7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 6e3d2729-e48b-5b2a-9794-4ea1acb92dd0 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.8 - Compaction – General Fill
label | bb884270-feaf-59be-a600-5abec26bcd56 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 05d12917-fbc1-5758-8677-6ec9dcee6006 |  | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
label | bc5d9241-7517-592b-85fe-ff58f4c13fdf |  | note | ○ Minimum relative compaction to be 92%
button | 83c40a5f-54f8-5c63-a42b-8c14a456cf2a |  | button | Acceptance | Yes,No,N/A
label | 73f31aad-58c7-5d92-a349-b59e0dc854dd |  | note | Key - S
label | adf492b2-6aad-5d2e-83a4-4322dc9b2125 |  | note | UGL Key - S
label | cae9f35a-bf6e-561f-af4b-04a455754847 |  | note | SHL Key - S
label | 9bb4978a-6ec1-5909-b652-893289272857 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9239e268-0440-5d33-9b4d-8dcfe8eebb75 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.9 - Compaction – Select Fill
label | 99d875bb-fe85-58e5-96f3-ea4e1823933a |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 10801a2f-3707-59f4-9581-861f619b3d28 |  | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
label | 612ab17d-8a28-55b5-b69d-c3473b39a27d |  | note | ○ Minimum relative compaction to be 97%
label | cb43e6d3-2048-53f8-bb62-c9b26fa9e14e |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 3cf32d62-c834-5e43-9773-be84621efc4a |  | button | Acceptance | Yes,No,N/A
label | 9da1c436-0bad-5fe0-bf14-c28271914954 |  | note | Key - S
label | e7e83739-6d73-5494-8537-eb8a7b3bebcd |  | note | UGL Key - S
label | 40826797-56b4-5756-b52e-20a838c3cc70 |  | note | SHL Key - S
label | 9b59522e-62b2-50ef-a4b4-1ee7985d0b7c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f1957a72-ff7e-5466-9285-e9ee6875fdd9 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.10 - Moisture Content
label | 19761f25-2593-5ae0-b042-aed249a07cd9 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | e10142cb-b80d-560b-abaf-0ec1e117b201 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | 610fb572-a673-5707-807c-d34bf335d7fa |  | button | Acceptance | Yes,No,N/A
label | 21e94893-7b23-5c13-95ed-8193222e1450 |  | note | Key - S
label | 13e3d2be-203f-581e-8d38-363c240a2050 |  | note | UGL Key - S
label | e775a438-3407-52ba-b2d9-1c94bc8dc289 |  | note | SHL Key - S
label | cc13a7f5-e89b-5bc8-81f5-43d482b771af |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d0ddeeec-b716-5cca-9dac-0026760a953e |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.11 - Marker Tape
label | 0a0a3811-7cdf-5719-b859-35aecd60c6fb |  | note | Ref docs - Design Drawings
label | 5ec0eb52-2bc2-5167-a2e5-764c57f5b747 |  | note | Acceptance Criteria - Detectable Marker Tape to be installed a minimum of 300mm above the pipe. Tape to be red and labelled “Danger – Buried Fire Main Below”
label | 78ef5e3b-28d0-5db8-b485-fa2d17bd5868 |  | note | Key - S
label | 8fe73eb2-66bb-5cfd-9b72-c09dca9975a7 |  | note | UGL Key - S
label | 610d5196-4b0e-5c31-aca8-892e9fab57e1 |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Testing, Commissioning and Conformance
checkpoint-status |  |  | checkpoint | 3.1 - Preliminary Pressure Test
label | 658b9809-c9b3-542a-9562-6d64543e4863 |  | note | Ref docs - AS/NZS 3500 Cl 17.3.1.
label | baac80e3-2bfd-5e97-bba2-8ce5033c7596 |  | note | Acceptance Criteria - Subjecting the pipe to 1500kPa for 30 minutes and checking for any leak.
button | af568c36-f89e-510c-96f3-3eb0601db28a |  | button | Acceptance | Yes,No,N/A
label | 7a357b65-c0ad-5a26-a3ac-f9b62fa41c5f |  | note | Key - H
label | 051871ec-a337-596d-ae55-7eb7dc152002 |  | note | UGL Key - W
label | dd429d1b-dda5-5b7e-8fc2-a8de293c5121 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 3.2 - Hydrostatic Pressure Test
label | a43c674a-b701-5dff-9f9e-625f35117764 |  | note | Ref docs - AS/NZS 2033 Cl 7.2
label | ee4f8f9a-8aca-57a0-8d01-382bc4a59f92 |  | note | Acceptance Criteria - Has the line undertaken a hydrostatic pressure test in accordance with AS/NZS 2033 Clause 7.2 achieving at least 1.25 times the maximum working pressure of the pipeline?
label | bf75e12f-dc23-52b2-ac86-20e75b5d7fb5 |  | note | HOLD POINT
button | 4f8780cd-5d08-565f-9fe2-c641d6dfe377 |  | button | Acceptance | Yes,No,N/A
label | 5023016b-c7ee-59a5-9fd1-36011a2d9d47 |  | note | Key - H
label | 89a39c94-e020-5d93-bf52-331fc126da37 |  | note | UGL Key - H
label | 4164db28-02fd-5780-bcde-5f94fedf6948 |  | note | SHL Key - H
label | 62475eef-04b7-506e-921d-3dd8fa329740 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | fd0044ea-de91-5f54-9c36-a20c3fe6dd34 |  | tickbox | Test reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Survey Report
label | c0da7a8e-15a3-512f-8e4a-c79dd30a644c |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13] RFI-026
label | 9ca798c0-1f5c-57bc-85b1-785d3177d4ef |  | note | Acceptance Criteria - Has an as-built survey of the system been completed to ensure all pipes are within construction tolerances.
label | 9931fa96-d006-5538-9618-b74b8ebdc08a |  | note | Plan: +/- 200mm
label | 176d5af6-3eeb-5360-a6d6-059104312b63 |  | note | Level: +/- 50mm
label | 55f715b8-faf0-54b9-861c-69d197ac5e71 |  | note | HOLD POINT
button | 4eadd377-06e1-5e0b-8b15-13c84751d660 |  | button | Acceptance | Yes,No,N/A
label | 33dbfa69-1d12-5866-9521-711b40ae2231 |  | note | Key - H
label | fe8c77ab-873a-5291-bc5c-edaad46c712d |  | note | UGL Key - H
label | b8cb4c01-e831-524a-9c30-6a08e5161a36 |  | note | SHL Key - H
label | 53db7897-62c1-52d2-8cc6-0c554b8b48e7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9e5726f8-b6ff-5862-b8f7-77bfcf521cc5 |  | tickbox | Survey report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Acceptance and closure of non-conforming items
label | 1d89d995-969b-51e5-ab26-1d1428e2fc8f |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | e8427969-ec9d-5077-a62c-7c05a0329ab4 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 5278f50b-546e-5c08-ab53-2e42bc1ae23b |  | note | HOLD POINT
button | 5c90771e-7cbf-5afa-9d81-4e4a491d4127 |  | button | Acceptance | Yes,No,N/A
label | 1e0dc990-5aee-569c-b3af-18d1ff5160b9 |  | note | Key - H
label | 01820eff-1ba4-5b97-8bdf-63aa4d1f87ac |  | note | UGL Key - H
label | 9da76c7d-ae47-582e-a0b4-12b76cd09c87 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-001 Bulk Earthworks & Checklist - Rev.3 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-001 Bulk Earthworks & Checklist - Rev.3 | 88fbcd33-6954-4124-8bb4-46efae87e1fc
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 4696e360-6706-5633-9663-8bcbe15254d0 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 013def14-cf79-5efb-869c-2b9bbb83305f |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | b9c399fc-6343-5a03-9f4d-50ee36d84a0d |  | button | Acceptance | Yes,No,N/A
label | 6135b702-35a2-58cf-bcb6-1559fb507f98 |  | note | Key - S
label | 85b45940-dae0-56c1-9a06-51985d98d5f6 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | c3a326aa-c6ab-5aae-9640-610b03b84454 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.2]
label | fd603c18-bd36-5ed4-a905-4ec863558523 |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | f7753dac-8340-5916-acf4-c75c82a06687 |  | button | Acceptance | Yes,No,N/A
label | 86107e68-e40b-57ab-a460-b896d999dcf1 |  | note | Key - S
label | 1317bf0e-2a16-5d3c-87ca-bd979da777a7 |  | note | UGL Key - S
label | 7c49259a-b987-55b1-ba10-b19b97523ddb |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Survey set-out
label | 87133787-5225-5350-839c-53fd8c6bf54e |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 2.2]
label | 3068e502-ed19-51e2-8b4b-ac8b489ba282 |  | note | Acceptance Criteria - Has the work area been set out as per the drawings?
button | 1b5471f2-dfe4-55e3-8016-454f9e3c4042 |  | button | Acceptance | Yes,No,N/A
label | 3d2afec8-e542-5c31-9fea-56ee0cca2ad6 |  | note | Key - S
label | 8fea5ff9-dffe-5e50-9f62-4bcbdbedaf1f |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Establishment of stockpile sites
label | 3beaacff-396e-5222-a76e-a8a86fa8f93c |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.1]
label | 097571b0-da21-56ff-9638-bc9b49aaca36 |  | note | Acceptance Criteria - Approval to use any stockpile sites not shown on drawings.
label | ffd20870-488d-5961-9fb9-58d94c6d757e |  | note | Notice: 3 working days before stockpiling
label | d2459f7b-e33a-5d02-b799-8dd49de807d2 |  | note | HOLD POINT
button | db3ad070-b24a-5217-a02b-4a117238bb20 |  | button | Acceptance | Yes,No,N/A
label | 2721a10a-cfa4-5c37-b169-e68cfe422612 |  | note | Key - H
label | 3158d9b9-bedd-5f94-a748-fb9933bb0210 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.5 - Excavation material classification
label | 6b50a60f-6f45-5750-87e8-045346b4e827 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.7]
label | b2f6099a-5fd5-5354-bce4-b114a3ccba64 |  | note | Acceptance Criteria - Ensure that excavated material is separated as follows:
boolean | b87a2944-89d2-5921-81c9-5ed54b5cadeb |  | tickbox | Topsoil
boolean | 672e6764-5101-5b54-b4e4-d8d0fccc39a8 |  | tickbox | Embankment Material
boolean | a37e4463-265b-560e-9624-3656c6c8351b |  | tickbox | Unsuitable Material
button | cd4b3d1f-59fd-5e54-92e0-887dcce16f99 |  | button | Acceptance | Yes,No,N/A
label | e8fbc2fe-8dff-53fd-b44c-0397006406d9 |  | note | Key - S
label | 43f89437-bea7-5c97-93dc-766d64367869 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Fill Material Conformance
label | 5515c456-7574-5dce-b488-ab2fa9dadd75 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways)
label | 9d8ec027-aaa8-5188-a32f-bbd8c439d5e4 |  | note | Acceptance Criteria - Fill Material to be free of roots, clay, topsoil, steel and organic material. Use primarily Site-won cuttings and supplement with imported material if necessary.
label | c83d6b3c-11d7-542e-93fb-a9c37031fa89 |  | note | CBR to be > 3%
button | 8127a4d5-6555-5f17-9b12-c66ea492024e |  | button | Acceptance | Yes,No,N/A
label | 44f7166c-cfd3-5226-a3aa-b764723a5b44 |  | note | Key - S
label | bf80df97-a76e-5f80-9f45-1f655f340e8e |  | note | UGL Key - S
label | 0fb8b48f-aa51-533a-8629-f133d46bf719 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Material Test Reports
checkpoint-status |  |  | checkpoint | 1.7 - Water management
label | 37c9bc8c-9c9f-5d43-bc04-17afa5dc432f |  | note | Ref docs - Spec. 1102 Control of erosion and sedimentation [Cl 3.7]
label | b99a4caf-338b-5286-a552-b231835a9a2c |  | note | Acceptance Criteria - Where necessary, have batters been rounded and catch drains constructed to allow for potential surface runoff during the course of excavation?
button | 741f393d-d7ae-5b2d-9375-d9eb9970fb2b |  | button | Acceptance | Yes,No,N/A
label | fa0ff31a-18eb-579a-bc83-b655b374743c |  | note | Key - S
label | e066d9f2-1ca4-577d-bbac-f017d0365d71 |  | note | UGL Key - S
checkpoint-no-status |  |  | checkpoint | Is the area in cut / fill / both?
label | fc3b7499-5312-52a5-bcef-421e48500f56 |  | note | If in cut proceed to step 2.0 and strike out section 3.0.
label | 1268a80e-20c8-5967-9630-9e822a0538f9 |  | note | If in fill please strike out section 2.0 and proceed to section 3.0
label | 4c788961-9e69-59fa-9f41-3bb2cd645505 |  | note | If in both proceed to step 2.0 as well as section 3.0
checkpoint-group |  |  | section | 2.0 Bulk earthworks – cut
checkpoint-status |  |  | checkpoint | 2.1 - Subgrade preparation
label | f461c88b-7d7a-5420-a4fc-cf2847dd77ab |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.1, 4.3]
label | 4f66a7df-f6a5-52fe-9161-ff4016c7da19 |  | note | Acceptance Criteria - Has the cut surface been trimmed to an even surface free from lose material and within tolerance of +/- 50mm from design floor level?
button | 61a28f2f-c44a-548c-a55a-8e3c71bac737 |  | button | Acceptance | Yes,No,N/A
label | 2aaefec1-6b57-55c6-8b92-0962653e7cfc |  | note | Key - S
label | 03d4d489-5209-5b95-ba80-cf7ffb6fde1a |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable material removal
label | 95a391d7-f824-5ac8-a410-22ae62246f9c |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.6]
label | b8691008-62f5-5a89-94c8-24198d9b9d2d |  | note | Acceptance Criteria - Any Unsuitable material to be removed as directed by the superintendent
label | 48987e77-0e37-537c-b5c1-074177fcd6f4 |  | note | Notice: Progressive
label | 2a9ccd3f-adb4-5c99-93da-5d7dff8928a4 |  | note | WITNESS POINT
button | 4fc7b399-e3b8-5ea0-ba25-56c40098f560 |  | button | Acceptance | Yes,No,N/A
label | 0e48c763-37ff-5c42-a254-6a358ac48ab8 |  | note | Key - W
label | b70e0bed-744c-59fd-878a-4750143238f9 |  | note | UGL Key - W
checkpoint-status |  |  | checkpoint | 2.3 - Unsuitable material floor inspection
label | 79f22ddb-7cab-560f-ae79-2326e9dabb19 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.6]
label | 7d1f0f90-60ff-58ab-9af0-ce05b999e72b |  | note | Acceptance Criteria - Floor of excavation to be inspected to determine sufficient depth of unsuitable material has been removed
label | 84974ed1-bf3b-59d2-8ca9-cef3bf316b32 |  | note | Notice: Prior to Backfilling
label | 9f3fb20f-c5c1-5f67-b07b-f8ce9a93c543 |  | note | HOLD POINT
button | 2adf6d8c-f44d-5522-91a2-0a84a1eed9fa |  | button | Acceptance | Yes,No,N/A
label | 17199164-84c4-5714-b06d-1ddce625ef8f |  | note | Key - H
label | e2c96273-c5d8-5b90-b909-3229c115db69 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - CBR Testing
label | 1d0f57bf-41c6-5435-9b71-8ab0f3341e45 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3]
label | df9caefa-248d-5ac3-b0c7-0f3a819a981a |  | note | Acceptance Criteria - Prior to ripping, test the CBR of the material in the cut floor to ensure it is > 3%
button | ba7a1352-70cd-5fff-8e3f-e41bdbb53241 |  | button | Acceptance | Yes,No,N/A
label | c16d7e1e-4450-57a3-9f79-3bc745e9208c |  | note | Key - S
label | b41245d3-dc88-5204-baf3-3295c02b5890 |  | note | UGL Key - S
label | 4f9d0af2-5039-577a-858b-118b11e172eb |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Ripping Cut Floor (Not required if foundation is in stabilised remediation pad)
label | 283eb690-01a7-5633-bcbd-24ee5ca39cea |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3]
label | 4cf9467b-3059-56f0-9244-6d3cf45eee61 |  | note | Acceptance Criteria - Has the floor of cuttings been adequately ripped to a min. depth of 200mm?
label | 861103f1-b231-567c-b570-29c28992ea1d |  | note | ○ The max. dimension for any particles in the ripped or loosened zone not to exceed 150mm.
label | 4e24dc71-ec40-5c5f-8e44-1794910f0168 |  | note | ○ Ripped material to be presented for inspection.
label | 3776d547-939f-5ea3-b026-f283c87675b9 |  | note | Notice: Before recompacting commences
label | 9285daa6-9fd6-5fdd-88aa-ef26f0ae43c0 |  | note | HOLD POINT
button | 41d23ae7-bec7-513a-a2ed-66ff60086fde |  | button | Acceptance | Yes,No,N/A
label | 5e03a6ae-7c3d-50be-a58f-e95b0866972d |  | note | Key - H
label | 5e8d1ed2-20c7-5dc5-8a6d-52459ac9fdbc |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Re-Compaction
label | fe430ead-0c05-5ec6-ac10-f6dbcd6c48cf |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.3, 4.13]
label | 183d4e54-adaa-52eb-aae7-57293678a4e4 |  | note | Acceptance Criteria - Re-compact the ripped floor to achieving a relative compaction of 97%
label | c9062d73-a958-5481-83ed-280c2a6cb2d8 |  | note | ○ If unsuitable replacement has occurred, compact the replacement layers to 92% and the design cutting floor to 97%
label | 930fefed-3947-527b-85df-fc27f0086125 |  | note | Notice: Prior to placing subsequent layers
label | b3c0dfae-6e63-516a-ba33-fad41d92691d |  | note | HOLD POINT
button | 8eb39b96-b627-5d88-971e-87456836f4a1 |  | button | Acceptance | Yes,No,N/A
label | 323561c5-007e-5ce9-83cc-e9cb4bec9016 |  | note | Key - H
label | e7c19d9a-3849-511a-b7c8-06dd5c53363d |  | note | UGL Key - H
label | 92ad1e3d-64b9-5d08-a638-c0c589be208b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.7 - Proof Roll – Subgrade (Not required if foundation is in stabilised remediation pad)
label | bd8b44d9-246d-52e9-8252-6661fafb7032 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | 4b2d77b8-5770-577e-aee1-b9df8a4a029a |  | note | Acceptance Criteria - Does the layer withstand proof rolling without visible deformation or springing?
label | b7f687c2-49d5-515e-a1a9-103b71e983bc |  | note | Notice: 2 working days before next activity
label | aa1e615d-83d8-5bad-b2e7-53fdad3601aa |  | note | HOLD POINT
button | 6338445f-b54b-5eb0-aff5-ccacec1a47d3 |  | button | Acceptance | Yes,No,N/A
label | bff96121-fd83-5b72-9198-3ce438f267d0 |  | note | Key - H
label | 77f8526d-5dae-57b6-b6a6-add97a841e20 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 Bulk earthworks - fill
checkpoint-status |  |  | checkpoint | 3.1 - Foundation Preparation (Not required if foundation is in stabilised remediation pad)
label | fb74d701-d333-5454-98ea-426e9dbef07f |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.7]
label | 7f4b06ef-abe2-59bb-ad41-9730a4af6b7a |  | note | Acceptance Criteria - Grade and level the area, adjust the moisture content and compact the top 200mm to 97% relative compaction
button | db862a33-326e-5548-ae65-fe4bfe9bb8f3 |  | button | Acceptance | Yes,No,N/A
label | 6afbfc88-44be-5c86-8fea-2727f858ef59 |  | note | Key - S
label | ad335d83-227f-59c0-b81e-e65caa8d57ad |  | note | UGL Key - S
label | 22adc40a-b218-532a-851e-58bbaba10fb6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.2 - Foundation Inspection & Unsuitable Removal
label | ac808c7f-e80c-5731-8371-568452891142 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.6, 4.7]
label | 90eef1d0-7385-5db2-85d7-2209e47385a2 |  | note | Acceptance Criteria - Embankment foundation to be inspected by the superintendent. Any Unsuitable material to be removed as directed.
label | 596cf531-372e-542e-9a5d-4c778e8f379c |  | note | Notice: 1 working day before next activity
label | ed6a07b6-432e-5466-86f5-b9067b2e2be3 |  | note | HOLD POINT
button | d4ea34d2-de1b-5aff-a44f-3df24328de97 |  | button | Acceptance | Yes,No,N/A
label | 40feab0d-c22d-5930-8390-a1c336bae061 |  | note | Key - H
label | cf6f0333-b8f3-525f-acbb-e4b7edfe400d |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Unsuitable Material Floor Inspection
label | 0aa52c79-aa6f-56fd-9f3e-d6e759b5176c |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.6, 4.7]
label | 43686d00-e0f3-5735-8a6a-e19c5ea62575 |  | note | Acceptance Criteria - Floor of excavation to be inspected to determine sufficient depth of unsuitable material has been removed
label | 25f9e4af-7e9a-5319-aa2c-d16590c92927 |  | note | Notice: Prior to Backfilling
label | 0269b13d-15bf-5bcd-81e2-4a10f847a47f |  | note | HOLD POINT
button | 75370c17-a183-507a-a818-5864379caf0f |  | button | Acceptance | Yes,No,N/A
label | 961afba1-98cb-5532-8db0-79dae7e688f4 |  | note | Key - H
label | 85ed0ff9-559d-54e5-aa12-abd452227be7 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Proof Roll – Subgrade (Not required if foundation is in stabilised remediation pad)
label | 13ff1fc6-0de0-5688-96f7-c288fdc0da1c |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | 366f0571-43d8-5beb-a382-f8db6b6bd3ba |  | note | Acceptance Criteria - Does the layer withstand proof rolling without visible deformation or springing?
label | 29893099-104c-5d42-91bd-f77ecd26cb5f |  | note | Notice: 2 working days before next activity
label | 55ad7eb2-e006-5417-bb9e-aa151f1bddd0 |  | note | HOLD POINT
button | b6720e68-973b-5324-aa2b-1e7670760684 |  | button | Acceptance | Yes,No,N/A
label | a9a26522-08dd-55e7-8edf-126406317156 |  | note | Key - H
label | 54adf87d-d559-597b-86bd-32f1145a53d5 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Fill Placement
label | 0f8c760f-b526-5ba1-9313-697cadc9cfe6 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.8, 4.10]
label | a0bf6be6-e2b3-5497-b43b-bc30a0a81f3d |  | note | Acceptance Criteria - Has fill been placed in maximum 200mm compacted layer thickness?
label | 93ce3dab-17a4-5502-b387-ba31c6d2d5b8 |  | note | (Approval required to increase compacted later thickness to 300mm)
label | c618a1c1-7113-5e42-baf3-0b2771b9b230 |  | note | Note: Maximum fill layer thickness adjacent to structures 150mm)
button | f8af81f7-bd30-5bb3-b992-5539f28fe4c9 |  | button | Acceptance | Yes,No,N/A
label | 8d766eda-d4e0-5c81-9975-f0d61d0e5592 |  | note | Key - S
label | ad886a6a-8226-5c13-a9a5-559304799182 |  | note | UGL Key - S
label | a3e3576f-27c7-583f-8baf-2e5866ee3d61 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery dockets (if imported)
checkpoint-status |  |  | checkpoint | 3.6 - Moisture Content
label | 979ac656-16ac-59a9-8f53-a6181c78c3cd |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1]
label | 5d2d97e7-3eb6-59f0-9ec9-26e62503f625 |  | note | Acceptance Criteria - Is the moisture content within the range of 60% to 90% of optimum moisture content for all fill layers
button | c01c5f92-8549-5799-9e30-d455adb22434 |  | button | Acceptance | Yes,No,N/A
label | 325aaa53-02a0-5be9-bc2b-bd738a036ed7 |  | note | Key - S
label | e3c2dfe4-76c2-5cda-970e-08a3eb9fdce0 |  | note | UGL Key - S
label | 9ac9edec-6dd6-5e01-a047-2633aa78a381 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.7 - Compaction (General)
label | 4e03acbc-6071-5187-8681-d32ae69b8dd6 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1], Spec. 0161 Quality (Construction) [Cl 7.2]
label | 1b2b4ad5-45eb-5def-a365-6f0667c2b820 |  | note | Acceptance Criteria - Compact any material used for unsuitable replacement, general fill (>1.5m deep), verges and medians to a relative compaction > 92%
button | 1c052d3f-b9de-524c-a1a6-5a2b51b6d9e5 |  | button | Acceptance | Yes,No,N/A
label | c745cbce-8bbb-5303-a801-0cd6d612d01a |  | note | Key - S
label | 8a92805d-b290-5781-8ee7-9b5f4c82054d |  | note | UGL Key - S
label | 6b3f53e8-18c0-5ec6-9ad7-ba9ec36d505b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.8 - Compaction (Selected Material Zone)
label | a4a737d3-0d8d-5e20-8c03-dcf308762421 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13, 7.1], Spec. 0161 Quality (Construction) [Cl 7.2]
label | 3394df36-966b-5805-b085-5ace6661f960 |  | note | Acceptance Criteria - Compact any material used for shallow embankments, Select Fill or behind kerbs to a relative compaction > 97%
button | 16d38a1a-f6d0-563b-96d4-76744a412b3b |  | button | Acceptance | Yes,No,N/A
label | 07fac88d-0f4f-5540-9f39-ca96018be5d2 |  | note | Key - S
label | 72c377f3-1238-56b1-ace8-0db945627cee |  | note | UGL Key - S
label | e7e75c42-9ef6-5bd8-bde9-f953a34353db |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.9 - Compaction (Fill adjacent to structures)
label | 57714ef7-d9b2-5c1a-a534-2608ca273919 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.10, 4.13]
label | 2557e20a-fbfd-5b53-b6d6-10b1654217be |  | note | Acceptance Criteria - Compact all material adjacent to structures to achieve a relative compaction of 92% (up to 1.5m from top of pavement) or 97% (within 1.5m of top of pavement)?
button | 89f10f07-e954-5aba-a2c2-051f779ce024 |  | button | Acceptance | Yes,No,N/A
label | 7a8032b6-4499-54e6-bb73-05b09e008da3 |  | note | Key - S
label | 028820a7-5089-5242-bf24-c127ca0398dc |  | note | UGL Key - S
label | b295a7fb-a103-5bcf-9fe6-05abe0bab800 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.10 - Material Conformance (Fill adjacent to structures)
label | f7bfc18d-5aac-5bc1-82fd-6944495568fb |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.10, 4.13]
label | 43c39af6-f5df-589a-bf0c-1d7b3d2d5ae2 |  | note | Acceptance Criteria - Backfill material granular and not exceeding 50mm particle size
label | a80f2c71-ea63-586c-898e-d19cbdbc1636 |  | note | ○ Plasticity index in between 2 & 12
button | 16e89a58-4df0-5ea4-aed4-aeb6ec3278eb |  | button | Acceptance | Yes,No,N/A
label | 9921222c-267c-5548-876f-14bd4dc403ba |  | note | Key - S
label | 8989c222-6093-5db1-bba2-c7a0949cb93e |  | note | UGL Key - S
label | 045403db-fc2c-5947-845f-96fe87d2fa2c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test reports
checkpoint-status |  |  | checkpoint | 3.11 - Proof Roll / Select Material Zone Inspection
label | f7efddd8-f163-52b0-8695-bdf7543398f3 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.13]
label | 8f60cc89-8d14-5ffd-a205-a2d64f54386d |  | note | Acceptance Criteria - After trimming & compaction, present the top layer of SMZ for inspection.
label | ba2ac883-1b7d-5c12-9f36-821645345d8c |  | note | ○ Does the layer withstand proof rolling without visible deformation or springing?
label | 51915861-4640-50c6-bd5e-ab4acfbf304f |  | note | Notice: 2 working days before next activity
label | e3eaf345-e0a7-5bad-8de8-a6f8bdaac16a |  | note | HOLD POINT
button | 27689cbe-885a-5fb4-9520-d77a9cededce |  | button | Acceptance | Yes,No,N/A
label | d33e7a56-581d-53c3-8ed9-8cfe51eaf099 |  | note | Key - H
label | d8e623de-77e2-506a-b416-b2ab7832a385 |  | note | UGL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 Bulk earthworks - other
checkpoint-status |  |  | checkpoint | 4.1 - Batters
label | ac21fd95-b28d-5372-9caa-2eb3b137ad3d |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.4]
label | 40a5098e-70a6-5d5d-99cb-c6f830c8a7b4 |  | note | Acceptance Criteria - Provide batter slopes as shown on the drawings. Clean the cut faces of any loose or unstable batters as the excavation proceeds
button | c7ead50c-f5b1-5648-a656-60dab4594f83 |  | button | Acceptance | Yes,No,N/A
label | 3c164c4c-1b63-5741-8999-9fee218e5fec |  | note | Key - S
label | f8b8f131-8de8-52a1-822f-533706770888 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 4.2 - Cut to Fill Transitions
label | 89a4625b-a3f6-5060-aa13-6fa759ab592b |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.5]
label | 88a0fec4-b27e-534f-a470-74843b15df2f |  | note | Acceptance Criteria - Excavate a terrace as per the figure in Cl 4.5 for the width of the SMZ to a depth of 900mm below the cutting floor
label | b28b1c6f-c70b-5332-8aa6-7e34abe46306 |  | note | Notice: 1 working days before excavating terrace
label | d24d9c08-e10f-5273-a733-098e4a8e0dff |  | note | HOLD POINT
button | 404c55ec-93e1-54bf-bd48-c17bf9559867 |  | button | Acceptance | Yes,No,N/A
label | d173e752-03e8-57a7-97a9-6775eb21b810 |  | note | Key - W
label | 12171cfb-96d4-5c76-bcb0-73df88de9b1e |  | note | UGL Key - W
checkpoint-group |  |  | section | 5.0 Conformance check
checkpoint-status |  |  | checkpoint | 5.1 - Width and alignment
label | 694ba50e-899a-5bbc-a9e9-02fd88432907 |  | note | Ref docs - Drawings
label | 6c42acac-64dc-58bb-b2ca-53432e984c31 |  | note | Acceptance Criteria - Has the pavement been constructed at the correct width and alignment as detailed in the construction drawings?
button | 6fdfc552-bff0-5894-9ac7-b3879b4d8b80 |  | button | Acceptance | Yes,No,N/A
label | be85e040-cc15-57f9-8db9-01a4f09ce257 |  | note | Key - S
label | 41291405-f7e3-5e59-8546-a5decdb1c7b9 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 5.2 - Level Conformance – Top of Embankments
label | 004278b3-f6fe-5d14-b5f5-f9c1d834a9e6 |  | note | Ref docs - Spec. 1112 Earthworks (Roadways) [Cl 4.8, 5], Drawings
label | 3c29808b-09c8-594b-8507-b7521ae632db |  | note | Acceptance Criteria - Trimmed top of embankment to be within the range -40mm to +10mm from design levels
button | 976d33fd-033e-5d84-a15f-007db5f93b74 |  | button | Acceptance | Yes,No,N/A
label | 74bd0c03-dc7f-55cd-99c7-e4bef54dcb68 |  | note | Key - S
label | 965bb813-9b26-5b71-bafa-e099876fd375 |  | note | UGL Key - S
label | 6f6c8d7f-415d-580c-98bd-4dd06e70e575 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As built report
checklist-flat |  |  | checklist | [5 empty] | Yes | Historic Lot | 9112d206-004b-46cd-a660-624c1afbb9a5
checkpoint-status |  |  | checkpoint | Optional Document Upload Below
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-024 Pit Works Completion - Rev.1 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-024 Pit Works Completion - Rev.1 | 9299f117-aea5-474d-8a01-74ccbaae6af6
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | e61ec239-8510-57e5-8992-dd3048295b6e |  | note | Ref docs - Issued drawings / Site copy drawings
label | 55181d03-e94c-59bb-96e4-0db291eed78a |  | note | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | ed1856d2-cd89-594d-9080-24c142478f97 |  | button | Acceptance | Yes,No,N/A
label | 9684aed2-1ac6-57ab-97d2-eece8586e134 |  | note | Key - S
label | 6089f9a4-4f77-5766-b14b-6a52f1cfe4cd |  | note | HPP CON Key - S
label | 06f3e7fd-0cde-5f77-85d3-7b66a7735d29 |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 45db2d01-0476-5249-9646-0facb254d64f |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | 067ddfb4-a961-5660-98f8-dc2c7e5095f2 |  | note | Acceptance criteria - Prepare a lot map for traceability of the work area
button | c41f31fa-5bfd-5dc7-b13e-4b2f00ac7403 |  | button | Acceptance | Yes,No,N/A
label | d8fefdfd-9b05-596d-8676-febc2620f3be |  | note | Key - S
label | 98873dd8-0397-5370-9644-843ca8105042 |  | note | HPP CON Key - S
label | 477b0f5a-0b9f-50c9-9b34-3495df7155e8 |  | note | HPP QA Key - S
label | ef45c7d2-2339-509a-8c6d-fac12f1f7301 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | a73ce992-ddd0-5dfc-aeeb-829936401382 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Set out
label | 8ec6cb18-8acd-5121-b264-771825158194 |  | note | Ref docs - Drawings
label | 70962006-3e98-54b6-9e35-959b0bd81eba |  | note | Acceptance criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | 112c0b17-54f9-5959-b8d7-2331058960a2 |  | button | Acceptance | Yes,No,N/A
label | 89a280d8-1362-5386-9059-2fa58949e100 |  | note | Key - S
label | 17339e9b-484d-5be9-b40d-c51cf2ea252b |  | note | HPP CON Key - S
label | cf51b3f5-ae9c-5ff5-85ba-a3d48dbf13b3 |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Pit Handover
label | f044fd67-833e-54d6-8171-35e24a195947 |  | note | Acceptance criteria - Each pit shall be visually inspected prior start of the completion works. Any defects recorded must be reported and rectified before receiving back the pit from HPP.
button | c2dc11e7-3fec-5b40-8fd4-77ca3234ed7b |  | button | Acceptance | Yes,No,N/A
label | 791d1645-f70a-5e9e-8ed3-3ada10155587 |  | note | Key - H
label | a6baa41a-e393-554b-8803-8606c74b4341 |  | note | HPP CON Key - H
label | 7cd3fe3d-1d1a-5350-953b-6b5e380b9439 |  | note | HPP QA Key - H
label | ec9bd782-64c9-56ff-984f-f99af20053ac |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bd8f6d18-792d-55ff-bf85-14b9b7a9a17d |  | tickbox | Joint inspection with HPP rep
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Pit Completion Works
checkpoint-status |  |  | checkpoint | 2.1 - Pit Lid Installation
label | abd0ef4b-dbb8-5208-9f7c-08e1f091c6fb |  | note | Ref docs - Drawings
label | e2032b54-0666-5cae-8e7c-18d706b60317 |  | note | Acceptance criteria - Pits Lids to be installed as per drawings and manufacturers specifications utilising certified lifting points.
button | 4925e610-26c9-566e-afa8-5f47838b1fa2 |  | button | Acceptance | Yes,No,N/A
label | 74b4a2b6-fb8c-5e0a-8d6e-d02a4f70e7d5 |  | note | Key - S
label | 322d5375-b51a-5c2e-85e7-530fe48f9ea9 |  | note | HPP CON Key - S
label | 704286ee-96be-5b54-9def-1b175c0af115 |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Access Covers & Grates
label | 18e1d97c-3992-5b86-a12e-7fdfc0d436a4 |  | note | Ref docs - Drawings
label | 21f8b887-65fd-5ded-a2cc-a269d15a08e4 |  | note | Acceptance criteria - Access covers, grates and frames to be installed as per the drawings AS 3996
button | 528bc8da-86e8-54fc-a712-384026b99043 |  | button | Acceptance | Yes,No,N/A
label | 09efdcdc-eab1-5483-936c-9c0983c2c780 |  | note | Key - S
label | 57137039-9949-500a-9529-e1915f9101b0 |  | note | HPP CON Key - S
label | 358a1700-a7ee-5e98-a1b9-88b9f4bd9a1e |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 2.3 - Step Irons
label | 1fb84644-c189-59ff-b767-ce198566eb13 |  | note | Ref docs - Drawings
label | 6214f175-073f-51d6-b7c1-f952b3dfd7f6 |  | note | Acceptance criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | 6fc41aca-3238-5c1f-a590-a2ea53277c37 |  | button | Acceptance | Yes,No,N/A
label | ce723ef7-c0e3-5810-8b42-c3ae352b01be |  | note | Key - S
label | 3b2e50f3-6d62-5921-960b-94b394503ff4 |  | note | HPP CON Key - S
label | 7d7a8dca-d691-53dc-a03e-b59bdbdd98be |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 2.4 - Pit Jointing (if applicable)
label | 283fcc88-7339-558c-96d1-4fc0b18b28a5 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
label | 1569402b-9d47-5258-b51f-403a615bf110 |  | note | Acceptance criteria - Internal joints between precast pits and riser units to be waterproofed as per Symal RFI-037 & manufacturer recommendations.
label | 5e9e13a9-b9fb-5005-94ac-59278885253f |  | note | ○ External Joints between pits and abutting concrete pavement, kerb or structures to be a 10mm isolation joint.
button | 71779113-9d1b-5066-a3ec-e09880d1b1ad |  | button | Acceptance | Yes,No,N/A
label | b0347bb7-6504-5add-9b83-0ac413af1f6f |  | note | Key - S
label | 6cebeb2a-7037-5d2a-a983-9195d9477b7a |  | note | HPP CON Key - S
label | 22295906-6b26-590b-9d7f-82d4adcae0c9 |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 2.5 - Brass Marker Plates
label | 4c4eba4c-3157-57c5-af1f-3e1b26d67f74 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11] Drawings
label | 1ab208ca-7298-5d1c-8f27-f6bd6954ce16 |  | note | Acceptance criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
button | 47901522-0fb7-5305-8a76-e0e38106008a |  | button | Acceptance | Yes,No,N/A
label | cbf7d792-403a-5ebc-a0ad-ca1c3126c6d9 |  | note | Key - S
label | 605d7ad5-fd0e-55a8-aae7-e2544e738d9f |  | note | HPP CON Key - S
label | df173096-0d8c-50a1-bd0e-7a564afcdf0b |  | note | HPP QA Key - S
checkpoint-status |  |  | checkpoint | 2.6 - Cable Markers
label | 5ed0c067-b8e0-59ed-b65f-07b555c473c3 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.10]
label | b56769d5-14f2-551a-91cf-dfc24c784cd5 |  | note | Acceptance criteria - Install Concrete Cable markers on the surface of all underground cable joints, at every change in direction, and on straight runs at least every 30m.
label | 73ac4fc6-ac91-5d3d-a3fe-3ef1a085c1e5 |  | note | ○ Markers to be a 400mm square and 100mm deep concrete block with a brass label attached. Label to identify conduit type and direction.
button | 843b76ec-9ca5-53c5-9f90-4186e3ef63fb |  | button | Acceptance | Yes,No,N/A
label | bbc7edd2-2eef-5f44-b018-f7ab4665430c |  | note | Key - S
label | 0e952a99-3b81-58d4-9585-c7a4b4d7bfd6 |  | note | HPP CON Key - S
label | 8662dcf3-86a7-56a7-9bd1-0b72a037b1b2 |  | note | HPP QA Key - S
checkpoint-group |  |  | section | 3.0 Conformance Check
checkpoint-status |  |  | checkpoint | 3.1 - Survey Report
label | c2a71412-116d-5cf5-bb2c-9286ad436339 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | ec149948-100f-5a7f-9834-8afcd0d5682a |  | note | Acceptance criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | d660b14e-1587-5757-8112-2e22ac772606 |  | note | HOLD POINT
button | a89e3409-ba2f-5c30-bd06-f2008493d924 |  | button | Acceptance | Yes,No,N/A
label | 2f3a6307-2dbf-5ee4-9f02-33471a9b5f51 |  | note | Key - H
label | f103582b-02be-5740-b75a-f9554541a3e3 |  | note | HPP CON Key - W
label | bc113066-15df-514b-b3ef-88791cf2b7c7 |  | note | HPP QA Key - S
label | 800bb9b9-bd30-5113-af0b-1f9da1f3c7a2 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 885cd394-acf0-51f9-a392-0005efa9f5c1 |  | tickbox | Survey report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Acceptance and closure of non-conforming items
label | 69d49436-69b0-58a0-9e23-ade7f3ab53b9 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 4d0a49af-b892-5b34-b4cf-1a21b3e1612a |  | note | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 1c99141d-39fb-5bf6-b79d-c0ac1f4ead9b |  | note | HOLD POINT
button | a30d12f0-917e-5081-a74a-ba88334e51bc |  | button | Acceptance | Yes,No,N/A
label | e6e76ae8-030a-5e45-9d11-4e56b021e05e |  | note | Key - H
label | e5d16bea-9de5-54cb-b1df-93521a518aee |  | note | HPP CON Key - H
label | 750ebf31-0c0d-5e44-af8f-9b1262ea48ec |  | note | HPP QA Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-018 Conduit Pits (In-situ) - Rev.2 | 948b8c0a-21e7-4bad-b3f7-f9244f4a8714
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | d94fabb2-4c63-5dc1-9756-9a4c4ef18f37 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 8d8ef602-28be-5b9f-a99d-9afe5d150deb |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | eeedd88b-fb82-56b6-8671-63e12f6f8eb5 |  | button | Acceptance | Yes,No,N/A
label | 3fae3d80-69c2-5fb9-9cae-65ebf7fc7a06 |  | note | Key - S
label | 0a5f6fd1-a9aa-52f8-a817-ec295473f341 |  | note | UGL Key - S
label | 25396972-0970-5e8e-bea6-bc2363939bd8 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | f4088ac4-1aa2-59fa-b2da-a09ea4340ff0 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | 56e7ad99-9f15-5342-a100-7d82cac9cf3b |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | a93d5c68-58be-5685-bc2c-f207760f4f65 |  | button | Acceptance | Yes,No,N/A
label | cb1a23db-91e8-5b49-96d2-ff55f2406cf0 |  | note | Key - S
label | 8c16765a-b2c9-59eb-b783-1e2e00ca2c51 |  | note | UGL Key - S
label | 6773634b-960a-58dc-9f76-980e8474980a |  | note | SHL Key - S
label | fc37cd2a-d112-54bf-836d-bc615887198d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 5af32261-ccc0-5725-ae07-74596f175fb3 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Underlying Lot Conformance
label | 3e620195-dee3-560b-8d28-2902ed740290 |  | note | Ref docs - Underlying Lot ITP
label | f1a47fe9-a1aa-536d-96bf-269ab6eb6dac |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above. Refer underlying lot ITP(s)
button | 52d977eb-0612-5dc0-90d3-b783e5d52922 |  | button | Acceptance | Yes,No,N/A
checkpoint-status |  |  | checkpoint | 1.4 - Set out
label | 0521baa2-d9f9-5574-b602-d912c13e187f |  | note | Ref docs - Drawings
label | db0859f5-1358-5240-84b8-2ff8342391ee |  | note | Acceptance Criteria - Setout pits to the location and levels on the drawings
button | 46ed1b8a-7158-52f0-a0fe-32302555e094 |  | button | Acceptance | Yes,No,N/A
label | 677cc112-a137-59a0-a20c-1ce2bea4f5d3 |  | note | Key - S
label | 487069ad-efa3-5eb1-a282-7198153727d9 |  | note | UGL Key - S
label | d7be1716-bfbf-544f-9ec2-3c393253a501 |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and Bedding
checkpoint-status |  |  | checkpoint | 3.102.1 - Excavation
label | 9d57023a-8986-53a7-ac6e-57faf12f2db0 |  | note | Ref docs - Spec. 0002 General Electrical [Cl 6.6]
label | 4ef34b1a-cbe3-5a9f-ae48-8d9351339f68 |  | note | Acceptance Criteria - Excavate to the depths and widths of the design drawings
button | 63c24624-673b-5443-b703-76a8815f3a51 |  | button | Acceptance | Yes,No,N/A
label | c6ece6c2-76ec-5f04-8aec-20d96645b74d |  | note | Key - S
label | 413cbf32-4295-5dcc-a060-5f68b24b114d |  | note | UGL Key - S
label | 733f74f7-d065-5516-8348-0ce755dacd86 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Place Bedding
label | a7c89144-1003-5f02-95f0-a643a62f59d2 |  | note | Ref docs - Spec. 0002 General Electrical [Cl 6.11] Drawings
label | 470900b9-a868-52d0-81e9-3383f64d304d |  | note | Acceptance Criteria - Pits to be installed on a 100mm thick compacted sand base.
label | 7e3af4e9-85c4-588b-a486-76c91577c7af |  | note | ○ Alternatively, a 150mm thick 20mm crushed rock layer can be used if the pit floor is below the water table.'
button | b6619676-0e3e-52b4-b1ce-8949ca03d0d4 |  | button | Acceptance | Yes,No,N/A
label | 8a09bd64-b62b-5908-99a0-4b34cd82d079 |  | note | Key - S
label | 6cba7b9e-c75c-546d-ad89-44410a6b13ec |  | note | UGL Key - S
label | a815db8e-42db-5754-b242-dd82ad2c92c1 |  | note | SHL Key - S
label | 0632b814-9272-5751-919d-c2d5c191f5c8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 14f349af-37ff-577d-b76d-7c04dfd52b6f |  | tickbox | Material Dockets
checkpoint-status |  |  | checkpoint | 2.3 - Blinding
label | 47b3bc8c-b9d6-5caa-b90c-66b5ed472bbc |  | note | Ref docs - Drawings
label | 7b736405-20d9-5bd4-9f2a-5e37d0be05ff |  | note | Acceptance Criteria - Blinding (15MPa) for Pit Bases to be a 50mm thick mass concrete layer.
button | b426333b-5104-51da-a51b-2b171dcd28f9 |  | button | Acceptance | Yes,No,N/A
label | ecf8c69c-5d0f-5c70-8734-b9dea46963cd |  | note | Key - S
label | 1590100b-e369-5200-8228-a81426b9173d |  | note | UGL Key - S
label | 340b8ebd-9bb5-5713-af5d-408d8c538fce |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Cast in-situ structures
checkpoint-status |  |  | checkpoint | 3.1 - Formwork (Base)
label | 44a5da7b-56fb-5eff-92fe-9c872bff2507 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3] Drawings
label | 0d9dec8e-2b1a-5a26-8f1c-1652378b7261 |  | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | 61ff1710-74ad-5bce-957c-ff5cd10107a7 |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | dccb2817-f867-50e0-ab09-9cbdb2a7085a |  | note | HOLD POINT
label | 940fd6b0-67f8-54ae-8181-62452d2df4e9 |  | note | Before Placing Concrete
button | 40590182-6461-5b84-9fe9-71bd02f9eb1e |  | button | Acceptance | Yes,No,N/A
label | 4d6a3e4a-41dc-5c02-b9ed-f8789d6ae619 |  | note | Key - H
label | cdee1992-e1e5-5914-be8c-99214ef5aa54 |  | note | UGL Key - H
label | 730b970e-4b1a-56bd-8aaa-1fa5923ec513 |  | note | SHL Key - H
label | 151db578-6653-591b-8232-8581e6d28788 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 57835752-4319-58c7-b7ae-374d8c3180f4 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Steel reinforcement (Base)
label | 50fa6676-48d6-542b-849e-44f405c7d03a |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | 46ac5531-6dcb-5a3e-b84b-bdd9ee0ea893 |  | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | 9335e728-2aec-51bc-9c55-d71fd95748a7 |  | note | ○ Concrete pre-pour inspection complete.
label | 396f4e81-a5c6-58a0-bc19-70c338a11d42 |  | note | HOLD POINT
label | d598caa8-22a5-53b7-a981-3ece7c9e3e21 |  | note | Before Placing Concrete
button | 304f5d13-5942-5da6-b7e6-d17ffc7643c1 |  | button | Acceptance | Yes,No,N/A
label | bdcf67ea-bcfa-54b0-9a63-aabf3efc277f |  | note | Key - H
label | 034eb040-4b71-509e-a502-dc70658bc1a9 |  | note | UGL Key - H
label | 7c09f218-e49e-587d-b22e-de0ddad6daa4 |  | note | SHL Key - H
label | 2f663674-2b92-519f-a680-6be3ed709e15 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 37f2e658-f957-5be0-8b31-911a48e97ea3 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Formwork (Walls)
label | 9ffe4a18-584a-559e-b601-67ce27ac2194 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
label | 69384eba-edd2-523a-8b1c-49e15625a660 |  | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | f2d11411-e075-5a5c-90dd-9db5ae974857 |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | 7d96f31b-fd8d-597b-8223-b3db4528fcf6 |  | note | HOLD POINT
label | a17fca45-a238-57e7-a110-20594a879140 |  | note | Before Placing Concrete
button | 9a2cb1d0-ccc5-572a-b424-805de5115143 |  | button | Acceptance | Yes,No,N/A
label | 79b50740-0aad-5968-b8b2-62b38aeecee1 |  | note | Key - H
label | 2c02e33e-7284-5b26-93ca-f5a002b0b5d4 |  | note | UGL Key - H
label | 349d222a-da19-5d7b-9472-8c06f126b6e1 |  | note | SHL Key - H
label | 860cdcd5-035f-5b96-8e26-1cd752cba69a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ab3d6a7c-7be5-5936-994c-f0c44424f558 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Steel reinforcement (Walls)
label | b43c08b3-98da-570f-88bf-a9f05fe22df8 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | ac2851bb-78dd-5a39-8709-820194cf71a2 |  | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | edd705ab-e98f-5922-8673-fa15a7952bce |  | note | ○ Concrete pre-pour inspection complete.
label | 38c97513-7119-5238-8fc5-616938ea4e75 |  | note | HOLD POINT
label | b82dcc14-dcd0-5786-934b-3f6cc35041af |  | note | Before Placing Concrete
button | 0373189c-48f4-5e24-9117-118790011af8 |  | button | Acceptance | Yes,No,N/A
label | a3eca659-ee19-554e-8600-a994ad669372 |  | note | Key - H
label | 82727c24-d1f3-5b4f-911b-5dec7f62066f |  | note | UGL Key - H
label | 381037ff-ab3a-54b2-b2c5-430667d28b54 |  | note | SHL Key - H
label | 24d5219c-0b8e-5162-bf65-752116f6000a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 8ed255b2-47e8-549e-9166-95dbfdb50068 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Bell-mouths
label | 902aad4c-e6e8-58b0-8199-5894279e9d8b |  | note | Ref docs - Spec. 0002 General Electrical [Cl 6.11]
label | 51ecdaee-d064-542e-b2db-d18ab7bd14ee |  | note | Acceptance Criteria - All conduit entries are to be fitted with proprietary bell-mouths installed flush with the pit wall as per manufacturer specifications
button | d83c7939-261e-59ba-83a6-d03bf4a08aec |  | button | Acceptance | Yes,No,N/A
label | d5e915ea-3cd9-57c7-90fd-1dcd32dbc86b |  | note | Key - S
label | 737c614b-357c-5f49-90ab-d244f6803600 |  | note | UGL Key - S
label | fcbfea45-c8a4-5c6e-93b0-3d332856482b |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.73.6 - Concrete supply and placement
label | 92f885c5-8d59-53ac-9179-d4e6cbc4028a |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11], Drawings
label | e6d0f79e-e045-50fa-97cb-6ca502d56ca4 |  | note | Acceptance Criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
label | 21737322-578a-5e39-a6f7-ab4dd44f3dd6 |  | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | 5506dd69-acae-50cb-9195-bfcd74ce6da8 |  | note | – – – – – – – – – – – – – – – –
label | 046c587b-d233-5245-813c-5ae39082d32c |  | note | Concrete temp at discharge (°C) ¦¦ Max elapsed time (hours)
label | 57ca3ff4-0fbe-500e-bef6-5258eacc4f4e |  | note | 10-24 ¦¦ 2.00
label | 61d4e9ff-1740-597a-9e84-da68f88736ab |  | note | 24-27 ¦¦ 1.50
label | ad93ca03-34d7-5dc3-abef-cd3b4c136931 |  | note | 27-30 ¦¦ 1.00
label | 696cf7bd-2af7-52db-a748-363f468772a3 |  | note | 30-32 ¦¦ 0.75
label | f911c453-6407-578d-926a-0ac0690172f5 |  | note | – – – – – – – – – – – – – – – –
label | 8611d3e5-8c36-5899-b904-686bbb6996a9 |  | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
button | 076f6ad3-7bc4-597b-80c7-c8b026ece200 |  | button | Acceptance | Yes,No,N/A
label | 2b134cf6-0800-55ad-9a9c-bfd4a17c1f5c |  | note | Key - S
label | a092a379-0157-5586-a9f2-a74a2ba70139 |  | note | UGL Key - S
label | 01c9e696-8c5a-5215-ad15-0f88742ae22d |  | note | SHL Key - S
label | f25b4ac2-dfe0-55fc-8776-4a81eb25479b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 72564d24-566e-5675-b558-1ed48eae62db |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 3.7 - Concrete sampling
label | 10202c0c-8c69-5f65-b65d-8eb53e4dd210 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | 5ab7f1d9-0d79-5f67-98de-15ab947e21d0 |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
label | 690fcd52-4db7-58b7-8a98-f2236cd4a978 |  | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
label | 36e2162c-ab29-52aa-8855-f671a0707914 |  | note | (b) Slump: One per batch of concrete
button | 6ca33135-2747-5751-a956-e9d282cb2202 |  | button | Acceptance | Yes,No,N/A
label | cc27d0b6-2a6b-5463-b941-3a6438a9e589 |  | note | Key - S
label | db470424-fcec-593d-a6aa-9a73c5db8bfa |  | note | UGL Key - S
label | f9a63336-b513-5a54-9d12-c79260390e7e |  | note | SHL Key - S
label | 1a397a1c-751e-5e3d-be95-cb34a4214d60 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 4f819a2b-bf9d-52b2-8834-d918ab38718d |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 3.8 - Concrete testing
label | 50a1e29b-7501-5713-8808-d64e36cfdb79 |  | note | Ref docs - Drawings
label | 4beb37b8-51b4-53ad-80f5-bb56a58b4ab8 |  | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements. Slump within tolerances specified in AS 1379
label | d17f611f-313a-5e94-801a-a4f98dd0f46a |  | note | – – – – – – – – – – – – – – – –
label | 573a6566-0cf1-5ed3-aa55-ad132cdf2f00 |  | note | Table 5.1 PERMISSIBLE TOLERANCE ON SLUMP
label | c4a30649-8513-59c9-892b-1d510a102ccc |  | note | – – – – – – – – – – – – – – – –
label | 023a60f4-8e28-5707-a5ce-8d0fe55cdb38 |  | note | Specified Slump (mm) ¦¦ Tolerance (mm)
label | 399617e6-4f34-5c25-830b-b7f0e5810380 |  | note | – – – – – – – – – – – – – – – –
label | 120aa10c-2940-5773-b806-dbe523e44304 |  | note | <60 ¦¦ ± 10
label | aa88cf8f-9faf-5b60-8e82-f2bb050e85ba |  | note | ≥60 ≤80 ¦¦ ± 15
label | 1af050d3-9e45-5b66-9ee3-643aa3d14e34 |  | note | >80 ≤110 ¦¦ ± 20
label | 089472c1-7679-553c-a175-76335bdb2d3c |  | note | >110 ≤150 ¦¦ ± 30
label | 7e997f8a-4918-55fa-b461-cbf6b2b0206c |  | note | >150 ¦¦ ± 40
label | c177be6a-69bb-52a4-90f3-a7f59cca3aff |  | note | – – – – – – – – – – – – – – – –
label | 1705e6fc-58b6-57c0-b062-b6d90818748e |  | note | Testing to be in a NATA accredited test facility
button | 411fb446-af35-527a-afe5-fe5bd7c703bd |  | button | Acceptance | Yes,No,N/A
label | 8bc506cf-17d4-597b-a12f-397abab21c64 |  | note | Key - S
label | af12d071-fb57-5ee1-9763-e4d3f57d93f8 |  | note | UGL Key - S
label | a12eaff2-239b-594a-920a-c8be597a2b9a |  | note | SHL Key - S
label | a1284c01-c52f-5827-b310-5019cf581c57 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0cf96643-3fd8-5bb9-8e91-085ab9e18daa |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.9 - Curing
label | ab43d534-ae88-5630-8ff7-ba0e3e6271b2 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | d12c167f-6bd1-5f1e-8d30-d25657e26977 |  | note | Acceptance Criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention for a min period of 7 days or as directed by the Superintendent.
button | 9173e4e0-49eb-573f-b9d2-7aeee2079300 |  | button | Acceptance | Yes,No,N/A
label | 8c9a57d3-f846-5d87-b039-87be6f9cdf06 |  | note | Key - S
label | 7daf9624-6860-5fe6-8f82-3edf47efaa7f |  | note | UGL Key - S
label | e076b065-0822-5342-822f-ff29d4ba0587 |  | note | SHL Key - S
checkpoint-group |  |  | section | 4.0 Finishing Works and Backfilling
checkpoint-status |  |  | checkpoint | 4.1 - Pit Backfill
label | fa1febc7-9a2f-5509-95a9-14cec49c175a |  | note | Ref docs - Spec. 1354 Earthworks [Cl 3.7]
label | fa1b7ebd-05ed-5e68-ae21-2cae5f6b584a |  | note | Acceptance Criteria - Pits to be backfilled in 150mm thick layers for a horizontal distance of 300mm as per RFI-069
label | 61ac2f8f-a4c7-51f9-994e-b81c5c34915b |  | note | ○ Backfill to be with a thermally rated compacted sand as per the design drawings up until the top of the conduit bank. The remaining backfill above the conduits to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
label | 01771d15-3efe-50e0-a656-abd6b2f592f0 |  | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
label | c48e43e1-d79d-5be9-92d7-f030a841c8d8 |  | note | ○ Backfill shall not commence until concrete compressive strength reaches 15MPa unless approved otherwise by superintendent
label | a84110a4-565c-5217-b6eb-2867e49af437 |  | note | HOLD POINT
button | b9337800-fad9-526f-b06a-49b10d3dbe1c |  | button | Acceptance | Yes,No,N/A
label | ba4aaf2e-bf73-5b2c-875c-f96ba3bc990c |  | note | Key - H
label | 58564afc-0936-5fd6-a078-6f758ad98ca2 |  | note | UGL Key - W
label | dc563456-4e58-5abb-b673-b7310810781a |  | note | SHL Key - W
label | 780c23f1-94f1-5740-a483-8b5e1d6a9f9f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 2fd1d111-5e4f-5ea0-9168-f91513498c62 |  | tickbox | Material Test Report
checkpoint-status |  |  | checkpoint | 4.2 - Compaction - Backfill
label | 3512927a-4e77-5397-a926-9ab6fb4dc244 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.6], Spec. 1112 Earthworks [Cl 4.13]
label | 06c50918-5ce7-571d-b8eb-f4ed6228cdf0 |  | note | Acceptance Criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be:
label | d832aa35-1ad5-5948-9fb1-3a1200e12f6c |  | note | 95% for pit bedding and conduit embedment
label | dcb2149a-af43-52af-aef8-24c71299f905 |  | note | 97% for select fill areas
label | 94d9ccb6-0f00-5caa-b917-a025953119c0 |  | note | 92% for general fill areas
button | a0b9a39d-1d31-5a24-bc6b-2ebc48a3557a |  | button | Acceptance | Yes,No,N/A
label | 63fdab33-885c-57ba-83e7-9fe81360b9c0 |  | note | Key - S
label | 3dd66666-c478-5f2a-9772-e7b707bf5389 |  | note | UGL Key - S
label | 276d4a47-065c-52da-b405-7b4f5c3e8540 |  | note | SHL Key - S
label | 7391ae49-8916-545e-9a79-5bb11b91bfd7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 6f81194b-bc3f-5d12-86ad-f9fc40cfa891 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 4.3 - Access Covers & Grates
label | 783783d9-776d-55ac-b43b-1b36a2b5dab7 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | a629818f-13b1-5c36-a9d4-0cd17e59ddcd |  | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
button | ab5067da-461f-55b0-826f-c3e55e060290 |  | button | Acceptance | Yes,No,N/A
label | 6de30edc-81e2-552b-abaa-4fa66c3ab92b |  | note | Key - S
label | 5e769ff3-2ea2-5f32-9d19-ca0004a7fdb4 |  | note | UGL Key - S
label | 1d7d118e-8c7d-5d7a-a2b6-019e810d0ade |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.4 - Step Irons
label | 9fd07298-875c-50b6-86ff-a460018c4c75 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 8b9ea3e7-4cff-5415-b746-59760bdecee0 |  | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | d8d56b7b-d820-5ddb-83f0-7a309ff15788 |  | button | Acceptance | Yes,No,N/A
label | 03e5ca79-78b9-5f9d-b9fb-58566b024adc |  | note | Key - S
label | 6c682768-1737-532d-a9de-f937da8fd25a |  | note | UGL Key - S
label | 6bcf8eb1-91c9-5346-9e1b-3313804dbdc6 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.5 - Brass Marker Plates
label | 668b4488-81fa-509f-a751-dc87a28b22b8 |  | note | Ref docs - Spec. 0002 General Electrical Installation [Cl 6.11], Drawings
label | 3f279001-fa76-5719-9d8f-682bc4f0559a |  | note | Acceptance Criteria - Brass marker plates to be installed at each pit showing cable/conduit routes, contact phone number, organisation & drawing number.
button | 429f24d9-dae4-5dfb-8058-264ad855853a |  | button | Acceptance | Yes,No,N/A
label | f2ea165a-260f-521d-8dae-7cda2e062d34 |  | note | Key - S
label | e58b4623-46b8-51dd-a7f6-a742e08066e6 |  | note | UGL Key - S
label | 8ab3ff55-e733-5bbc-92e9-f6768c7e898c |  | note | SHL Key - S
checkpoint-group |  |  | section | 5.0 Conformance check
checkpoint-status |  |  | checkpoint | 5.1 - Survey Report
label | 3147cfdb-d122-56cc-b7bb-e610ab9a6fe1 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | 4c1650bb-82c4-53af-969b-8e0c8bc5a98f |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | 36fbe3a8-e5b9-5323-8cce-7695c4d795f4 |  | note | Plan: +/- 200mm
label | 0c1d05e5-646c-56dd-bd1e-b23190091340 |  | note | Level: +/- 20mm
label | a89dca7b-10f6-57a8-8e38-a65d5236f9b6 |  | note | HOLD POINT
button | ad8f20e4-3531-502d-a906-f1329f51dde0 |  | button | Acceptance | Yes,No,N/A
label | d9fdb5fe-9298-5ffb-a5b7-9e8fe794481f |  | note | Key - H
label | fa3c2b2e-f5e5-5dc6-8982-1ddc92122c4f |  | note | UGL Key - W
label | 9af37690-ea71-5f84-9da8-e553071c6ae4 |  | note | SHL Key - W
label | 41ddebdf-dac6-57c8-92ef-e1e5d911a993 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 5a64189f-2675-5ebf-a733-a5c51b1e8db4 |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | 67ef945c-95a3-5ec9-96d6-8e7fc42171cf |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 3f4829a6-6b10-5c67-bb1d-33c16b29a6d0 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | ea803b06-cf4b-5f2c-a221-20356cb49492 |  | note | HOLD POINT
button | 4026c9f6-3d80-5834-b3d1-8d0d363e57e6 |  | button | Acceptance | Yes,No,N/A
label | ad737eb9-523f-5e20-996f-182e76d095e9 |  | note | Key - H
label | 96b62041-3720-5841-870e-fcae89569f0c |  | note | UGL Key - H
label | 7feda0e6-9061-5112-b456-d749600766c5 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-011 Drainage (Cast In-situ Structures) Checklist - Rev.7 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-011 Drainage (Cast In-situ Structures) Checklist - Rev.7 | b326d542-6f60-47e1-b80a-8f936d22d315
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | b4330d9a-ff27-51fa-a9d7-b75d35fbcc6d |  | note | Ref docs - Issued drawings / Site copy drawings
label | fb2f14e1-b116-56c8-80f3-62abaa94459c |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | f3bebeb3-5632-5e0c-84d7-5408a7ce9c29 |  | button | Acceptance | Yes,No,N/A
label | 16f639fc-1cca-5b09-a352-d3f41c0c3781 |  | note | Key - S
label | 2181298b-95c1-5504-bd40-f99bb6c67440 |  | note | UGL Key - S
label | 56a4e974-1724-559a-a1ce-ea7c680f0b69 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | c021c42b-f697-505b-ae78-9b15b20d79d8 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | ced49139-ebc5-5554-bfac-3579fdedfd8e |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area
button | 2cc4bbc6-1973-56f4-8710-4f89b15dc6dc |  | button | Acceptance | Yes,No,N/A
label | dd5899c8-7b9a-5697-98eb-87352ca1013e |  | note | Key - S
label | 92a87bb9-7f15-54ba-9d54-48d27ee1b9fc |  | note | UGL Key - S
label | 0df97870-74e7-5bd2-9795-5fee64531441 |  | note | SHL Key - S
label | 09415c81-8375-5cec-8e05-9adaefb91b4e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 186440cb-101f-5b78-8096-4dc1065fde80 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Set out
label | 1decb66f-6e95-5c30-b94d-d71359983699 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2]
label | 2f49cf5d-fd34-5f4e-b8b2-b2d120bab394 |  | note | Acceptance Criteria - Setout pits to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | a60808a7-a9da-51f2-9907-abb5185525aa |  | button | Acceptance | Yes,No,N/A
label | e7e42383-97f5-53ec-8407-6038c439e209 |  | note | Key - S
label | 54c8e17f-7d7a-53fa-b045-eeaf4c21608b |  | note | UGL Key - S
label | e4f73d71-45fb-5aea-a111-5938d18014bc |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and bedding
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | 89fa53eb-a244-57df-af79-15e309075640 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | 3929a98d-3530-5847-a42e-20323434c0b1 |  | note | Acceptance Criteria - Excavate to the depth nominated on the drawings and remove any loose material at the base.
label | 6406d9ef-6732-5454-92df-874f0731e192 |  | note | ○ Ensure excavation is carried out to a width which will not impede external formwork.
button | f26b3de7-f505-5304-8d01-bee0bc636f55 |  | button | Acceptance | Yes,No,N/A
label | 16eb51a3-c3bf-5e06-86c2-8cea21050a2b |  | note | Key - S
label | 0d80c7f9-1983-5a17-bade-5cf537fec72e |  | note | UGL Key - S
label | d9d53534-5f67-53ca-9eea-2aa02b4224d8 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable Material
label | e8b21db5-e0a2-5021-b701-3346170c4075 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | 1ffc03e8-b80f-5622-915d-a00cbb21e229 |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | fe0b8ad8-2349-5c1d-a86a-4eafa0a515ff |  | note | HOLD POINT
button | ebff2412-5eb6-5514-94ea-5e6abf0faa6e |  | button | Acceptance | Yes,No,N/A
label | 6ff0bf35-6113-5c39-81ac-e9a5eba5e975 |  | note | Key - H
label | 30a057f7-b584-59bb-ab37-0dea51f62616 |  | note | UGL Key - H
label | c4274d5f-4798-597b-9dc8-9311df6e1072 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Compaction - Foundation
label | b8ab4afa-f945-5e40-90ef-e62700c8e0cf |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | 47fa45f8-5f2f-5310-bf01-a2d419fbe878 |  | note | Acceptance Criteria - Foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
button | b9ded0d5-4979-59e1-bbd3-88f07e0a1ae2 |  | button | Acceptance | Yes,No,N/A
label | b75e0453-bbec-5b4b-ba35-0339de4c071c |  | note | Key - S
label | 31266d5a-f90e-53ea-91c9-f49d3721e7f9 |  | note | UGL Key - S
label | f862ea4f-d501-5876-82eb-56ec74c6e482 |  | note | SHL Key - S
label | 048202a5-5d71-59a8-8110-5936131042f6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 38e79ea6-af4d-5422-ad11-f31cfc8a29ee |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Foundation Inspection
label | 1759df0a-7122-5d77-bc43-453efa6391fe |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
label | ddaaf121-b0be-5261-8aa5-742e321eecaf |  | note | Acceptance Criteria - Foundation to be inspected by the Superintendent prior to placing blinding
label | 50e0f992-0e0c-5328-a772-7adedaf29d64 |  | note | HOLD POINT
button | 3f70b98b-10b8-583a-8409-488e0f5c1f41 |  | button | Acceptance | Yes,No,N/A
label | 46a85f3a-ed83-507e-a99e-c9ab28a39b38 |  | note | Key - H
label | d7bbd712-8f8d-5670-bce5-1a25fe68fd95 |  | note | UGL Key - H
label | 8c96de65-3612-5c0b-848a-44c2c8dafe37 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Blinding
label | 190e2ea4-e804-5c7f-8375-4b2a59d38ec1 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.6]
label | 76bac32e-0a41-5d31-8ec9-9462f26e91bf |  | note | Acceptance Criteria - Blinding (15MPa) for Reinforced Concrete Bases to be a 50mm thick mass concrete layer.
label | 74b4f274-35b5-5b33-929f-dd366810ac4e |  | note | ○ Unreinforced bases can be poured directly on the earth
button | 729fd8d1-7e0c-565c-8f97-5291a85370ef |  | button | Acceptance | Yes,No,N/A
label | 46e1d911-ff84-54ae-ac64-7078705093bb |  | note | Key - S
label | 7bf97374-f12d-526e-8d06-8a3e3e991fe7 |  | note | UGL Key - S
label | 361974f4-e2b5-5773-ab47-c89d4856c281 |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Cast in-situ structures
checkpoint-status |  |  | checkpoint | 3.1 - Formwork (Base)
label | 093980e3-8aca-5639-b3cb-d0c4e46047ca |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
label | fa2644eb-4774-50b7-a8c4-176d86a39295 |  | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | 7ac211a5-3612-5d2b-a05f-d10c983a71ad |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement
label | b8930497-1ae7-5c15-872c-53346e47174a |  | note | HOLD POINT
label | 7b5ce84d-e00a-5ea5-b5bd-148088ef3b34 |  | note | Before Placing Concrete
button | 9480154c-77e6-5d7c-a6f4-08c2a9d82b71 |  | button | Acceptance | Yes,No,N/A
label | eb24de67-e03c-5dfd-b21c-51220e1f172a |  | note | Key - H
label | 1203b3b7-428f-59f9-be75-1a47e249541d |  | note | UGL Key - H
label | 7d0f4715-564a-5f8e-9bbe-f4f621a22bc2 |  | note | SHL Key - H
label | dd311c6b-0ca1-5157-b590-bb0c2c94a298 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 53604dd8-c58e-5459-864b-de1eca210a77 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Steel reinforcement (Base)
label | 7f6e2671-fd94-55dc-828b-e3541d8fd2f3 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | e0ef7b28-2670-5be0-aaf5-2eccf4289a6b |  | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | 3b9338c4-0933-5c94-b92d-ed6dc7a2e8fe |  | note | ○ Concrete pre-pour inspection complete.
label | ff757bf6-0c2b-5fcb-bfe5-aef8175ab80b |  | note | HOLD POINT
label | fba25cf8-1c8e-5d72-a025-8be1fde81c75 |  | note | Before Placing Concrete
button | 1e975776-47a1-5930-8a25-7c1d7f8ea801 |  | button | Acceptance | Yes,No,N/A
label | 2bceb529-e11b-5822-8365-2ba7fbad8e1d |  | note | Key - H
label | 5a8b6ec2-e08c-536d-9f37-ab457589ea4a |  | note | UGL Key - H
label | 2be77881-a1b3-5bd9-a2ea-a2fbcbadd940 |  | note | SHL Key - H
label | d75d420b-dcfe-5aba-9381-bce17a97d30c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d3b8d330-09a1-5553-985e-d7dbdd7c92cf |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Formwork (Walls)
label | 9fd7d194-7b7c-5027-b45a-3b0c022fe68d |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.3], Drawings
label | 6f914e52-7941-5904-838f-b7cdb3febeb7 |  | note | Acceptance Criteria - Formwork installed as per drawings and adequately supported.
label | 019292cc-f271-5111-bb7c-6bca9134ebaf |  | note | ○ Completed formwork to be inspected by the Superintendent prior to concrete placement.
label | 6e48350b-6911-54a4-9222-ed6a52865a2c |  | note | HOLD POINT
label | 241204f5-9b66-5819-b7a6-34389540adff |  | note | Before Placing Concrete
button | 018b8538-2c51-5b35-a7c1-319e91768139 |  | button | Acceptance | Yes,No,N/A
label | efc702fe-f193-5618-a8fc-0ae836983d0e |  | note | Key - H
label | 58955405-f3c3-56cc-bfe9-afbaafa1b19b |  | note | UGL Key - H
label | eeb03852-3864-5b7b-a9e2-a8ac2d530c2e |  | note | SHL Key - H
label | 3c1f85c7-1405-5595-b10e-e6aa204e6a8f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ed329e55-d0a8-5250-9134-af303766222b |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.4 - Steel reinforcement (Walls)
label | a69bba4f-3cfa-5de1-a582-58408f76c7ed |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.5], Drawings
label | 4e9f01df-0229-5d17-8027-a26f40cd8992 |  | note | Acceptance Criteria - Reinforcement installed as per drawings, ensuring sufficient lap length and cover is achieved on all bars.
label | 98a53fa3-9d41-5ac1-a286-8f424f485326 |  | note | ○ Concrete pre-pour inspection complete.
label | a2843d51-8582-5617-b8d9-5e1531e2bf07 |  | note | HOLD POINT
label | f007e801-350b-55ed-ad3e-612093ef56bb |  | note | Before Placing Concrete
button | 0e1560e6-b3cb-5669-b9c9-726c7dc40b56 |  | button | Acceptance | Yes,No,N/A
label | 6f56205f-e21d-5724-af3c-e636c834ceb1 |  | note | Key - H
label | 95c22c11-68e9-5de5-b79a-1f3565d74571 |  | note | UGL Key - H
label | 041ce3ea-e8e9-53af-b508-4b72681a73eb |  | note | SHL Key - H
label | 62ec69e1-db28-5c62-8dc3-651228116d7c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | b33fedaa-2846-55aa-b453-dfb7c77856b8 |  | tickbox | Pre-pour inspection
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - Pit & Pipe Connections
label | a6c2c8f7-d9fc-5c9c-97a5-c7fd7db85828 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 9733dc89-7f22-516d-9e1f-55dc15eecec6 |  | note | Acceptance Criteria - Inlet and outlet pipes to be integrally cast into pit walls and the joint waterproofed as per design requirements.
button | d65295d9-5e4b-5fab-8e8c-f4d1ce92a097 |  | button | Acceptance | Yes,No,N/A
label | 0c9012e0-e222-5e79-b5e9-8ba5955a5739 |  | note | Key - S
label | cbb8639e-cf49-545f-8224-629385f37e7f |  | note | UGL Key - S
label | d41749da-d81a-5bb8-b920-c915058bab12 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 3.6 - Concrete supply and placement
label | 20b97170-c23b-5bff-be64-99eaca04daa5 |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.8, 4.9, 4.10, 4.11], Drawings
label | 3d7e3bd6-e2e7-58ad-8b61-3f271c9c14d7 |  | note | Acceptance Criteria - Concrete strength of cast in-situ units shall be min. Grade N32 or as otherwise stated on drawings.
label | 23dccb60-9e71-5f85-a444-70c5406e4eff |  | note | ○ Ensure the temperature of freshly mixed concrete is maintained in between 5°C and 35°C. Ensure elapsed time between batching and discharge of the mix complies with the below table.
label | 0a09fcb8-90f9-5acf-8eb6-e5226d10c8a5 |  | note | – – – – – – – – – – – – – – – –
label | f5c7fbda-f46a-57a9-98e1-c436c63f8c81 |  | note | Concrete temperature at time of discharge (C) ¦¦ Maximum elapsed time (hours)
label | 3b0b15fa-91df-5e31-8c60-bb35b824defc |  | note | – – – – – – – – – – – – – – – –
label | 0e497f29-f9e0-561e-967e-3d4b6f11e22b |  | note | 10 - 24 ¦¦ 2.00
label | 8af4b7de-547e-5f2b-8ebc-1fa59118e1c8 |  | note | 24 - 27 ¦¦ 1.50
label | 42946e4b-1c8e-551f-ae1a-27e433228dc3 |  | note | 27 - 30 ¦¦ 1.00
label | a9d498cf-512f-5917-988f-b56b45eb5c56 |  | note | 30 - 32 ¦¦ 0.75
label | 89251d67-0168-5bc6-991a-bf5dda58e771 |  | note | – – – – – – – – – – – – – – – –
label | 95ec4718-644e-5bbb-85c0-0367ac0f9b86 |  | note | ○ Concrete placed in layers ≤ 300mm thick and adequately vibrated avoiding over-vibration.
label | 10677aef-c1e0-5be8-bbb1-61570b00d6bb |  | note | ○ Design slump shall not exceed 75mm unless shown otherwise on the drawings.
button | f15d3336-0b29-5d60-a4f3-5f0149e9bb8c |  | button | Acceptance | Yes,No,N/A
label | 9cec0849-aa4d-577f-9fbb-4b7a0ce5db55 |  | note | Key - S
label | e43bc7b1-2ab4-531a-8f44-ed6e14b1d5d7 |  | note | UGL Key - S
label | ced24efc-8061-5003-adc1-9c9d464777bc |  | note | SHL Key - S
label | 96aa044a-dfb0-5446-b050-746c82694f29 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d3c84e2e-a0b6-5cbf-9c5a-0c8bb9c308a0 |  | tickbox | Delivery dockets
checkpoint-status |  |  | checkpoint | 3.7 - Concrete sampling
label | 5542c73c-0673-5f3f-bab6-d1d9130c4bfc |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.2]
label | 174c2bde-5e8c-507b-95c6-a720c9149093 |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken:
label | 4ce67011-ab45-56fc-897f-d9affcb244bc |  | note | (a) Compressive strength: One set per pour or as otherwise directed by the Superintendent;
label | 70047186-d673-5951-8b38-46c7a8470f91 |  | note | (b) Slump: One per batch of concrete
button | 71b82711-57ff-5cb7-9093-a17b5ed0b75e |  | button | Acceptance | Yes,No,N/A
label | 9c381db3-94f7-5afa-9df6-c5aacbeb21c3 |  | note | Key - S
label | 8a3e7d52-4d6c-5f2e-9139-14a156273807 |  | note | UGL Key - S
label | 9abfe893-e5dc-571c-8b11-26082a5ef0c1 |  | note | SHL Key - S
label | e823a7ce-7e51-5c67-a863-44c57c9a189b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 4fc00cb8-d144-5031-892d-c8d3eee7f23a |  | tickbox | Concrete pour record
checkpoint-status |  |  | checkpoint | 3.8 - Concrete testing
label | 9f92fc6e-8557-5445-8a63-b45978907ada |  | note | Ref docs - Drawings
label | c3c75e51-6d4a-59ef-b140-802e1043ce1e |  | note | Acceptance Criteria - Average compressive strength at 28 days meets minimum design requirements
label | 556a7ad4-e4ac-59ed-9474-01da93ad631a |  | note | ○ Slump within tolerances specified in AS 1379
label | d52aa0ba-bb9e-528a-b6d2-66f40c0ef22c |  | note | – – – – – – – – – – – – – – – –
label | c75e816b-a45d-5cc3-8308-201c56ce4a37 |  | note | Table 5.1 Permissible Tolerance on Slump
label | fee8faea-4d56-5dd4-8f08-1833dccd96b9 |  | note | – – – – – – – – – – – – – – – –
label | ed24ec92-cbfb-5a96-ac47-92273d4173d6 |  | note | Specified slump, mm ¦¦ Tolerance, mm
label | 995038dd-1e27-5c6f-aa3e-14415e611384 |  | note | – – – – – – – – – – – – – – – –
label | c2627da9-7bdb-56b9-a010-2c7f4e504b84 |  | note | <60 ¦¦ ±10
label | d6a45446-9278-52c9-8d1a-12b156273694 |  | note | ≥60 ≤80 ¦¦ ±15
label | 469a25c6-e38a-59ed-8b3b-364055f31d8e |  | note | >80 ≤110 ¦¦ ±20
label | f21cac15-9c4e-5a0a-97a0-fa03e80fa3bc |  | note | >110 ≤150 ¦¦ ±30
label | 3e303904-dc47-52d3-952e-15fa1fcdd340 |  | note | >150 ¦¦ ±40
label | 0a6ae6cb-af28-5424-bb46-2cf03cf96d2f |  | note | – – – – – – – – – – – – – – – –
label | 5f6333fa-6bca-5584-8fc6-08075abb7ade |  | note | Testing to be in a NATA accredited test facility
button | 85406c4d-5c2e-5f8c-a061-d9a51bce02c4 |  | button | Acceptance | Yes,No,N/A
label | 50e43d65-3dc0-52f3-b146-d0e0cec540d1 |  | note | Key - S
label | 4eb768d0-e345-5045-ac36-bc791b7323b7 |  | note | UGL Key - S
label | 824d560e-b8eb-591c-bdb4-1436544711c8 |  | note | SHL Key - S
label | 1d1e4a96-5aaf-5f5c-b94d-69aea1805488 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ab262bb9-077d-5f19-97ba-5f477c83ed00 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.9 - Curing
label | 5d9662ea-2557-5ad3-9516-2bffabb7be7d |  | note | Ref docs - Spec. 0319 Minor Concrete Works [Cl 4.13]
label | 264e1d72-aafc-5258-a148-d68fb25dc5ae |  | note | Acceptance Criteria - From completion of finishing; cure continuously with either curing compound, wet curing or form retention until 15MPa is achieved unless directed otherwise by the superintendent
button | 5aea7650-c74b-5977-8d64-90514908d8f1 |  | button | Acceptance | Yes,No,N/A
label | 823a2eaf-e6ed-5509-95a8-a21491a16af1 |  | note | Key - S
label | c1ada7b0-11ac-5892-9ba2-6ca4cbfcc96a |  | note | UGL Key - S
label | 8ba04dd6-6e78-5806-a327-815f5a1df95f |  | note | SHL Key - S
checkpoint-group |  |  | section | 4.0 Finishing Works and Backfilling
checkpoint-status |  |  | checkpoint | 4.1 - Access Covers & Grates
label | 95107d71-1af9-5771-9628-75bda02f346d |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 43e7f39f-4d73-5dd8-a439-04a0aa5d5fc7 |  | note | Acceptance Criteria - Access covers, grates and frames to be installed as per AS 3996
button | edc53d99-f050-5b07-a0db-136055f74cc0 |  | button | Acceptance | Yes,No,N/A
label | de041491-a40e-5407-b2a4-576a31f7194c |  | note | Key - S
label | c1f9dd1f-9ed2-5264-94f4-a8f19e6a45be |  | note | UGL Key - S
label | 29746b71-6afa-546c-8e80-de74539456ff |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.2 - Step Irons
label | bad9168f-d24c-5c30-8a62-d16213bab03a |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.3]
label | 0dd72312-1b86-5dfc-bf50-6da3e37f3ac9 |  | note | Acceptance Criteria - Pits deeper than 600 to be fitted with galvanised plastic-coated step irons as per AS1657
button | 203f4056-ea64-5169-8704-35c8c5dccfcf |  | button | Acceptance | Yes,No,N/A
label | 44b0bbb9-ab8d-55e3-ba51-6780ef1012ab |  | note | Key - S
label | 1436d06d-f4bc-5471-95ff-cacccb58d607 |  | note | UGL Key - S
label | a3f0e69c-4a3e-50a6-b958-6c274f4fb0f4 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.3 - Pit Jointing
label | 24cda578-c261-5e56-8524-7fcb53a24f54 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.5]
label | fef0333d-01cc-52c7-bca5-ca497aefaa38 |  | note | Acceptance Criteria - Provide a 10mm isolation joint in between precast pits and any abutting concrete pavement, kerb and gutter or concrete structure
button | 5cb40e18-9a6b-57cd-b722-25d0c5188a33 |  | button | Acceptance | Yes,No,N/A
label | d64da8ee-d627-5601-a5b5-205b86f757b3 |  | note | Key - S
label | b1ad3c7c-3839-5a63-a50e-78bf9edf8dac |  | note | UGL Key - S
label | bb6c829d-bfc5-571e-9713-31c1846f00b9 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 4.4 - Structure Backfill
label | 3a6e3816-4287-551d-b34b-6d174f0d6be6 |  | note | Ref docs - Spec. 1354 Stormwater Drainage Structures [Cl 3.7], Spec. 1112 Earthworks [Cl 4.10]
label | 7f380d8b-05d6-5e12-86e4-64f6e681d59b |  | note | Acceptance Criteria - Backfill shall not commence until the compressive strength of concrete has reached at least 15MPa unless otherwise approved by the superintendent. (Wingwalls shall have no backfill placed until 21 days after casting)
label | aa1556af-84de-5400-ac98-0e9f68eb8778 |  | note | ○ Drainage Structures to be backfilled in 150mm thick layers for a horizontal distance of one third of the height of the structure.
label | e40f3368-61e8-5657-9f99-8d601ea44f27 |  | note | ○ Backfill to be Select fill for material within 1.5m of pavement and General Fill below 1.5m deep.
label | f8e12239-6fe9-5b32-9d41-cf7a503acbbe |  | note | ○ Select backfill material to be a granular material with a maximum particle size of 50mm and a PI between 2 & 12
label | bfa3490d-e06c-591b-b59c-328dd558dce9 |  | note | HOLD POINT
button | 1c34ef61-cd78-5398-a878-f9673e39581a |  | button | Acceptance | Yes,No,N/A
label | 94c75314-0573-57ee-a5b3-290bf398365f |  | note | Key - H
label | 2c7e0805-1580-5a3f-8ee6-cda2f878f85b |  | note | UGL Key - W
label | 4d2a3294-4f90-5873-a117-2c32cdc61c74 |  | note | SHL Key - W
label | 31b49d18-57dc-5a4e-ae19-01bf648423e5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | fd6d79ad-f40b-5bf2-8955-b503b10a092e |  | tickbox | Material Test Report
checkpoint-status |  |  | checkpoint | 4.5 - Compaction - Backfill
label | de322539-cabd-557e-9fd8-6af02f8d422e |  | note | Ref docs - Spec. 1112 Earthworks [Cl 4.13]
label | 746b90f4-6909-52f3-a4af-ed4c559f39a2 |  | note | Acceptance Criteria - Minimum relative compaction requirements for backfill against pits to be:
label | 495e6f81-18a3-5412-88e1-6c6826025917 |  | note | – 92% for general fill
label | b9710709-0ca6-5ea8-9563-b379738a8c8d |  | note | – 97% for select fill
button | 251530df-31be-52a5-ae8b-f38c2b02a005 |  | button | Acceptance | Yes,No,N/A
label | 93ba04db-2825-535b-83f3-c324be664c48 |  | note | Key - S
label | 5c84ab42-265c-5826-9c5c-cda2bf84066d |  | note | UGL Key - S
label | 62062831-be4b-543c-a522-9fa77b045271 |  | note | SHL Key - S
label | 7d692315-73e2-5abf-b5e7-8edaacbc100d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 746d608c-fedb-5b2e-93cb-165424a7dcad |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 4.6 - Moisture Content
label | e1e24c70-6d47-5ccc-8c0a-b9e61fdee3d1 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 319b3ca8-2a43-562a-9942-7ad3a0416283 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | 72d7cbdd-a995-507c-bab2-66e6321dd81b |  | button | Acceptance | Yes,No,N/A
label | 11795a05-a4a9-5ebd-bfe7-c02db0e9501c |  | note | Key - S
label | 3992fc76-e1b1-569a-809d-bba5e5e59a43 |  | note | UGL Key - S
label | 570e010a-ba66-5857-a5e4-e6e56796c8c2 |  | note | SHL Key - S
label | 27de1742-9905-515d-bf54-90ce934e3a92 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 3ef99f4f-07ba-55e7-9551-6062e595752c |  | tickbox | Test reports
checkpoint-group |  |  | section | 5.0 Conformance check
checkpoint-status |  |  | checkpoint | 5.1 - Survey Report
label | b0b462e6-7c91-5cc6-9910-7ad02d837183 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | 7a2cf670-e172-522e-bc95-82da5f236f2f |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | f94305a3-651c-5db7-9270-6e26e18ccd3f |  | note | Plan: +/- 200mm
label | cd6d3568-0c7a-52c7-bbfe-4c6e1c056914 |  | note | Level: +/- 20mm
label | bfe84377-67aa-5c5e-89dd-691815f4ab40 |  | note | HOLD POINT
button | 17c0f20f-8894-5a8b-a4aa-f862fde4a8d3 |  | button | Acceptance | Yes,No,N/A
label | b85bcd9e-5e68-50fa-89ee-b564b9c3caca |  | note | Key - H
label | 9742ac72-7e3d-5b8b-b4b2-a89b3082674c |  | note | UGL Key - W
label | 4671c790-2dc8-5085-801c-2b4692611e02 |  | note | SHL Key - W
label | 444bec38-97aa-570d-ae06-538e56227a62 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0f7fe90d-cd86-57bd-ba2d-8c56e7396e39 |  | tickbox | Survey report
checkpoint-status |  |  | checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | c65f1a4f-4561-5997-8a70-64b4be41718d |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 65f8bc45-f375-553d-ae9c-f64ef7a57f25 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | 99b27de5-e7c3-58b1-b5b9-5458392645aa |  | note | HOLD POINT
button | b3e091ac-d9c7-5a68-8663-54fd29cbdb95 |  | button | Acceptance | Yes,No,N/A
label | 30a86b2d-3e8e-5d9b-aafe-2dc6b3f09d03 |  | note | Key - H
label | 2f1ceb4f-2931-5b74-8e1c-b839683278f3 |  | note | UGL Key - H
label | 509b911a-7a2e-5c93-ae97-d5eab0c9c43d |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-005 Trade Waste (Pipe Laying) & Checklist - Rev.6 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-005 Trade Waste (Pipe Laying) & Checklist - Rev.6 | d733d7bf-8d5b-4f9b-beb7-dad07f97e591
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 61facac9-e3dc-5b4c-9155-100c10f3f3fd |  | note | Ref docs - Issued drawings / Site copy drawings
label | 35b272ff-64b1-5b53-9dd3-15a81efb97eb |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | a1479f5a-ce6c-5c2f-86ea-5991e3e46757 |  | button | Acceptance | Yes,No,N/A
label | bcaca99b-a26a-5af8-8b3e-dd61219aacc8 |  | note | Key - S
label | 124ef8ff-d241-5f2f-b59f-703b1f9e7d70 |  | note | UGL Key - S
label | a8a2ee59-c0c4-52c5-ae09-76c5dd0670c1 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Lot Traceability
label | 16982c54-3040-573c-9e97-0e2d74b92314 |  | note | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | 10151db4-d628-579a-98a0-744232c1739b |  | note | Acceptance Criteria - Prepare a lot map for traceability of the work area.
button | 8ef016d9-4e99-511d-ad47-77e230b4af94 |  | button | Acceptance | Yes,No,N/A
label | e9347d70-f21f-569e-a536-78393d5b943e |  | note | Key - S
label | 1a5e639d-3167-54ef-8bb5-27ea027e4960 |  | note | UGL Key - S
label | 7939ec0a-e366-53bc-b9c0-e0de98ac3543 |  | note | SHL Key - S
label | 492ba1e5-ba76-579b-bc1f-e5fbc9e72264 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | eabac4e8-3d7d-58a7-abac-6178d39d4121 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Drainage Pipe Material
label | 3628a0d4-a4b3-5bfa-a780-cac22db7c83b |  | note | Ref docs - Drawings
label | f7e7f162-22ed-5004-a5a0-1b1a1febf1fc |  | note | Acceptance Criteria - Has the correct class & type of drainage structure been supplied and free of defects?
button | 513d2c68-91c5-5563-9004-decb6a3533a7 |  | button | Acceptance | Yes,No,N/A
label | fa500248-eacd-577d-9cfc-60f387573cdc |  | note | Key - S
label | 24f75e1b-a9a7-5a94-b23d-49afaf7053ea |  | note | UGL Key - S
label | 286d914d-271d-5888-8e26-d2ec638f515d |  | note | SHL Key - S
label | f227a9f2-0e60-53d6-b3c4-4a464fcbdc52 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 7e40a5d0-a454-59e8-acdf-3f8c7901be06 |  | tickbox | Material conformance certificate
checkpoint-status |  |  | checkpoint | 1.4 - Embedment material
label | a330ad52-9747-51a8-aa9d-a7e395a5a864 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1]
label | 1b711836-42b5-5b7a-bc70-022a42af65ec |  | note | Acceptance Criteria - Material has plasticity index less than 6.
label | 0ec9f40c-c411-5f13-befb-c286fdc3bbab |  | note | – – – – – – – – – – – – – – – –
label | c2a7ec02-989e-57a9-89c4-8e88156835f1 |  | note | Table 5.1 Embedment material grading
label | 30d5622c-53f9-59f6-8848-56de2a4e2156 |  | note | – – – – – – – – – – – – – – – –
label | 041ad20c-d80f-5e36-87b1-290e9b81e12c |  | note | Sieve size (mm) ¦¦ Weight passing (%)
label | e2aa3b40-f6f5-54d1-9726-da9bc7feec14 |  | note | – – – – – – – – – – – – – – – –
label | 0c10928e-a0c0-5b2c-84b4-694ccb312fce |  | note | 19.0 ¦¦ 100
label | e1efc8c9-01f8-5e84-866f-b82115ddc2ee |  | note | 2.36 ¦¦ 50-100
label | d083f9c0-7c0d-51e9-9276-e0f7ed9e02c4 |  | note | 0.6 ¦¦ 20-90
label | a9276b93-6ae2-5a87-9c22-6267916daa85 |  | note | 0.3 ¦¦ 10-60
label | 63167605-c8de-5700-b97e-2b3678f23ed1 |  | note | 0.15 ¦¦ 0-25
label | 58c3a3f8-0a3a-5156-b318-2fb09e0bbcb4 |  | note | 0.075 ¦¦ 0-10
label | 4ab8ce50-9686-5473-97b7-53748951c426 |  | note | (Table taken from AS/NZS 2566.2, Table 5.5)
label | 7cce10e1-a990-5f7a-a865-b92b16c8a661 |  | note | – – – – – – – – – – – – – – – –
button | 586ab23e-1335-5e03-ba53-d6b7b85b0209 |  | button | Acceptance | Yes,No,N/A
label | f99a20eb-8090-5fa2-b959-a6eb7e4e9e9d |  | note | Key - S
label | 0d833831-2575-55b4-b851-0fd62d95064f |  | note | UGL Key - S
label | a4591bf2-b135-57ca-8087-8432dbcd9b46 |  | note | SHL Key - S
label | 8f81dfc8-6404-5503-bceb-f8145e8ac6b1 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e76e7139-1b23-5b40-8ad5-547baa4a5e20 |  | tickbox | Delivery dockets
boolean | 1d7edbd3-1660-5c50-9523-f7284067818c |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 1.5 - Underlying Lot Conformance
label | 48458496-dc29-55a0-b321-d9b3c0541c12 |  | note | Ref docs - Underlying Lot ITP
label | 9b157007-af1c-5fce-890f-8df0a0843689 |  | note | Acceptance Criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | 2b5b25a7-df96-58d2-a3c7-a4a29524b644 |  | note | ○ Refer underlying lot ITP(s)
button | 2a5384b5-aea9-5711-905e-b2cb25805fc9 |  | button | Acceptance | Yes,No,N/A
label | 4c1de4be-911b-5e06-948a-b2bb3f80a84c |  | note | Key - S
label | 83de4c13-ee74-5fb3-915a-8a3030d47f7c |  | note | UGL Key - S
label | eab8133a-1d74-5035-9b1b-39a50c67c749 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.6 - Temp. drainage during construction
label | 50d54d77-aa53-5edf-be30-2841f9ee5122 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.1]
label | fd0effa3-5b6e-53cb-beeb-b7be2f1dbb50 |  | note | Acceptance Criteria - Adequate provision for runoff flows at drainage works under construction implemented and in good repair.
button | a0acbacc-2eff-5b1b-98c5-aa2cd53c2335 |  | button | Acceptance | Yes,No,N/A
label | ddc39fcc-09ec-5ecb-a9d0-ef0a9d96a1f3 |  | note | Key - S
label | 0237c8eb-63dc-5bbd-a3e3-77c4968e096f |  | note | UGL Key - S
label | 85ec4ea7-8370-597a-9768-104e26f6b00d |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 1.7 - Set out
label | e476485e-5e5b-5cf1-9374-d8b19fae90ae |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.2], Drawings
label | 905cfc32-f23b-55d0-bba2-7e2ce12d0c34 |  | note | Acceptance Criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | c9e0d9cd-efd7-54d4-94bb-13070a469a63 |  | button | Acceptance | Yes,No,N/A
label | 6fb78b81-f365-523d-bf46-a6a5c608d1b8 |  | note | Key - S
label | 73e28545-fd47-5e20-8a53-2c466000dc3d |  | note | UGL Key - S
label | 7bb631eb-2386-5e17-9eca-268046ef55aa |  | note | SHL Key - S
checkpoint-group |  |  | section | 2.0 Excavation and Pipe Laying
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | 878dec8a-9762-50ba-a671-d2ea2bf1a8bd |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
label | 7051af7e-6be8-534e-9339-49ef18db683f |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 91097225-e32e-5ba0-851d-a8c8c8eda2b5 |  | note | – – – – – – – – – – – – – – – –
label | af0ea196-c850-57f0-8857-18ea8e41e466 |  | note | Table 5.2 Trench and embedment dimensions
label | 3386acac-99b1-5bba-8be5-9f3669966f9a |  | note | – – – – – – – – – – – – – – – –
label | a6de63b7-b14c-5abe-8364-efbee72e6869 |  | note | Extreme external ¦¦ Minimum dimensions (mm)
label | a80e6273-e75f-57d9-8640-dbcf639ad46f |  | note | Dia (De)mm ¦¦ x : s : o : y
label | 0d9e9d9c-cc6a-5691-a219-774b0994c611 |  | note | – – – – – – – – – – – – – – – –
label | f2263322-f663-5136-84fc-34cbc24800c8 |  | note | ≥ 75 ≤ 150 ¦¦ 75 : 100 : 100 : Pipe dia.
label | 5d19b4d1-f514-5fb8-80d5-441abdfdfc2f |  | note | > 150 ≤ 300 ¦¦ 100 : 150 : 150 : Pipe dia.
label | 671938ff-95df-5559-8fc2-f4ad9e33d106 |  | note | > 300 ≤ 450 ¦¦ 100 : 150 : 150 : Pipe dia.
label | e5ee3bc1-0512-560d-8b19-4871b1733323 |  | note | > 450 ≤ 900 ¦¦ 150 : 300 : 150 : Pipe dia.
label | 9f676a0b-f371-5da4-9671-abd75f6b94b6 |  | note | > 900 ≤ 1500 ¦¦ 150 : 350 : 200 : Pipe dia.
label | e87a978a-ea49-5ba3-87af-cac9e5375df5 |  | note | – – – – – – – – – – – – – – – –
button | 4426939d-7031-59e3-856c-857d29e6fa5a |  | button | Acceptance | Yes,No,N/A
label | ebdabf2e-2e8d-5d16-8475-b578971eacbc |  | note | Key - S
label | f12cbfb9-8c11-5ef7-983d-ad20490367f7 |  | note | UGL Key - S
label | eefe3761-37c6-5a30-853d-7b73b33486d6 |  | note | SHL Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Unsuitable Material
label | 3feb7b30-3194-5f10-8f08-c800813cb412 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.3]
label | 3503c098-e841-51e9-96d2-738eaa876214 |  | note | Acceptance Criteria - Any Unsuitable Material to be removed to the depth as directed by the Superintendent
label | bbb5c848-dffc-584f-87e2-ec5f4d41ddcc |  | note | Notice: Prior to Placing Bedding
label | 300e46e5-faac-5707-bcd8-86c2631bcf8a |  | note | HOLD POINT
button | a9d55456-16c8-583f-81bb-61263ba7b7ba |  | button | Acceptance | Yes,No,N/A
label | 48a4a65e-ac65-5336-9b45-c9485dc9f7a4 |  | note | Key - H
label | dbea6244-aaaa-5d90-bc95-8052e7babd54 |  | note | UGL Key - H
label | 4f86f875-5e12-5a9e-bfff-af2e2fffb6e7 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Compaction – Foundation
label | 5f709cea-f991-547b-aad8-839f7756ffc4 |  | note | Ref docs - Spec. 1351 Stormwater Drainage [Cl 2.5]
label | 0211d37f-17be-530f-b663-2b2dda4efa71 |  | note | Acceptance Criteria - Trench foundation (including any unsuitable replacement) to be compacted to a relative compaction of 95% to a depth of 150mm below foundation level
button | 0b8d2ab0-95f3-5c97-8fdd-1dab451f0245 |  | button | Acceptance | Yes,No,N/A
label | 0c6e9c54-91f9-5e9a-9cad-0a402f9bece9 |  | note | Key - S
label | d39b00aa-0f6b-5e95-9104-6fcbf2dffc4d |  | note | UGL Key - S
label | fe6010ea-e543-5209-a179-c3f640841b53 |  | note | SHL Key - S
label | f4d6198d-a74e-53c0-bdd8-c5456dba9c89 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d1a1ec00-8c3e-557c-bf0a-fb2952b8f423 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.4 - Compaction – Embedment material
label | 6e01f189-2cb3-513a-b9da-4ce878e6f3cc |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | f6ee1d6c-7498-5397-8cb7-9200757b9b44 |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 02569b82-4749-5eb0-9888-988d3dd34a8e |  | note | Bedding:
label | 1bd41751-d66e-53c1-bf7e-cec57b0ae24b |  | note | ○ Required relative compaction in the bedding zone shall be 95% (AS 1289.5.4.1 Standard Compaction)
label | 0e193389-72b6-5640-949a-c065cf68fe37 |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 2fb664cc-9058-5de0-9453-32688f43b2fd |  | button | Acceptance | Yes,No,N/A
label | e9037cfa-2b79-5154-a028-d735b43f6b4e |  | note | Key - S
label | d877f2a2-059f-502b-a3bb-efdc119c3c6b |  | note | UGL Key - S
label | 914c5a50-3dd5-5585-97da-a47f375d9572 |  | note | SHL Key - S
label | 485fd6eb-0fa3-548e-a617-2c3cec2f0a5e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d7479dc3-999a-5dd0-b370-5934527ad6d8 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 2.5 - Pipe Laying
label | 14a50dbd-5377-5007-83ed-0faff49e4254 |  | note | Ref docs - Drawings, Manufacturer Specifications
label | 2b99f398-74e0-567b-857f-2883cf27d416 |  | note | Acceptance Criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
label | 35ce6004-c936-5758-89eb-623b6bd4ccf8 |  | note | HOLD POINT
button | 9a3f0f0e-c257-5d43-b2c0-2fec169fc723 |  | button | Acceptance | Yes,No,N/A
label | 6b68db4e-0df1-56ae-801f-53b597e4a2d3 |  | note | Key - H
label | b8523d44-e022-5bd7-986d-b1b57b0be489 |  | note | UGL Key - W
label | 46a53c0d-b9f0-5285-a6ca-2cf58167cad3 |  | note | SHL Key - W
checkpoint-status |  |  | checkpoint | 2.6 - Pipe joints
label | c2efa52e-6d45-56b6-9830-10c0293552ba |  | note | Ref docs - Manufacturer Specifications
label | 5c193d32-b816-51d3-8bd2-c51eca023eed |  | note | Acceptance Criteria - Pipe joints installed as per drawings and manufacturers specifications
button | 24e5f5d2-ee90-5bd5-ba5f-ebb6bc8d9734 |  | button | Acceptance | Yes,No,N/A
label | 14e20436-1db1-539d-886a-fbf8ac828991 |  | note | Key - S
label | 9d6754fb-7098-5aeb-9f8d-d2e62ff647d9 |  | note | UGL Key - S
label | 8ed63abb-b341-59d6-81a7-15b0fdef05f6 |  | note | SHL Key - S
checkpoint-group |  |  | section | 3.0 Filling and Compaction
checkpoint-status |  |  | checkpoint | 3.1 - Compaction – Embedment material
label | 1543b433-cdc6-5a80-bb28-974077570148 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.4]
label | 4aa9dbea-e5bb-5522-8651-f728b67877f3 |  | note | Acceptance Criteria - DICL and Plastic Pipe:
label | 872208a1-9712-5ceb-9ec6-8bf4ae2cdf37 |  | note | Side and Overlay:
label | 05a1e4c7-6aae-58ac-84ae-74b5fec5dd35 |  | note | Required relative compaction in the side and overlay zone shall be 70% for trafficable areas and 60% for non-trafficable areas (AS 1289.5.4.1 Standard Compaction)
label | 128248b0-595d-5cae-b491-b99608df2df2 |  | note | – – – – – – – – – – – – – – – –
label | 5fde0226-d1fb-5771-bbf8-5463cb54a8c0 |  | note | Table 5.3 Minimum relative compaction
label | 0e830e34-310c-5d1e-b65c-37d38414c1da |  | note | – – – – – – – – – – – – – – – –
label | 1b30095c-702f-5521-904d-a5b920929962 |  | note | Embedment material ¦¦ Test method ¦¦ Compaction - Traffic loading :: No traffic loading
label | bbbbc9d5-a1a0-5d08-8d40-6582a771ddff |  | note | – – – – – – – – – – – – – – – –
label | efb0d61a-f515-5be4-9f3c-e30e0063e52e |  | note | Cohesionless ¦¦ Density index (AS 1289) ¦¦ 70% :: 60%
label | 227990aa-2a80-5c73-b0ad-de8b94c98a68 |  | note | – – – – – – – – – – – – – – – –
label | 622f93fb-237a-5345-9510-f3c53a596de5 |  | note | Layers not to exceed 150mm compacted thickness.
button | 063a1f7e-a886-5394-9f80-3ca407631528 |  | button | Acceptance | Yes,No,N/A
label | fb1d0930-b97c-5813-8924-27830e0d08f8 |  | note | Key - S
label | c9a9ceaa-2a9a-5ff0-bbe7-bf4b7d6a773e |  | note | UGL Key - S
label | cc7f66c1-1277-5f9d-8755-3fb51315d63b |  | note | SHL Key - S
label | 7969f9da-4abd-59c6-9e79-061bb2b007f5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | c7699a8f-41ad-5b1c-a371-441c85a5afdf |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.2 - Compaction – General Fill
label | d1a2553c-d7f4-5afe-920e-08c9f9c495d6 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 12b41f59-469b-5813-bb23-27bd08d2508d |  | note | Acceptance Criteria - For sections of the trench above the overlay zone; backfill with general fill if in verges, medians or greater than 1.5m from top of pavement.
label | 5630da14-a461-5584-9399-b6b5c585e5c2 |  | note | ○ Minimum relative compaction to be 92%
button | f6b285ea-1852-5dd3-a7f9-9efc5bf1fd56 |  | button | Acceptance | Yes,No,N/A
label | 4346bbec-56f8-52fa-bd27-7e73c7fc14f6 |  | note | Key - S
label | 4d7f54f7-b879-5446-aa68-8d5d3078250c |  | note | UGL Key - S
label | 64dfc4a9-f428-58aa-a97d-2683efd21ab5 |  | note | SHL Key - S
label | ec8a7189-a423-531a-8d70-1d8ac5a52380 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 8d1d212e-9f2b-5c4c-b27a-852e7c40e884 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.3 - Compaction – Select Fill
label | fe9c7797-6ca5-5a4a-a96f-283d3a36da77 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 5c69ce6b-9ead-5c79-a22e-4d6c78c3bc84 |  | note | Acceptance Criteria - For sections of the trench above the overlay zone and within 1.5m of top of pavement; backfill with Select fill.
label | f486a7e4-e4c4-5d54-8ef9-e259d12bc487 |  | note | ○ Minimum relative compaction to be 97%
label | c12c466b-aa47-5567-84f2-50c61ea51679 |  | note | ○ Layers not to exceed 150mm compacted thickness.
button | 3bdf3481-cece-5310-9ca7-0363a74f71a6 |  | button | Acceptance | Yes,No,N/A
label | 69188c1e-8b74-52bf-9da9-ee25f969b255 |  | note | Key - S
label | 3360d85e-afdd-53e2-9c29-7173be0e83e3 |  | note | UGL Key - S
label | a4e67042-88ef-5d5f-9ef5-265f8ca6b7bd |  | note | SHL Key - S
label | b073d468-c1f8-52e8-a3f6-196faa31bc52 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 69427aea-90ca-5ee5-a1ed-1a4ffe4edb85 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.4 - Moisture Content
label | 46a7962a-f3da-5e0e-a90f-dc7fbebcf440 |  | note | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.4]
label | 0049f6b7-3338-5f77-88e4-d5eed2954950 |  | note | Acceptance Criteria - Moisture Content for Backfill material to be within 60% to 95% OMC unless otherwise approved by Superintendent
button | 39d9d994-e63c-5e32-8720-3ee754646991 |  | button | Acceptance | Yes,No,N/A
label | 2a132d63-09ba-50d0-aaff-158afe4cf08f |  | note | Key - S
label | 48f4013a-904f-58ec-8ed0-e01fa08031f1 |  | note | UGL Key - S
label | ea7f8406-e09d-5db8-a4f4-6e0b20b09ae0 |  | note | SHL Key - S
label | 76b18279-7721-58be-9093-8301375fc6a7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | a2f4fa73-6b27-5b28-be61-fae6acadb903 |  | tickbox | Test reports
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Survey Report
label | 7565097b-e223-58c2-a4db-035f37f1be4d |  | note | Ref docs - Spec. 0161 Quality [Cl 3.13], RFI-026
label | fe739ef8-83ae-56f7-ac78-520500f9c92a |  | note | Acceptance Criteria - An as-built survey of the drainage system been completed to ensure all structures are within construction tolerances.
label | ad92ce90-6548-5609-a6f0-3bc55ba0670f |  | note | Plan: +/- 200mm
label | cbc991eb-3b12-5558-b209-256d43052627 |  | note | Level: +/- 20mm
label | 4f2394a1-b6e9-52c8-94fa-6a360a5b62eb |  | note | HOLD POINT
button | 7db28fcd-3abc-534d-acf8-76c86bb0c1d5 |  | button | Acceptance | Yes,No,N/A
label | d6500556-6d7e-5b2d-84d1-606445311462 |  | note | Key - H
label | e4c78f02-95ce-5084-8924-60912e7fc580 |  | note | UGL Key - W
label | 3bb1894d-014e-5034-a71a-7a57d1c8c401 |  | note | SHL Key - W
label | 8b608ebf-3628-5fc8-bd0d-33d8f5a7ce63 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 30abe145-f226-564f-80f0-65ecef61a06c |  | tickbox | Survey Report
checkpoint-status |  |  | checkpoint | 4.2 - Acceptance and closure of non-conforming items
label | 61245c85-96aa-5499-9f8a-b8ed234fc910 |  | note | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | 14dcb91f-370b-530f-83aa-96a2349223ab |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | bf72dbda-eb97-5419-827b-08bd9b126a56 |  | note | HOLD POINT
button | 6a7531a3-ec48-5126-8b78-1ea1a9735c94 |  | button | Acceptance | Yes,No,N/A
label | 2df17620-649d-532f-93c1-455f9ba36116 |  | note | Key - H
label | 21c5c2fe-4b44-5d1f-864f-ecc25f0ec446 |  | note | UGL Key - H
label | d2b051df-1bad-5790-bad1-c91e196113f8 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-014 Piles with Checklist Rev.4 | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-014 Piles with Checklist Rev.4 | e835eae4-11df-4f84-995e-d3c83fe1c76c
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 759b92e2-a8ff-53fe-ba97-47d6973469c6 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 1f7f5fa7-20e1-5a9e-8c7a-67d412790b6d |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | 8652baa2-1298-54b0-a0c1-fcb64381cab8 |  | button | Acceptance | Yes,No,N/A
label | 0ea19db8-dfed-582f-8373-345b2167d068 |  | note | Key - S
label | 5b398d33-fa34-573f-98ea-73229df0d6c1 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | e8549d01-b700-50c3-94d9-374c55f118b4 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | 8a54e627-6cbd-5701-a90c-0323547a9129 |  | button | Acceptance | Yes,No,N/A
label | d9957f74-7b7a-580e-abb0-794fbae31ad1 |  | note | Key - S
label | 7545c04b-c0b6-5f5f-93e8-d23c47a466d2 |  | note | UGL Key - S
label | 7879e1be-7e52-5b7a-8d0c-1dd85adb2fce |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | b5acba0e-acea-51a4-b6c3-e7657d6d2d78 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Geotechnical Engineer
label | 255174e1-1d02-594e-80e6-690028c95c95 |  | note | Ref docs - Spec. 0003 Piling [Cl 2.7.1]
label | 2e876a51-5eab-5e68-8fba-31bc794f0d43 |  | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience.
label | 41afc3fe-a1c2-5ea1-8c60-d552ce181a95 |  | note | ○ 5+ Years Geotechnical Experience including CFA Pile installation
button | c385589a-c0cf-5e90-ac05-01004f45d2aa |  | button | Acceptance | Yes,No,N/A
label | c718ac41-01cf-5921-b41f-28067bb1e659 |  | note | Key - S
label | 9ae287a0-d883-50c2-a6a5-8fa7679404b7 |  | note | UGL Key - S
checkpoint-group |  |  | section | 2.0 Materials & Equipment
checkpoint-status |  |  | checkpoint | 2.1 - Boring machine
label | 3c3d4ae2-7a02-5266-b782-06b540b265b7 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | 7bb57bb4-1cd4-569d-abc8-7628b951bfa6 |  | note | Acceptance Criteria - Details of the boring machine and any other tools that may be required shall be provided for approval by the Superintendent
label | 1035676e-b2ac-53f5-b4b3-f554ad82989f |  | note | HOLD POINT
button | d368a72e-a4b8-50ef-9f09-5c5d71d4f148 |  | button | Acceptance | Yes,No,N/A
label | d84d1500-5d93-5b85-8c92-b92fb59c1505 |  | note | Key - H
label | 04780f44-4839-5ee6-96c8-30c6f2c200a0 |  | note | UGL Key - H
label | f7eadc60-3e4f-52a6-b9f3-fc82277e75f8 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | aa2dd959-6332-5943-8ad0-d3f6475694ab |  | tickbox | Plant documents
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Approval of Concrete Mix Design
label | 2815f80e-1f13-533e-8097-8305ab438143 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.1.2]
label | fe982c8e-05ee-5033-a318-fd6f1863977b |  | note | Acceptance Criteria - Concrete Mix Code: S40/10/220 – Special Mix
label | 0d7708ad-2dda-5069-9fd1-b19fa5499b41 |  | note | ○ Strength: 40MPa
label | ef768259-732b-5aeb-b851-5808ed42e97d |  | note | ○ Agg Size: not greater than 18mm
label | ea094abb-7a66-57e8-8bc8-37a0dcd21a03 |  | note | ○ Slump: not greater than 220mm
label | 2b1bfefe-2532-59a3-8b90-998a0dc2f713 |  | note | ○ Required to achieve 25MPa @ 7 Days
label | 4c82c5f8-d6e8-5380-98bb-a856ba12313b |  | note | HOLD POINT
button | 92bcdf33-ba6f-5aa1-81a8-1dfb26b45541 |  | button | Acceptance | Yes,No,N/A
label | 7f11d634-2d48-520e-a47e-694beaecd5e5 |  | note | Key - H
label | 5578e3af-4b85-5b3d-92e4-8efc63a3e651 |  | note | UGL Key - H
label | b08aa235-c0e0-518d-a7ca-b0f8df25fef2 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0c7fa7a0-c309-5dcc-b8c1-ab5274cdcbba |  | tickbox | Mix design
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Pile Cage & Spacers
label | b5ce277b-5dab-5731-ad69-b7072b42174b |  | note | Ref docs - Drawings
label | 6396ff64-6fcd-58b5-8813-404f9e493365 |  | note | Acceptance Criteria - Certificate of Compliance for Pile Cage
label | 825dca7f-95a1-5c2f-aa3d-f8e1f909104b |  | note | ○ Cage Manufactured as per approved IFC Drawings and welding to approved weld procedure LOR-CJAUTO-12/20-250/500-1
label | 653b80d3-7f24-5bca-a0d5-b8b34ba504eb |  | note | ○ Site splice weld as required IAW approved weld procedure WPS-CSS-014
label | 1315d59d-9ad2-5b16-8449-fc1d750f9848 |  | note | HOLD POINT
button | 2116fbd1-bd8c-5cde-b5d9-3aeb96f2c965 |  | button | Acceptance | Yes,No,N/A
label | 7b8fd4c2-220a-5bf6-9fc6-59c7f4b54d84 |  | note | Key - H
label | 21e95615-8b70-5d35-bbfa-5620cd2045a6 |  | note | UGL Key - H
label | 44e7f603-80ac-5fc0-85f7-74ac6b5b66b7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 50cc7e84-f15b-5fbb-b1fc-4878b6a585cb |  | tickbox | Material certificates and COC
boolean | 0a5bedf2-7df9-5c63-b8d8-df2187964c53 |  | tickbox | Site Daily Weld Repot
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 Piling
checkpoint-status |  |  | checkpoint | 3.1 - Survey Setout
label | f49f86d8-66f2-5328-8089-224ba3ca6841 |  | note | Ref docs - Spec. 0003 Piling [3.10], Drawings
label | 184f0ef8-6374-54b0-83b3-657b331db588 |  | note | Acceptance Criteria - A registered surveyor shall be used to accurately located all pile locations as shown on the drawings and specifications.
button | d6e532e1-9f22-57a9-984d-74a56128c230 |  | button | Acceptance | Yes,No,N/A
label | 94d2fcf1-e947-51c4-ab2e-4984e10ce0bd |  | note | Key - S
label | a96bba7e-6fff-5e7e-bc67-5430c8b135b9 |  | note | UGL Key - S
label | e82faa99-55a4-572b-926d-7152972baee3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bf21aa2c-8cea-5637-ba63-7037032ae326 |  | tickbox | Survey Report
checkpoint-status |  |  | checkpoint | 3.2 - Concrete lines primed and in good order
label | 5c2ee664-7d61-5325-a0df-3b081d9eae43 |  | note | Ref docs - Wagstaff WP-MS-09.3.07 [ Cl 6.2.1]
label | 3ece6f12-c6e1-5d92-a55b-759eacd92765 |  | note | Acceptance Criteria - Inspect concrete liners have no damage and are primed correctly.
button | 527ed809-94d5-5680-99c7-c82463466450 |  | button | Acceptance | Yes,No,N/A
label | eed04f08-ed87-5820-afbe-8216f9cec143 |  | note | Key - S
label | a7f03a6f-2c97-553e-b8f2-a8eb7f5bcfa7 |  | note | UGL Key - S
checkpoint-status |  |  | checkpoint | 3.3 - Excavation of bore hole
label | 6e4ca09d-c0e4-55b2-807a-31c4e74b2ac5 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3], Drawings
label | 9fb6edb1-e8ea-523a-9d3b-0f75942467f2 |  | note | Acceptance Criteria - Verify: (via Pile Rig)
label | 1756b181-36f8-56a4-b76b-b2891396f82d |  | note | – Inclination. +/- 4%
label | 3eb7d374-e09a-5e77-bf11-5d33754f3f82 |  | note | – Diameter: 900mm
label | edcd1da7-c5c1-56e5-9660-0468c747944c |  | note | – Depth: Refer to drawings for min. depth into socket material
label | 97378cad-d03f-503a-8abd-8ac98d7d4829 |  | note | – The tolerances on the level of the bottom of the piles shall be +0, -100mm from the RL nominated on the drawings or as directed by the Superintendent
label | 5dc19090-5c22-5efb-b14e-3ccf1a22bca5 |  | note | – Length of pile/pile liner shall not be less than total length shown on drawings
button | 2ff48166-c930-5a41-88a4-6008d5f43dc5 |  | button | Acceptance | Yes,No,N/A
label | 4674aefb-353f-5cb6-903a-9b724e70ce06 |  | note | Key - S
label | 6acd9cd2-23ac-57f2-87cd-100e35e08276 |  | note | UGL Key - S
label | 695a6b8a-2666-5062-9f46-e91aa2cee700 |  | note | SHL Key - W
label | 9ce04fc9-8493-5ffa-8c13-7bde62b5437b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9fdf29cc-afbd-5b73-82f0-aa268b715323 |  | tickbox | Pile Log Sheets
checkpoint-status |  |  | checkpoint | 3.4 - Excavation conformance
label | 6ede19d9-f918-5bae-9409-f55c40e21551 |  | note | Ref docs - Drawings
label | 1d7c3333-2b41-5fb2-a892-f4e99bc63ebe |  | note | Acceptance Criteria - Check dimensions and cover are within tolerance refer to below conformance check section for details. Correct toe level as per plan. Material encountered consistent with design. Softened soil shall be removed from the bottom of the drill holes.
button | 602e6c91-2f9b-5ade-a15e-6ff0e5023ff7 |  | button | Acceptance | Yes,No,N/A
label | 7948bc18-f14f-50cb-9542-3a4e8d090cf3 |  | note | Key - S
label | 05b68a63-7c07-5738-8aed-214be7fb8c37 |  | note | UGL Key - S
label | 6b1d5a26-0211-5da5-b8e9-de65a624dc7c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | a67e551b-cc6c-5c4e-80a3-d7aa1ff13692 |  | tickbox | Pile Log Sheets
checkpoint-status |  |  | checkpoint | 3.5 - Examination of borehole
label | 751c918c-4634-5478-be4a-665fc8dfbed4 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
label | 3b759c44-3c11-5896-a459-457913c92e73 |  | note | Acceptance Criteria - Boreholes excavations shall be inspected as the work proceeds. When the founding level as shown on the drawings or as otherwise directed has been reached, each hole will be subject to a visual examination (or other methods of examination) by a Geotechnical Engineer appointed by the superintendent.
label | eb394a4c-024c-5da5-90cf-2b9e7c1f3530 |  | note | ○ The Geotechnical Engineer will advise whether a satisfactory founding level exist or whether further excavation is required.
label | b5db4c64-d2d0-5d97-970c-6a8eb1f84d26 |  | note | HOLD POINT
button | 6f5258d5-45cd-5950-bdfb-85bfa25cc8ef |  | button | Acceptance | Yes,No,N/A
label | 0c13c1e7-8596-51cf-aab0-f061a709ac1d |  | note | Key - H
label | e5690cec-037a-58fd-adf1-e489583f7c9a |  | note | UGL Key - H
label | c69d6824-200a-551d-ab48-7d449df4330d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | bd94c1f2-cd97-5155-8391-bf31588fa384 |  | tickbox | Geotechnical Engineer Sign Off Sheets
boolean | d65ff8b6-65d1-5659-84fa-448ffc592ba0 |  | tickbox | Pile Log Sheets
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.6 - Concrete supply
label | 8d960b30-136f-599f-af43-6f4081d5cf01 |  | note | Ref docs - Spec. 0003 Piling [3.9]
label | 524c62ee-c6e1-5d10-b32a-a7cce7f2f260 |  | note | Acceptance Criteria - Verify:
label | 65940216-dd57-540e-a596-0cb816c5c91e |  | note | Concrete mix
label | d3352389-b87f-5279-b765-86e03fd8203b |  | note | ○ 40 MPa 10mm 220mm TREMMIE [N545526]
label | 86cc3c22-19e0-517a-9329-e110bd35df03 |  | note | ○ 65 MPa 10mm 220mm TREMMIE [N876626]
label | 54d01b78-410a-514e-b8fd-d03735c87f2a |  | note | A concrete delivery docket to be supplied with each batch delivered.
button | 52e55c22-8873-5fd0-bd44-02a4e48393e1 |  | button | Acceptance | Yes,No,N/A
label | ea03b2d6-db08-522d-90b7-e530d4f6c7f8 |  | note | Key - S
label | 30e37087-cf6a-560e-9976-20096bf6f98b |  | note | UGL Key - W
label | 1bd3ca14-25ae-5542-b40c-a7eae138e189 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 31ef9eae-5ec4-5923-968e-45cd33600c08 |  | tickbox | Material dockets
boolean | 7e258bc4-74b5-5255-991f-4383603f3f11 |  | tickbox | Concrete Pour Records
checkpoint-status |  |  | checkpoint | 3.7 - Concrete Sampling
label | 3a6c65bf-bf0b-5150-ac15-1d599cc16dfe |  | note | Ref docs - Spec. 0003 Piling [3.9] Spec 0002 Concrete Supply, Construction and Grouting [10.2.3]
label | 5ed471a0-9362-5b90-833d-59c791193a8a |  | note | Acceptance Criteria - The nominal rate of sampling shall be taken after the concrete has been discharged at site prior to handling:
label | 0649ec6a-c23b-5a5f-a12f-ac4a34a53d47 |  | note | (a) Compressive strength (1 x 7 day and 2 x 28 day cylinders): One set per pour or as otherwise directed by Superintendent;
label | de9939d0-d326-54d8-9367-a9b715d6f624 |  | note | (b) Slump: One per batch of concrete
label | e45e05f7-e068-5b05-83e4-d6e8528214c4 |  | note | ○ Acceptance Testing shall be done at a NATA registered laboratory
button | ab3380f3-938a-5a70-850c-90b901cb08fc |  | button | Acceptance | Yes,No,N/A
label | 730edf9d-229d-56f9-bd85-f8fce696b1cd |  | note | Key - S
label | 709f15b7-67b4-5650-bd78-f08ff1a95cc8 |  | note | UGL Key - W
checkpoint-status |  |  | checkpoint | 3.8 - Concrete Placement
label | 7f6c3370-c887-5c93-9ef3-5074343958b1 |  | note | Ref docs - Spec. 0003 Piling [3.9]
label | 2cb62bc9-b65c-564b-99cb-f4ab64b3b7ff |  | note | Acceptance Criteria - All concrete shall be placed continuously and in the dry so as to ensure the exclusion of all harmful materials and provide a well-formed dense unit of full cross-section without voids or segregation.
label | 18405182-308b-5123-b9a2-1d3abb6db56b |  | note | ○ All concrete shall be placed by approved methods to limit free fall of concrete to a maximum of 3.0m
label | e380b84d-3e6a-5d1a-9cdc-7c2d354c5fa6 |  | note | ○ Top of 3m of concrete shall be well compacted with a high-capacity vibrator with a min. diameter of 50mm
label | d2ed76a4-0cb5-5572-9fed-fa7ea0dfbdf9 |  | note | Notice: 1 working day prior to placing concrete for test pile
label | a340b417-f304-59dd-be30-7bd3dd8a75a1 |  | note | WITNESS POINT
button | 7e96afac-ef3d-57e5-9136-b1da36cf1eae |  | button | Acceptance | Yes,No,N/A
label | 54d0552e-b178-5d16-a006-cd66caae3b1f |  | note | Key - S
label | e2b98283-70aa-55e2-ad9c-574672673526 |  | note | UGL Key - W
label | 8f359a13-4eb2-5960-ade0-0bc53664fa94 |  | note | SHL Key - W
label | ab5d78e9-3e56-51f3-8c93-4d0a223314b6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 6cd0486e-83a9-567a-a88c-c4570828be8e |  | tickbox | Concrete Pour Records
checkpoint-status |  |  | checkpoint | 3.9 - Concrete testing
label | 57927eee-6974-54ba-816f-6828c0ee4517 |  | note | Ref docs - Drawings
label | c07ad77a-2b4f-5ddd-8bd6-d3e0a4ae2cfc |  | note | Acceptance Criteria - Concrete test reports achieve design requirements
button | a36e85ab-f7e2-5e0c-8f1c-cb18583ea555 |  | button | Acceptance | Yes,No,N/A
label | bb8685fe-5921-5850-a27c-34c54d132b60 |  | note | Key - S
label | f9df19cb-4ef2-565c-9df2-7649738df222 |  | note | UGL Key - S
label | c34c5839-2398-5d92-8290-00adb4f03ec6 |  | note | SHL Key - R
label | f96e7ea1-71e7-5cff-a912-45630e6f1653 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ef58dab2-e6c7-509f-852a-312cc7b7daf5 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.10 - Placement of reinforcement cage.
label | 97a3e3e2-0b25-54cf-b055-3c14f36b2636 |  | note | Ref docs - Spec. 0003 Piling [Cl. 3.2.2, 3.8], Drawings
label | 259c4f37-5a23-51a6-b4a7-b5bfb403a204 |  | note | Acceptance Criteria - Ensure that cage is clean and straight. Plunge the cage centrally to pile hole and ensure spacers are attached at correct locations.
label | b876e97f-01e5-547b-a318-b4da38108fff |  | note | ○ Reinforcement cages and embedment to conform with drawings and specification.
label | 31aba693-03e9-5d78-a989-21dca6022bca |  | note | Notice: 1 working day prior to installation of each pile
label | d356712c-1bb2-535e-8f13-f579dd80ef68 |  | note | WITNESS POINT
button | fad83241-07bf-5d96-b511-c0b972f1349f |  | button | Acceptance | Yes,No,N/A
label | dd4c1ca0-39af-52d4-b589-172c1a6caf48 |  | note | Key - S
label | c7418b33-6db4-530b-8615-61913a08607f |  | note | UGL Key - W
label | 69c8e42d-efe2-521b-8a6d-9e16e3f7fdec |  | note | SHL Key - W
label | b3217662-010b-59d4-80d8-9b72543ce764 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d1befda8-bc96-5341-9194-0545b9db96fa |  | tickbox | Pile Log Sheets
checkpoint-status |  |  | checkpoint | 3.11 - Concrete RL and depth
label | 23a76afe-644f-5223-9456-bfd83723fece |  | note | Ref docs - Drawings
label | d7176361-dcb3-5881-9636-f3e4a5a8f07f |  | note | Acceptance Criteria - Bored piers depth, size, position and concrete RL as per the Piling Pile Log Sheet and Drawings.
button | 1eda28fb-fc86-5eba-ae4b-43c89ee88694 |  | button | Acceptance | Yes,No,N/A
label | 5c73f4f2-77d3-5dbc-beef-c69a33d3a8e9 |  | note | Key - S
label | c57dad27-ffd5-589b-b920-71c178b84acc |  | note | UGL Key - S
label | db059bf5-85d7-593d-bea4-8d0830368268 |  | note | SHL Key - R
label | 46d330b3-9d65-5b5c-bf78-3cf29ccbb1c3 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 63873dbb-c90a-50df-b291-10786d94aa41 |  | tickbox | Pile Log Sheets
checkpoint-group |  |  | section | 4.0 Integrity Testing - Dynamic
checkpoint-status |  |  | checkpoint | 4.1 - Pile Testing
label | 17b36df7-5610-5c8d-8474-dba61c44c30e |  | note | Ref docs - AS 2159:2009, Spec. 0003 Piling [Cl 3.13 (5)], WP-MS-09.3.30 Low Strain Dynamic Testing
label | 50f07fcc-8990-501e-83d9-dd1b6574524d |  | note | Acceptance Criteria - Minimum 5% sample size
label | ecc3f179-b8e2-51e8-92e1-2e9975dc7e48 |  | note | ○ Pile Integrity testing (PIT) as per Wagstaff Procedure WP-MS-09.3.30 Low Strain Dynamic Testing.
label | 31412fdc-aa71-5aff-b894-975248c2e54f |  | note | Notice – 3 working days to commence testing
label | 3fc80601-4580-5be1-bc59-22d42055fd40 |  | note | HOLD POINT
button | f756a290-0acd-5437-ae37-6031ae8c7d96 |  | button | Acceptance | Yes,No,N/A
label | 6fbe58b6-9291-5670-97e7-42c390154690 |  | note | Key - H
label | 70031fb2-f318-50c4-8ccc-34ed099df570 |  | note | UGL Key - H
label | 3401ffdb-d564-56c7-a308-3963f7486943 |  | note | SHL Key - R
label | 81b93211-d254-5a91-a78c-5edfc5cf1cd6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 55014ad5-b45e-5b16-a217-e2053ac23ef9 |  | tickbox | Integrity Test Reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 Conformance check
checkpoint-status |  |  | checkpoint | 5.1 - Survey
label | 0a526f08-650d-57f8-9a2a-789208165ab2 |  | note | Ref docs - Spec. 0003 Piling [3.10]
label | 3f5592d6-915c-59d4-9d39-d632f4a16b0e |  | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
label | e3485e79-7643-5e0b-ae66-27efc5a6fa63 |  | note | – The centreline at the top of the piles shall be within 50mm of the specified position
label | 48d074cc-eb80-5bbe-a832-e31799f389b6 |  | note | – The inclination of the pile shaft shall be within ± 4% of the nominated inclination
label | 7a369edd-f348-576b-838a-54ebedeebab9 |  | note | – The tolerance on the level of the top of the piles shall be ± 10mm
label | cb7eed98-80d5-5726-ba76-2bd4ef0c8d74 |  | note | – The tolerances on the level of the bottom of the piles shall be +0, -100mm from the RL nominated on the drawings or as directed by the Superintendent
label | 6e4c9fdf-1fe1-5118-8bef-8b54bed7ab52 |  | note | – Piles shall be constructed to the minimum diameters specified on the drawings
label | 14f6266f-b0ae-523a-a58f-92bed723b51b |  | note | – Length of pile/pile liner shall not be less than total length shown on drawings
label | 757bb383-f9f7-5fe8-b285-1fb6768e09f4 |  | note | – Maximum bow of pile shall be 0.1% of length
label | c0e96318-b276-5134-9842-34b484892893 |  | note | – The projection of the pile cage bars above the cut-off shall be ± 25mm from the nominated level
button | f17710c9-4884-59fe-96e5-c3dfaf73b584 |  | button | Acceptance | Yes,No,N/A
label | e9323d57-127d-5bf5-9273-29475bcd6544 |  | note | Key - H
label | 260d1403-fd50-5945-8f47-71135b145c29 |  | note | UGL Key - H
label | 099bb331-cc9d-5b7e-a5fc-09bd3734e242 |  | note | SHL Key - H
label | 8cb75bcf-6eba-569f-b2da-2446062351a5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 728af371-aba2-55f7-b336-8db39bbb1916 |  | tickbox | As-Built Surveys
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.2 - Acceptance and closure of non-conforming items
label | 34f73e26-0963-5964-9b10-276b43ceda2a |  | note | Ref docs - Spec. 0161 Quality [CL 3.8]
label | 123eb711-9971-5bd4-87a0-c1f64752fd91 |  | note | Acceptance Criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | dbee7849-413c-543a-b2d2-702ff5cf3850 |  | note | HOLD POINT
button | 0fcbce47-b530-51e1-94f7-0e338370dcbf |  | button | Acceptance | Yes,No,N/A
label | 909fa3d5-355e-5fb4-99cd-cb2759495fdf |  | note | Key - H
label | 8158d287-6083-54af-b274-26813c0d1e57 |  | note | UGL Key - H
label | 423e1fb7-335a-5433-bb08-4c4acdbe6569 |  | note | SHL Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4. | itp |  |  |  | Yes | INF-HSEQ CC0375-ITP-020 Screw Piling Load Testing. REV 4. | ee2eca22-9a52-4656-a5da-5f71c8719ae1
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Documentation
label | 0f23dc21-f8da-599a-8422-b42f00eaaa31 |  | note | Ref docs - Issued drawings / Site copy drawings
label | 637573b9-9ea9-5a10-adcb-c33690a4f665 |  | note | Acceptance Criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks. UGL to confirm current IFC Drawings & Spec
button | 2972d9ab-7417-5928-8093-f201977a26af |  | button | Acceptance | Yes,No,N/A
label | 12af8d57-272d-58be-8d37-f26a8c157dd2 |  | note | Key - S
label | a51e8c43-245d-5694-a5c6-c4af6d8b43fb |  | note | UGL Key - R
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | 1a5ab8da-ef6b-5461-9251-c9153f63bd58 |  | note | Acceptance Criteria - Lots to be broken up accordingly and outlined on a lot map
button | e89ab71f-7c3d-5c5a-b3ac-b06460d63189 |  | button | Acceptance | Yes,No,N/A
label | fac066b3-8062-5ce5-88fb-3b5281ed8df9 |  | note | Key - S
label | 9e1fafc7-3bdc-5d46-aa07-03bc889bef6d |  | note | UGL Key - R
label | c0a8081b-e0ac-55f4-944a-17ef22648db2 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 25918b83-dd71-5a66-9cc8-92271ee3f0c5 |  | tickbox | Lot map
checkpoint-status |  |  | checkpoint | 1.3 - Material Certification
label | 6a3ad37b-d497-5b73-98eb-8efddc99c91c |  | note | Acceptance Criteria - All Materials Certificate for all materials that are part of this works to be submitted to the client and approved
button | a4e3625c-264b-57d5-8d79-d895c00421c0 |  | button | Acceptance | Yes,No,N/A
label | 07c5afc5-3ffb-5460-939f-3c333a950e1c |  | note | Key - S
label | 89d759d1-ab13-5261-9df1-085508063e44 |  | note | UGL Key - R
label | 41aba242-7ca0-553f-b66a-c82abf2624fb |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | dad1b2a0-dd5e-5efc-bd3f-d2c2ac86b92b |  | tickbox | Material Certification
checkpoint-status |  |  | checkpoint | 1.4 - Geotechnical Engineer
label | 99f9fa54-ef65-592a-bc46-68ce1c86ff0f |  | note | Acceptance Criteria - Proposed Geotechnical Engineer holds correct qualifications and Experience to provide Screw Pile design.
button | 50878205-ff9f-56f2-ab5b-697f346c3dcf |  | button | Acceptance | Yes,No,N/A
label | 4e93d879-f352-51ec-a9b6-05bc127419ea |  | note | Key - S
label | 0e062795-453b-57ee-84f1-65b9add5811a |  | note | UGL Key - R
label | 37bf88e6-368f-50f9-b129-29a09e2ea176 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | c4cd47cf-0a1f-5ae4-bf28-21c56a7a95ff |  | tickbox | Bore Hole Log
checkpoint-group |  |  | section | 2.0 Materials & Equipment
checkpoint-status |  |  | checkpoint | 2.1 - Screw Piles Shop Drawing
label | 0e8d809a-181f-5707-9921-f3f68195fcc5 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | b23b2ed2-7aa0-5bc7-a089-df6beb2b1d4a |  | note | Acceptance Criteria - Shop Drawings based on BH-308 to be submitted, reviewed, and approved by UGL.
label | 1023f0ff-5bf6-5fc0-a64b-97cab1e3a1a1 |  | note | Shop Drawings to include.
label | 2ce57a3b-152f-50eb-bddb-490dfc92db76 |  | note | ○ Dimensional Requirement including tolerances if applicable.
label | d509b1a6-a0bc-5cfd-baf5-23708aee72a7 |  | note | ○ Sections designation and material grade
label | f855b6de-552c-5159-8034-ab1b30b2cfea |  | note | ○ All Welds and weld procedure
label | 84ef875a-f03c-5783-8032-f690cae2947b |  | note | ○ Corrosion protection requirements
button | e8dc42bf-6929-52e9-af5e-5052af7e1052 |  | button | Acceptance | Yes,No,N/A
label | fca86555-7e4f-5b31-a2cb-cac26da80193 |  | note | Key - H
label | 547ea1a5-63e9-5a53-8d38-8f433fd4c594 |  | note | UGL Key - H
label | f8ded7ac-9bcc-596b-8393-d965dffee6a1 |  | note | SHL Key - H
label | 6e4829bc-bcbf-5752-8301-2485a43f9d94 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | c199bdef-8722-5583-8492-02721fdb9b87 |  | tickbox | Bore Hole Log
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Manufacturing of Steel Screw.
label | 0769f6e5-8a5b-55cc-9ab9-98fb67d62e89 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | 755a21c3-4e0c-5bfb-b069-d156534a5a02 |  | note | Acceptance Criteria - Fabrications
label | 6f7884a2-8f53-5cf8-bc38-6a68971f89da |  | note | ○ Where CHS is cut using a mechanical saw, cuts to be straight and at an angle as the drawings, ±1%. The height difference does not exceed 5mm. There is to be no excessive gapping.
label | 88d6aaf5-1deb-524a-a1e5-aaa669135379 |  | note | Welding
label | 7860925c-bedb-5c1f-af58-257db3d75816 |  | note | ○ All welding to be in accordance with AS/NZA 1554. Welding procedure specification to be submitted, reviewed, and approved by UGL.
label | 4bd8155d-7d08-5843-9dcb-faafb900a3ee |  | note | Helices.
label | 27c89773-78ab-5bf6-bcbc-9ddc75a19e32 |  | note | ○ Pitch at the inside of the helix must be equal, (±4% and no greater than 10mm). Gradients of the helices to be constant. Any radial measurements of helices should be perpendicular (±4% and no greater than 10mm).
button | a786d9e9-1785-5bbb-8fc2-a7a70fd52d27 |  | button | Acceptance | Yes,No,N/A
label | 181b3852-00fc-535f-96b6-50161182a2e9 |  | note | Key - H
label | 0f1a9574-e689-5e75-aaab-8e0086db0f6e |  | note | UGL Key - H
label | 69e9b346-e8ec-5a89-b83a-b4e16042dbf1 |  | note | SHL Key - H
label | 190cd590-e959-5e44-95b2-86210cd7d6f9 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | f07d08df-5a95-59dc-8042-89aae99a3adc |  | tickbox | Material Certification
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Piling Machine
label | 57fecc29-1d2a-5fe8-9e12-22699c62b4f1 |  | note | Ref docs - Drawings
label | 62491929-985d-5598-9f6f-812447246527 |  | note | Acceptance Criteria - Details and calibration records of the Piling machine and any other tools that may be required shall be provided for approval by the Superintendent.
label | 6e8673b0-bde4-5982-a563-3b43bae40e45 |  | note | ○ Calibration records for piling rig monitoring instruments to be submitted to Superintendent
button | 755f8af6-b6d7-55e2-9fab-8c054396390a |  | button | Acceptance | Yes,No,N/A
label | 7f24bd46-7399-53e2-b0ae-358a91a65e9f |  | note | Key - R
label | 93e4290f-c0cf-5eca-8d1f-94aebaca3bcd |  | note | UGL Key - H
label | b1095940-bfe1-5152-b031-85b0c291d0bd |  | note | SHL Key - W
label | fc6e0c75-16bd-591b-b115-1917b89fa22f |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 5e75acb1-d07e-538b-b4e8-d6942b7c7592 |  | tickbox | Calibration Records
checkpoint-group |  |  | section | 3.0 Piling
checkpoint-status |  |  | checkpoint | 3.1 - Survey Setout
label | e7822654-2447-5538-b4f9-712e48170bb1 |  | note | Acceptance Criteria - Pile locations shall be set-out at locations shown on the drawings and specifications – 3 test/ centre piles to be located as per the markup.
label | c5277891-3dcc-51c1-8e82-abc28a870246 |  | note | ○ Each pile is pegged by the surveyor and identified with a unique pile number.
label | 9986b806-d60f-572d-9f37-c31cca826991 |  | note | ○ Static Load Test Compression: 4 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
label | 4922342e-2923-501e-b1cc-6f9c3a86d16f |  | note | ○ Static Load Test Tension: 2 Reaction piles to be marked out as per the dimensions of the I beam that is to be used
button | c4dabcea-2b0a-5749-b369-0b1feea19ff3 |  | button | Acceptance | Yes,No,N/A
label | cbd21f48-848e-575e-8a75-f39802883653 |  | note | Key - H
label | 5cd0f293-9e90-5a05-8025-77b5309d802d |  | note | UGL Key - H
label | b07b8e8e-5c82-5961-9735-6120bccc335a |  | note | SHL Key - H
label | 6c5897fd-a5dc-5ed5-8bbb-216b359fcf76 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | df9d01d0-71db-5e77-b346-da3fc42d07a8 |  | tickbox | Survey Report
boolean | 835e2e43-5d58-5844-a717-bb258e610b89 |  | tickbox | Test Setout Plan
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Screw Pile Installation
label | 871f0674-1399-5479-b3ef-684923c08f8a |  | note | Ref docs - Spec. 0003 Piling [Cl 3.4]
label | b4f15205-0e2f-5405-aca4-002a6f4b1d42 |  | note | Acceptance Criteria - Each screw piles shall be inspected as the works proceeds.
label | 22f17010-d81f-50e0-9bc8-52a21097e6f9 |  | note | ○ Rate of penetration to be monitored, if one helix pitch per revolution, it needs to be recorded and designer notified.
label | a766e73f-0c31-5228-8b5c-4d4f643dc00c |  | note | ○ Screw piles installed as per design and with min driving torque of 48,000NM
label | d796d75f-bf4c-50ca-869b-f8d2ee27951b |  | note | ○ Rate of penetration and torque vs depth to be recorded.
label | df7c3995-c01e-588d-8e39-a04490a0f2d4 |  | note | ○ Each piles finish height is to be checked.
label | 1d8c0082-241e-5531-9907-9b6157111b56 |  | note | ○ Testing piles to be 300 mm off the ground level, Reactive Piles to be made to suit ground level.
label | 945d2386-7ffb-547a-8f45-9b8bd8f2fedd |  | note | Notice: 2 working days prior to excavation of test pile
button | 482451d0-2b8c-53ba-8fb8-3234d1d16275 |  | button | Acceptance | Yes,No,N/A
label | accf6cdd-ac56-5527-aa76-8e0c47325d46 |  | note | Key - H
label | bd3816e9-95fa-5a71-b2e4-844a5a70e9a6 |  | note | UGL Key - H
label | 6e6ece65-00b3-54d0-a9a0-c3ede8b0bc41 |  | note | SHL Key - H
label | 9f0ab7de-57e5-5a09-a9d5-c2eb796a933d |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 9528dfe3-bfd9-551f-b7d5-3d4a9bf6f928 |  | tickbox | Geotechnical Engineer Sign Off Sheet
boolean | a05eb34b-3930-55a6-ba8d-93f2b8eb1dd1 |  | tickbox | Pile Log Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 4.0 Static Load Testing
checkpoint-status |  |  | checkpoint | 4.1 - Static Load Testing Set up
label | a9afe9a3-94dd-5af9-9d7d-9060fb39b5f0 |  | note | Acceptance Criteria - Australian piling Experts Static Load test Method Statement for set up of both Compression test & Tension test configuration.
label | 3097da13-d671-57d4-b9b9-8e01051c2fcb |  | note | ○ Place I Beam on the Test/ Reactive piles. Pile Stubs to be facing the same direction as the inner beam.
label | 7b8e86f2-8e07-5147-b21d-ef46aa6dc5a5 |  | note | ○ Place Hydraulic Jack and the Dial Gauge, allowing the dial gauges to slightly touch the reference beam and securing it into place.
label | 15044069-81d9-5018-bcbd-ba7cf65b7b92 |  | note | ○ Circular black casing to be turned until the reading is zero at 12’0 position.
button | c10894d4-969d-5f61-9c21-2b3e4e9f201e |  | button | Acceptance | Yes,No,N/A
label | 74536ce2-947e-5328-8c8c-3d5a1462898b |  | note | Key - W
label | 6f91848b-aa60-590a-b477-7026a5e34b24 |  | note | UGL Key - W
label | 2050903d-306d-5ec9-bc9d-5c9bdfd6fc58 |  | note | SHL Key - S
label | 9f540a42-6681-5863-8d08-e17ff29df943 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 45a1bb89-205c-595b-b0ac-796ea8f0e1bb |  | tickbox | Photos
checkpoint-status |  |  | checkpoint | 4.2 - Static Load Test Acceptance Criteria
label | fd1c4d40-1181-5666-9b58-32549a6c4b75 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.13]
label | e76f2075-a7da-5efb-a53f-70055ee125f1 |  | note | Acceptance Criteria - Test piles 1 & 2
label | f7c6f861-b0b7-5e88-8d8f-93b622f8d41f |  | note | Test results to conform to the following:
label | 51ee2831-03a9-5066-9bc9-3d16e364c017 |  | note | – – – – – – – – – – – – – – – –
label | 07993c19-2f5e-537b-b1bc-1ddb699d36a0 |  | note | Test Type ¦¦ Load: Description ¦¦ Magnitude (kN) ¦¦ Maximum Deflection (mm) ¦¦ Symbol
label | 856ce198-eb8a-51c1-a38c-bf1956be42fe |  | note | – – – – – – – – – – – – – – – –
label | fbaf8f7a-fa21-5448-a21d-faea14b0e851 |  | note | Compression ¦¦ Serviceability (Proof) ¦¦ 120.0 ¦¦ 5.0 ¦¦ Ps
label | d17d0e55-0691-5620-a0f8-1fda2b413324 |  | note | Compression ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 180.0 ¦¦ 10.0 ¦¦ Pg
label | f8875a03-5c97-5abc-9bc0-12e56c6492e3 |  | note | Compression ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 450.0 ¦¦ N/A ¦¦ Pu
label | 86799897-0c9a-5dbe-a14e-b7594a4c0c83 |  | note | Tension (Uplift) ¦¦ Serviceability (Proof) ¦¦ 80.0 ¦¦ 5.0 ¦¦ Ps
label | 86435cd2-e861-52d1-a6bc-50bce3671e5f |  | note | Tension (Uplift) ¦¦ Design Geotechnical Strength (Proof)1 ¦¦ 100.0 ¦¦ 10.0 ¦¦ Pg
label | 7775ede4-8dda-5cfa-be61-fa358ce18c80 |  | note | Tension (Uplift) ¦¦ Ultimate Geotechnical Strength (Ultimate)2 ¦¦ 250.0 ¦¦ N/A ¦¦ Pu
label | 2df981e6-8085-51cc-985a-0df173210a61 |  | note | – – – – – – – – – – – – – – – –
button | fdcf019e-64f8-53d9-9b36-639557ec1ad1 |  | button | Acceptance | Yes,No,N/A
label | 1c35cd27-5f1b-534d-aeb6-4d4e0af43607 |  | note | Key - H
label | 46b9adf1-c000-5f3c-86a2-18737a0e90ea |  | note | UGL Key - H
label | 733a355f-082f-5a79-9ee1-d92ccf514bf2 |  | note | SHL Key - W
label | 5b718393-456b-57d7-bdf0-a4540111d14d |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | be7550fd-44de-5329-9a87-5037718ee7e0 |  | tickbox | Static Load Test Reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.3 - Static Load Conformance
label | ef8a74bd-5c29-5cf0-aeff-2fb9be0832ee |  | note | Ref docs - Spec. 0003 Piling [Cl 3.3.2]
label | c032b46d-3957-5df8-8458-0a3a9a25fb2d |  | note | Acceptance Criteria - The testing piles to conform with the following.
label | 7ba459be-ffd5-56e7-b485-749ccd989e60 |  | note | – The loading system shall have a capacity of at least 500kN.
label | 74214283-8dee-5119-925b-a2513275ae3b |  | note | – The overall loading and measuring system shall be capable of accommodating a pile movement of at least 25mm.
label | c8bb052e-34cb-5c48-a293-45ce5ab4dfd0 |  | note | – Movements shall be measured with a system capable of delivery an accuracy of 0.1mm
label | c9b045c7-4df3-5269-b90a-b7a6ee75d706 |  | note | – Test piles to have a min spacing of 2.5m
label | 366cf292-3195-563d-a8c6-eb19fda6dcd0 |  | note | – Test piles top be min 5.0m from location of permanent piles.
label | fa1bd7ba-13c1-5ed2-ab9b-0a15dd21f18f |  | note | – After UGL review of the Test report, the test piles to be removed and kept on site to facilitate inspection by UGL to determine their suitability for reuse.
button | 0e297c71-8c01-5477-95fc-850f0f1ab8b6 |  | button | Acceptance | Yes,No,N/A
label | 4a9314fd-b9c0-541d-b02f-015ac557b3cb |  | note | Key - H
label | 9ab9dcad-efe9-577e-8a5c-7cc79dea98c6 |  | note | UGL Key - H
label | 52a18888-0df8-5be5-900f-aeb3f014f8c6 |  | note | SHL Key - W
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.4 - Test Method & Loading Sequence - Compression
label | bbcbf6b8-c127-5a36-81e0-1ad18bc01c25 |  | note | Ref docs - AS2159-2009 8.4
label | 4a8f2ec2-4aa0-587f-be4d-851de3392555 |  | note | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
label | 27615bba-b5a5-5e52-8d0e-94c8be49d10b |  | note | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
button | d699aca1-9ea9-5519-80be-8e29257b87ef |  | button | Acceptance | Yes,No,N/A
label | aa383a15-ca68-5ac1-81fc-c5b228c49772 |  | note | Key - S
label | c0056064-6cd0-5e14-baf7-24394c8a3ff3 |  | note | UGL Key - S
label | fe1a6dcd-dd66-56fb-af69-35cc6ccce3ae |  | note | SHL Key - S
label | fc29fee5-ae64-569a-95de-88ebb5133eb4 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | cdcad820-d475-579e-a7a8-d6aabe113987 |  | tickbox | Load vs Displacement Records
checkpoint-status |  |  | checkpoint | Test Method & Loading Sequence - Tension
label | edb9a01c-5b7a-5c9e-8f23-d321be0e9aa9 |  | note | Ref docs - AS2159-2009 8.4
label | 09a7b088-061a-5cb8-9ef7-87f195060195 |  | note | Acceptance Criteria - Schedule of Lod Test Requirements from AS2159 Figure A1 Completed prior to commencement of loading.
label | cf451820-db2b-5987-a0eb-89f0bd06ea77 |  | note | ○ Loading & recordings to be carried out in accordance with AS2159 Table A1 (Attached as rear of ITP for reference)
button | 0ff6f6c6-04ae-58e3-b104-40a6d47420c7 |  | button | Acceptance | Yes,No,N/A
label | 0425bd57-5833-5a1e-9ccc-477a79a10b12 |  | note | Key - S
label | 2a2b0316-7641-58af-881a-f0a017ba0321 |  | note | UGL Key - S
label | 4c18bb70-7ab1-53b0-9cfc-9bb6f3a5aa35 |  | note | SHL Key - S
label | 7da07abf-4a24-53a9-9703-2109f457e35b |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | e7c50564-30dd-501f-8dc2-1177f713c5c0 |  | tickbox | Load vs Displacement Records
checkpoint-status |  |  | checkpoint | 4.5 - Reporting
label | 1f3ad748-517e-5df8-9e35-bd6ab7233c84 |  | note | Acceptance Criteria - Test reports forwarded to UGL/Snowy for Review/Acceptance in accordance with AS2159 A4
button | 1f61aded-8cbd-58bf-bc8b-af1624347f15 |  | button | Acceptance | Yes,No,N/A
label | 1a2c2294-7e5d-51c9-91a8-5dbc657ae434 |  | note | Key - H
label | f318a3b6-634b-53af-85d2-515be59d5564 |  | note | UGL Key - H
label | f7102a2c-6a99-5437-8404-2bd3aa321d04 |  | note | SHL Key - H
label | 827039bb-ceda-5e71-9b2f-a23be8427ac5 |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 248efcc5-ad32-59b6-badf-4b4b9ee6300b |  | tickbox | Test Reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 Conformance
checkpoint-status |  |  | checkpoint | 5.1 - Survey
label | 036e2442-c56f-5e8d-b172-3a4589264906 |  | note | Ref docs - Spec. 0003 Piling [Cl 3.10]
label | dc17a448-3ff7-5aba-b8cb-aed3f80b9f58 |  | note | Acceptance Criteria - All piles shall be constructed within the tolerance specified below:
label | 691adba0-761e-579e-b053-88a0c09780d1 |  | note | ○ The centreline at the top of the piles shall be within 75mm of the specified position.
label | 585dca69-1282-53a0-947c-1eced45fa42a |  | note | ○ The inclination of the pile shaft shall be within ± 4% of the nominated inclination.
label | 80213c23-218c-56b3-9950-0b9e2760818c |  | note | ○ The tolerance on the level of the top of the piles shall be ± 20mm.
button | bf4f2fab-617b-595a-8d35-afa5d9df953e |  | button | Acceptance | Yes,No,N/A
label | a3da262d-ca15-50e3-891d-784bbe0f9c23 |  | note | Key - H
label | 57fe4a33-cabb-59c3-ba3b-e39799aa7e8d |  | note | UGL Key - H
label | 8de5f79b-b047-54b7-8c43-078019b76692 |  | note | SHL Key - H
label | d35d3c33-9fa8-5d18-9e36-56b11c2420fc |  | note | Remarks / record (e.g. test frequency, reports, certificates, checklist etc) -
boolean | 63b5fdfd-e682-5829-806c-6eeed78a092e |  | tickbox | As-Built Survey Conformance
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT