## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | GT4-ITP-012 - Concrete Structural Footings | itp |  |  |  | Yes | GT4-ITP-012 - Concrete Structural Footings | 17bf970a-fe1d-4816-ae05-7bd0e333549a
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check that current revision drawings are being used
label | e042817f-bc38-5ab8-8b4d-8aba0b78b231 |  | note | Frequency: Prior to Commencing Work
label | 63c7fe16-f3fa-56e3-9010-e04e2e423608 |  | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
label | 3a7eeb36-5a58-5757-85e1-7398959ac79c |  | note | Reference Documents: IFC Project Drawings/ Drawing Register
label | dc73a212-8e06-54e9-a98b-756a6fb779e7 |  | note | Inspection / Test Method: Document review
label | 74e851b0-1d05-56ac-9174-3bc98da1686a |  | note | Record of conformity: Latest revision IFC drawings, ITP signed
label | e29df691-d154-5405-8fef-469060371256 |  | note | HP*
label | cf200e6f-548d-598a-9ca5-d1736a6d14e6 |  | note | Responsibility: Site Engineer
date | 150ab7fa-d148-5a28-93e9-4668c90ee3f2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 3b10cc5b-bb0c-5fe6-a042-16cc53f77361 |  | note | Frequency: Prior to commencing any activity
label | 05cb82e7-65f1-513a-b87d-5502eb352894 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | 760eea08-bf03-544c-9701-7cb9138d05c1 |  | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
label | c59ec24d-86fa-5f2b-93d3-cc38195dac81 |  | note | Inspection / Test Method: Visual Inspection
label | 2d97d6a6-c2a5-5517-8d5f-e9bc68dac3a9 |  | note | Record of conformity: This ITP Signed
label | d682bc9a-3f5a-5488-b5b8-760accc22144 |  | note | HP*
label | d73d18f3-9c1b-515e-9f80-cb7be7ab35a8 |  | note | Responsibility: Site Engineer
date | 7bb33ce9-1ea1-5033-9cbf-5185a4b269ad |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Material Conformance
checkpoint-status |  |  | checkpoint | 2.1 - Materials & source Approval - Reinforcing
label | 829383c6-d207-5eaa-8fd6-24379019fb96 |  | note | Frequency: Prior to works commencing 1 per delivery
label | 12438b6f-aa2d-5502-8781-3a8125e438e0 |  | note | Acceptance Criteria: Reinforcing supply quantities in accordance with the drawings and AS/NZS 4671.
label | 7aec7f90-31fa-51cc-a7f9-24d8eea61047 |  | note | Reference Documents: Work Procedure
label | db8b695b-cbc3-5f83-afee-e48da51de39f |  | note | Inspection / Test Method: Visual Inspection
label | 88e912f4-f26c-5381-8caa-b85e7153e442 |  | note | Record of conformity: Receival inspection checklist
label | faed6a4e-b566-577a-bd1d-b8b8a2433e7c |  | note | IP
label | 9b60e8c6-9b03-5a1f-a20b-4b2f5a12d672 |  | note | Responsibility: Site Engineer
date | befdfc04-5757-5ad4-a6b3-e32fb50a0d94 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Materials & source Approval - Cast-in Items
label | 52c51619-2bf3-5252-bc7e-14c5af0ca091 |  | note | Frequency: Prior to works commencing 1 per delivery
label | f5202fbc-78be-59bd-83aa-6c2c2c0d7b62 |  | note | Acceptance Criteria: Cast-In items to be in accordance with the drawings and manufacturer specifications. All surface exposed, cast-in components are to be hot dip galvanised and fire protected as required.
label | dfeec2a0-c395-5bd9-a4a6-0d305f1293a4 |  | note | Reference Documents: EW-ST-DRW-10- 0005
label | b04ac50c-c760-54b8-9e86-2464e5dc9672 |  | note | Inspection / Test Method: Visual Inspection
label | 322fe641-8e40-5137-ba50-c7af441cf756 |  | note | Record of conformity: Receival inspection checklist
label | 3648e10e-3728-57cb-bff4-319a35053ce4 |  | note | IP
label | d2b7bc71-64c6-500d-97f2-6fa43d080161 |  | note | Responsibility: Site Engineer
date | ad83dee3-675b-5b7e-baea-624dfc9842d6 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Source In-situ Concrete Material
label | 63002da3-803e-5f62-a180-369f83613d0f |  | note | Frequency: Each Lot
label | bfe5a6ff-b111-5e02-af56-e368c2b06eff |  | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation. Concrete slump shall be 100mm +/- 20mm
label | 018d68ad-50ad-5c06-af02-88e01f663e49 |  | note | Reference Documents: EW-ST-DRW-10- 0005 Table 5.1 of AS1379
label | 8a1d1914-018d-5bb3-aafd-07f446170005 |  | note | Inspection / Test Method: Verify
label | 7128182c-8792-5ac3-b417-7a3361d1b462 |  | note | Record of conformity: Mix Design
label | 8ed36877-9110-52cd-8e67-0b11573927a3 |  | note | IP
label | 36f5fb7d-c078-5ef6-af1d-938752e66864 |  | note | Responsibility: Site Engineer
date | fb8e6a2a-b9a8-5bfa-9b62-ab45239fa550 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Construction \ Erection of Formwork
checkpoint-status |  |  | checkpoint | 3.1 - Set Out
label | 5cfc0a60-66cf-5f88-9f34-123705cb2168 |  | note | Frequency: Each Lot
label | aca1a1a9-03b8-58c0-804a-67f8f1e487aa |  | note | Acceptance Criteria: Provide 24 hr inspection notice for Superintendent confirmation of footings location.
label | 62e67905-baba-55c7-a778-0e6630dfebca |  | note | Reference Documents: EW-ST-DRW-10- 0005
label | f7e7b934-922b-5a33-bb5e-6715b69605a3 |  | note | Inspection / Test Method: Verify
label | f676945a-c920-585c-8644-629ec4dc985e |  | note | Record of conformity: This ITP signed
label | 449ae06d-9c91-55d0-93e5-30ce8af28de1 |  | note | HP
label | 9d4e0a16-57a5-5cb1-a349-3d417fcbcdad |  | note | Responsibility: Site Engineer
date | 99744db3-8f0f-5c02-9d95-d5c030c6a7e1 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Excavation
label | 0cb23bc3-dca2-5ffc-9119-30e42b7e5b70 |  | note | Frequency: Each Lot
label | fcf98c0e-2d1f-5e34-b5cb-a6d4312b36c3 |  | note | Acceptance Criteria: Excavation to be to the depth and size required for the concrete footing.
label | c928ace1-efe2-503c-a923-6feb7f45d9c8 |  | note | Reference Documents: EW-ST-DRW-10- 0020
label | 27182cba-bc57-58e4-b83f-3b468d04ba1a |  | note | Inspection / Test Method: Verify
label | b898e0c7-eab3-51fc-953e-6904e4cb4caf |  | note | Record of conformity: This ITP signed
label | 945ebad8-7059-5777-88de-0734eb47326a |  | note | IP
label | dccc1f34-5f79-589c-a416-bb71688425c8 |  | note | Responsibility: Site Engineer
date | dab1644c-7306-5365-8d2b-a73403b6f5d0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Blinding Concrete
label | a2a18cc8-44f4-5681-90b9-a090ff7bdfc2 |  | note | Frequency: Each Lot
label | ed62ebc5-05b5-5e25-8000-93eb5440b63a |  | note | Acceptance Criteria: Min. 200mm of concrete blinding layer below the base of the pad footing.
label | b8b17833-f993-55fa-a355-770b2a0d2d4f |  | note | ○ Where a footing does not extend to the level required within the acceptable founding material, the contractor is to provide a weak-mix blinding concrete (minimum N15) for the footprint of the footing to achieve the required depth
label | b5946aef-bd8c-5610-9c02-bb6496516055 |  | note | Reference Documents: EW-ST-DRW-10- 0020, EW-ST-DRW-10- 0005
label | 698672ce-c177-596c-b8b8-b1f7593036e8 |  | note | Inspection / Test Method: Inspection
label | 365671fb-bab6-5952-a4cb-ba1a28dd2cef |  | note | Record of conformity: This ITP signed
label | e5daa3ae-a702-5454-a5d6-453dd1206813 |  | note | IP
label | a493a29d-b0d8-5a60-b963-879012f7bd72 |  | note | Responsibility: Site Engineer
date | a3189298-0dd0-57c7-9cd0-7dbe7b34f6ce |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Formwork
label | dd9b026e-bd78-5fb5-aad8-91a41644ab16 |  | note | Frequency: Each Lot
label | b98fb8d3-cd93-599f-9680-faa46c20ed66 |  | note | Acceptance Criteria: Formwork shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
label | 5a63456e-bd83-5f30-9f39-3166ee1863ca |  | note | Reference Documents: Work Procedure
label | cce791c0-5a8e-591a-b2a6-517668553815 |  | note | Inspection / Test Method: Verify
label | c7da5815-0514-5a79-b4b1-850a6ad8f528 |  | note | Record of conformity: This ITP signed
label | adfb99c1-ff6e-528d-b16c-c8e4fcaa14cc |  | note | IP
label | 6c8ebaff-45a1-52e1-a8a5-0b7a62587359 |  | note | Responsibility: Site Engineer
date | 303593b2-7b7f-5fdb-89dd-cfa7977dbd34 |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Reinforcement
checkpoint-status |  |  | checkpoint | 4.1 - Steel Fixing
label | d19b2f0e-6009-547a-bfea-410815efdebd |  | note | Frequency: Each Lot
label | c356ab9c-c365-550f-b92e-de2802d11ede |  | note | Acceptance Criteria: Reinforcement type and design to be in accordance with DWG EW-ST-DRW-10-0020.
label | 9d50ec59-f0e4-56d2-bed2-43f13302a235 |  | note | ○ Reinforcing steel shall be bent and placed in accordance with AS 4671 and sufficient bar chairs shall be installed to ensure reinforcement is in the correct position.
label | 34397f99-67da-5082-baf2-ff3918ad23d9 |  | note | Reference Documents: EW-ST-DRW-10- 0020 Work Procedure
label | 863c0d38-ff96-50c2-b78d-773724803af5 |  | note | Inspection / Test Method: Verify
label | eff42568-57a6-5245-b3ec-730d7435171f |  | note | Record of conformity: This ITP signed
label | 96e83f75-cda0-5467-a731-7b69df8d7047 |  | note | IP
label | a2deb96f-3a8e-59d0-ab4a-0e5678589dd8 |  | note | Responsibility: Site Engineer
date | f5ad3420-0a5e-5c36-a4c2-dea640594326 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Reinforcement Installation
label | 1ef1b536-744d-5a03-9285-55f7a57fb029 |  | note | Frequency: Each Lot
label | 7d9b19d6-df0e-5a4f-b19a-00c9ef983879 |  | note | Acceptance Criteria: Pre-pour Checklist Completed:
label | f80ebc3c-33f2-59c2-9d07-78ba9e8f06e6 |  | note | – Position and spacing check and recorded
label | 09358062-8cba-50bc-b6aa-86b7f0f02033 |  | note | – Cover checked and recorded
label | bc889888-82e6-5ee3-8589-24624d8e0e46 |  | note | – Reinforcing supports checked and recorded
label | 7993d713-06d1-5260-b86d-ecc9be443262 |  | note | – Laps at required length
label | 76a2d624-60ab-5d69-9862-ecbde6e6b53f |  | note | Reference Documents: Work Procedure
label | bb81ee58-e2e9-5eb1-b292-4d6b465e050b |  | note | Inspection / Test Method: Inspection
label | b67afd47-bf9a-579d-a621-a6e01e59a865 |  | note | Record of conformity: This ITP signed
label | 636b442e-c476-5730-b36c-90bb40a00f88 |  | note | IP
label | 0cbe2900-f02a-5463-94d6-db4b3286f259 |  | note | Responsibility: Site Engineer
date | 4a8209ff-7a71-5913-a12e-bc610e76f5ad |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.3 - Cast-In Items
label | 4d4b417e-637d-538a-83f2-211b5b996489 |  | note | Frequency: Each Lot
label | 8b9f52b8-ebda-52fb-84e4-7a351e965ab3 |  | note | Acceptance Criteria: Installation of cast in items as per manufacturer specifications
label | b91002f4-866f-5ce8-92ae-3dd79fb77975 |  | note | Reference Documents: Work Procedure
label | ae9eb896-c340-5ea7-81dc-3f3eb54f5d87 |  | note | Inspection / Test Method: Verify
label | 5f6edbc5-1513-5dd9-9d20-7473ae853f9b |  | note | Record of conformity: This ITP signed
label | 6b9c2eec-d199-5a60-9441-571f788b6fad |  | note | IP
label | 31187ace-7958-5a58-908b-93c588af04ce |  | note | Responsibility: Site Engineer
date | e0623d9c-47a2-5b46-aece-db0814dba3bd |  | date | Date Completed:
checkpoint-group |  |  | section | 5 - Inspections
checkpoint-status |  |  | checkpoint | 5.1 - Pre-pour Inspection
label | fe0b865d-5924-5c08-a2ea-361da9175d33 |  | note | Frequency: Each Lot
label | e743ea08-1ca2-5318-acd8-e59585724747 |  | note | Acceptance Criteria: Concrete shall not be placed until:
label | 7d6ecb2d-abeb-578c-9b6c-f0252ef52438 |  | note | (i) the evidence that the forms, reinforcement, any stressing materials and embedments conforming to the requirements of the specification and the drawings, has been reviewed by the Superintendent
label | 94558cd8-caf8-5d83-b1dd-9045ce733678 |  | note | (ii) all foreign material has been completely removed from the forms
label | 8af1ed20-3b31-5b15-b078-9fea3bd42bb0 |  | note | – Superintendent requires 48 HR notice for inspection.
label | 332cf48b-57d0-5896-b265-24d4e3c36a42 |  | note | Reference Documents: Work Procedure
label | c46d07e8-8a49-5f49-983e-cc3102464afe |  | note | Inspection / Test Method: Inspection
label | 583bf6ae-2773-50d2-9d94-148caf432965 |  | note | Record of conformity: Pre Pour Inspection Checklist Completed
label | 02bf06e5-fcd4-54da-9c8b-420482a9d65c |  | note | HP
label | 73b2313b-ccb4-5065-8eeb-1259557ba651 |  | note | Responsibility: Site Engineer/Superintendant
date | 5a3287c2-22bc-5d68-ba30-85c20d83d176 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 6 - Placing and Finishing Concrete
checkpoint-status |  |  | checkpoint | 6.1 - Pour Concrete Footings
label | f7dbcb2c-1e75-5d64-ae5a-20a00b444d10 |  | note | Frequency: Each Lot
label | c7dc7b36-9b68-50ed-991c-d6003dd8ff7f |  | note | Acceptance Criteria: Footings shall be constructed in accordance with the detail shown on the drawings.
label | 1c7f35e4-27d6-5238-accd-d3001c8b07e0 |  | note | Reference Documents: EW-ST-DRW-10- 0020
label | 4b29888a-4235-5131-8f31-c907c290540e |  | note | Inspection / Test Method: Inspection
label | 3e8f7362-1d6f-590e-9664-294cd51e8bb3 |  | note | Record of conformity: Concrete pour record and delivery docket
label | 35d08bf8-6129-5dbe-b253-537d9e136fd2 |  | note | HP*
label | 41111358-69fd-5fee-abd9-879e232030b3 |  | note | Responsibility: Site Engineer
date | 30a2607d-7260-5f22-b37d-fd4af80baa00 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.2 - Finishing
label | c7de75f5-5f67-564c-93c2-d34214b0074a |  | note | Frequency: Each Lot
label | 882f4930-d402-5060-8b6c-67073edd45a3 |  | note | Acceptance Criteria: Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces. Concrete surface finishes to meet Class 4 requirements as per table 3.2.3 and 3.3.5.1 of AS 3610. (Attached Below)
label | f6728ca9-fe3c-5362-bdf4-39702c7b1ded |  | note | Reference Documents: Work Procedure
label | 45e20c05-d943-53f3-8804-e180d7e67d7e |  | note | Inspection / Test Method: Verify
label | 54d0f955-f0ab-5a12-bf6e-ea65834f5380 |  | note | Record of conformity: Completion of prepour inspection checklist
label | bac20014-3ce4-5e6c-88b6-a9a8d360272c |  | note | IP
label | 02d48317-e4a5-56fe-ab67-82654ae23db6 |  | note | Responsibility: Site Engineer
date | a35c1b9e-c7b0-56f5-a93a-1c538425faff |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.3 - Concrete Testing
label | b5ef7e95-ff44-50ad-8046-2f190ee5dde3 |  | note | Frequency: Each Lot
label | ddddae33-4866-5dfd-910f-60d011939daf |  | note | Acceptance Criteria: Testing for conventionally reinforced elements: UNO in specifications or on drawings, the contractor is to arrange for project sampling for every 50m³ of concrete supplied (1000m³ in the case of shrinkage tests alone).
label | 85b42144-0090-55c4-98ac-25838d64231b |  | note | ○ Provide slump, 7- and 28-day compressive strength and shrinkage test results in accordance with AS 1379 and AS 1012.1 to the engineer, as a minimum.
label | a44acbfc-aaaa-585e-b144-2257095b0ae2 |  | note | ○ Concrete Testing to be carried out as per specifications in AS 1379
label | 658e8331-2229-56fc-8d39-3e74fb3bb448 |  | note | Reference Documents: Work Procedure
label | e7370a4e-ea1d-5ade-bc8b-5f431dbd16c8 |  | note | Inspection / Test Method: Verify
label | 4a81a058-bc78-5b16-b558-144b09845c6d |  | note | Record of conformity: Test Results
label | 49649fed-89ec-5d42-b378-f670b59e5a65 |  | note | TP
label | d2da3098-36ce-5a81-a6fd-be856962c564 |  | note | Responsibility: Site Engineer
date | dc1bf875-6819-5eaf-b5b8-372d2543cf15 |  | date | Date Completed:
checkpoint-group |  |  | section | 7 - Post Pour Details and Inspections
checkpoint-status |  |  | checkpoint | 7.1 - Concrete Curing
label | aaee08da-ef17-59b8-8e24-0d38420f416e |  | note | Frequency: Each Lot
label | 49fd1c16-5fc5-56f4-a990-1ab245eeb1cd |  | note | Acceptance Criteria: Concrete to be cured as per project specifications.
label | c7f42e8f-8dff-5f85-ac97-5f08675919cb |  | note | ○ All concrete elements are to be actively cured for a minimum of 14 days following pouring by ponding or an approved proprietary system. The contractor shall submit the proposed curing methodology to the engineer for approval prior to pouring.
label | 65ce64b6-a500-546c-aa08-672e929e1906 |  | note | Reference Documents: EW-ST-DRW-10- 0005
label | e326c3d5-8124-5068-af9a-50e1a17436aa |  | note | Inspection / Test Method: Verify
label | 5eb9c8ac-214e-5152-b9dd-5a2307de2a10 |  | note | Record of conformity: This ITP Signed
label | 030ca864-6457-5720-9716-a4f19e00b096 |  | note | IP
label | beb3fc06-ead0-56e3-9e5a-5b98b1e9b275 |  | note | Responsibility: Site Engineer
date | ba09da84-32d4-5927-a1b7-9e766d14d542 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.2 - Removal of Formwork
label | eaee8a3b-ae18-5e2d-b979-d4c57f08eb64 |  | note | Frequency: Each Lot
label | 0bfc57c7-ff3b-58bb-a368-502a24278cf2 |  | note | Acceptance Criteria: Stripping of vertical faces in accordance with C.1.8.13 of EW-ST-SPC-000001.
label | 044af23f-d2e3-5041-963f-c7484f8cec57 |  | note | Reference Documents: EW-ST-SPC- 000001
label | 2a13e1dc-2cc0-57d2-970b-e0de6533b44f |  | note | Inspection / Test Method: Verify
label | 4da95a6f-d837-539a-aadd-c272afd5c592 |  | note | Record of conformity: This ITP Signed
label | 53f32647-eb8b-5ded-ac76-46486eb8fa7a |  | note | IP
label | 723bd709-d974-5cac-9d8d-2581609f941f |  | note | Responsibility: Site Engineer
date | 0777bf64-2121-589e-9ab6-a40914bcd9d6 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.3 - Allowable Tolerances Level & Alignment
label | 382f61d5-9b90-5f7b-98ab-0e28c1e6f529 |  | note | Frequency: Each Lot
label | bfb3eef7-4d5b-50e6-b013-02ca4ae3a939 |  | note | Acceptance Criteria: Surface Tolerances to be in accordance with Table 3.3.5.1 of AS 3610 As-built survey completed for lot
label | 0d548b08-44e2-5b11-bdbf-962e92863bc9 |  | note | Reference Documents: AS 3610
label | d5b2da16-46cb-5f4e-82a6-909fbcd40eca |  | note | Inspection / Test Method: Verify
label | 68d0fd7a-df6e-5c65-a027-039f3a29da40 |  | note | Record of conformity: This ITP Signed
label | 7e738aa3-d262-5f89-ab2e-eae77cac3da8 |  | note | SCP
label | 1bdeb4a8-435d-5a0a-8170-6aa3db75b899 |  | note | Responsibility: Site Engineer
date | 84c56df4-249a-5d8a-bb16-58b8dfdba2a7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.4 - Post-pour Checklist
label | 2cecf2cd-2bd2-5d54-9752-0a773d2498f6 |  | note | Frequency: Each Lot
label | 1359cbde-7b3f-55fd-937b-5abdfadafe22 |  | note | Acceptance Criteria: Completion of Pre Pour checklist quality checks.
label | ee53ea08-7acf-5339-b245-fe3d23b39137 |  | note | Reference Documents: Work Procedure
label | 5555985e-c494-5d57-9456-2fdc229a72b5 |  | note | Inspection / Test Method: Inspection
label | f8459f38-5b84-53bd-97f5-987e2e2d22b3 |  | note | Record of conformity: Pre Pour Inspection Checklist Completed
label | 2d74a70f-1ae7-54e9-9844-55ab7b4e533d |  | note | HP*
label | bc69b4d7-e1d1-53cc-b22e-6cc8b7816b61 |  | note | Responsibility: Site Engineer
date | ea5cc9f4-18cb-5c9b-a262-47984fd7b206 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.5 - Backfilling
label | c7a7316b-3f41-58a6-8d02-630cd07d945d |  | note | Frequency: Each Lot
label | 6b3d52d1-6129-51b1-bdec-31f51eb7484d |  | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
label | 0b38b463-25ab-5153-acb4-db905e214274 |  | note | Reference Documents: Work Procedure
label | 0d2f127b-5eb7-5d0e-85dd-ce473fff9db4 |  | note | Inspection / Test Method: Inspection
label | fbcaf8c6-d493-54f3-a26a-d9d2e772211e |  | note | Record of conformity: This ITP Signed
label | 57813096-0712-579a-af04-4281f142f367 |  | note | HP*
label | 210ea275-5632-5cd9-a206-bde4f0c3a5cf |  | note | Responsibility: Site Engineer
date | d858f164-83f9-50ed-a452-c007f5ed5ad5 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 3481137f-75f6-5842-8f94-0271f06f114c |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 7821dbf9-a69a-5617-9f5a-80c598b19a9c |  | textbox | Print Name:
text | 7f1d58ea-6186-5b89-a180-a0b72f8bdc83 |  | textbox | Position:
date | c8a49a26-8134-5e69-9a8a-c6925a9efe9d |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-001 - Removal of Existing Structures | itp |  |  |  | Yes | CTN-ITP-001 - Removal of Existing Structures | 1aba3ce5-a4e5-4f7e-994f-ff7bbf9f55c7
checkpoint-group |  |  | section | 1 - Design and Planning
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 817b18bb-702e-5e18-a1b2-284c8e1bb768 |  | note | Frequency: Prior to commencing any activity
label | a9e6268b-330f-55ec-b634-a1c3b849f4c0 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 8c4bf775-7159-55c5-9f4e-b9ccfb16c948 |  | note | – using the correct and complete set of drawings
label | 607d6183-556e-5220-af7d-a20ab900896a |  | note | – all drawings are the latest revision
label | 109cd616-6f80-5638-973e-1ff2c261ba1c |  | note | Reference Documents: Drawings and drawing registers
label | a84443f5-8667-56f4-b49d-d96cd94fd804 |  | note | Inspection / Test Method: Visual inspection
label | 9c8bb4d0-5825-535b-8171-a1a3ffe4a8ea |  | note | Record of conformity: This ITP signed
label | 75050a48-30bc-5b66-9292-c23a7b27e986 |  | note | HP*
label | 46e26e3a-5ca4-5cb4-9423-d1c99317d3e6 |  | note | Responsibility: Fulton Hogan Engineer
date | 38537439-82c0-5913-b243-715bbe60759b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 00566a89-788b-5881-be7b-4fdfb71441c3 |  | note | Frequency: Prior to commencing any activity
label | afc19906-a0e3-5976-a966-a66be289d429 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | ed2dbe6a-8a98-5635-90e0-731fd7a9c94f |  | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | 36ad26c6-db02-5298-a8bf-4e267b878369 |  | note | Inspection / Test Method: Visual Inspection
label | 1d1729d0-ed80-5bdf-bb6e-7a06a6599384 |  | note | Record of conformity: This ITP signed
label | 9fb9aaa3-9d2e-5999-b909-2d5d080de7f8 |  | note | HP*
label | df058994-288f-514e-883e-1805df3f7234 |  | note | Responsibility: Fulton Hogan Engineer
date | fd635579-5f26-5491-bd55-2c71400fd3bf |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Lift Planning
label | 29dfcb17-1b03-58b5-a80f-634239147555 |  | note | Frequency: Prior to commencing any activity
label | f1b731ed-5c52-522a-a881-6ca6ce215877 |  | note | Acceptance Criteria: Lift plan review compelted
label | 8c237f9f-3a0e-561c-ae09-a99ce1c795d2 |  | note | Reference Documents: Work Procedure, Lift Plan, HSMP
label | 0c5a7ed6-7a90-5079-b8ab-c6db6784e95d |  | note | Inspection / Test Method: Verify
label | c24c45fc-ccae-5e6f-ba0d-c6898b0b5fec |  | note | Record of conformity: This ITP signed, Lift Plan
label | 200891cd-e46c-5032-9e78-6b0d453488f4 |  | note | HP*
label | 95046906-a598-5da7-a033-14557266725c |  | note | Responsibility: Fulton Hogan
date | bb4c45c1-bd2e-5a8f-a372-f17dc93467ff |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Permiting
label | bec4c968-be4b-58a8-8a7e-9ad5b470be45 |  | note | Frequency: Prior to commencing any activity
label | c3c46484-0e1c-5de4-8cc3-376a84d06d44 |  | note | Acceptance Criteria: Verify approval of all permits and approval processes for removal of structure
label | 52ef8e3c-1d0d-50be-982a-47849bb49a91 |  | note | Reference Documents: Work Procedure, HSMP
label | 9c5a331f-03d7-5f58-af78-93b63840b74f |  | note | Inspection / Test Method: Verify
label | 5db321ad-849f-5522-ab01-9a3078ae934b |  | note | Record of conformity: This ITP signed
label | 9ffd4e6d-b2b0-5106-8a99-a1abd4d9f673 |  | note | HP*
label | de3bba13-3671-57d6-8c66-6ac0721ddd4d |  | note | Responsibility: Fulton Hogan Engineer
date | 18211a0e-589b-5830-9ff1-3a6b6cd63c45 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Transport Plan
label | e7bfc773-8f9a-518d-9a4d-6d67f5b6fb4c |  | note | Frequency: Prior to commencing any activity
label | 9114c291-fc85-5efc-8000-63f3f1c615ef |  | note | Acceptance Criteria: Transport route and plan complete, sight and review any transport documentaion
label | d7f67e9b-a5e9-560f-b25c-655b2df5246b |  | note | Reference Documents: Work Procedure
label | ada3b08f-2260-5654-ad6a-a53acd675498 |  | note | Inspection / Test Method: Verify
label | 97f8cd31-71bf-5cde-86fc-c771c891ab41 |  | note | Record of conformity: This ITP signed, Route Map
label | a3aafef6-65dd-58f9-a878-1b9978bfaaf2 |  | note | HP*
label | b21d2842-f472-5211-8993-72d52b2c5778 |  | note | Responsibility: Fulton Hogan Engineer
date | 57d9f657-ab8b-550a-8444-f9c27f59d896 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.6 - Asbestos
label | 3f232614-6821-53f6-b3fc-719ba5f83ea9 |  | note | Frequency: Prior to commencing any activity
label | c5a2b937-2024-5932-83ea-4c34a30baa81 |  | note | Acceptance Criteria: Identify and verify removal of any asbestos material
label | ad5526a3-900b-541b-93f8-81fe0493ab2f |  | note | Reference Documents: Work Procedure
label | 8a1c7cc4-b1d5-5fa7-912e-f8a82dba0cca |  | note | Inspection / Test Method: Verify
label | 44eb7fa0-dfb4-51f1-af1e-69117c57eb42 |  | note | Record of conformity: This ITP signed
label | 7bf95f35-5196-5976-887f-011979a59c3a |  | note | HP*
label | d52a15bc-5477-55e4-bc3a-85e53193f691 |  | note | Responsibility: Fulton Hogan Engineer
date | 3dd83419-4914-5081-838d-a03412ec3199 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.7 - Exisiting Services
label | 839cb016-6b8d-54e6-beb1-adb4afbc2541 |  | note | Frequency: Prior to commencing any activity
label | bb924931-bfe4-520e-92a6-669f3ffab0e7 |  | note | Acceptance Criteria: Verify the disconnection of any existing services to structure
label | 9f951521-2699-5b1d-8331-8234df9f2233 |  | note | Reference Documents: Work Procedure
label | 2e5d9da0-2fd9-5318-a9ad-51a90df3e5bf |  | note | Inspection / Test Method: Verify
label | 00c5e5b0-b8ab-5c5b-9953-58b90242e159 |  | note | Record of conformity: This ITP signed
label | 46ebe4a1-b75b-595c-9931-7158a8b987a8 |  | note | HP*
label | 96d088a3-d162-5d2b-b479-165608b95417 |  | note | Responsibility: Fulton Hogan Engineer
date | 56b19786-8ae3-507f-9778-cc066d0c8da4 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Structure Removal
checkpoint-status |  |  | checkpoint | 2.1 - Exclusion Zones
label | 5db35ba3-1e09-58f2-9ac9-df9fc4206478 |  | note | Frequency: Prior to demolition
label | e28d4e4e-0116-5d52-bcb7-2dd533546e4d |  | note | Acceptance Criteria: Identify and establish any no go and exclusion zones required for demolition
label | edf8650a-5a16-5fa2-af40-7b1ad1c92917 |  | note | Reference Documents: Work Procedure
label | 3c0c4fbc-c58a-5681-88ed-fafd9f35426e |  | note | Inspection / Test Method: Inspect
label | fe1c09aa-6535-52b1-b418-efe449724129 |  | note | Record of conformity: This ITP signed
label | 16123fa8-f713-5350-9b49-238f6f05620b |  | note | HP*
label | d2768fe1-03d9-58c2-81c1-9321d04ef647 |  | note | Responsibility: Fulton Hogan Engineer
date | 46381fc8-344c-59ed-bfdb-0866015365ec |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Demolition of Incidental Strutures
label | 428c1495-994f-5e4e-8b64-a2f44b1ebe05 |  | note | Frequency: Prior to concrete pour
label | 41524d0e-b47c-5f90-8299-38d88f024203 |  | note | Acceptance Criteria: Identify and remove any incidental structures relating to the main structure
label | 607c8df9-e046-58e6-8e00-1fec565cd3a8 |  | note | Reference Documents: Work Procedure Drawings
label | 23183848-36fb-589b-a525-5a824da599f8 |  | note | Inspection / Test Method: Inspect
label | 8d5302af-ef46-5dea-8fd4-aab87fbfb192 |  | note | Record of conformity: This ITP signed
label | 2216c056-dd8c-537e-8a94-f7b83f9e45c9 |  | note | HP*
label | 77a70266-0100-537f-a03e-f17e1acede07 |  | note | Responsibility: Fulton Hogan Engineer
date | 18e9a6fe-d2af-509e-9211-9d80281d42b0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Relocation Route
label | d9a8a110-a1c6-501a-817f-7cdb5534698a |  | note | Frequency: Prior to Removal
label | 3210e208-06f4-5db2-9cd0-8b8bf39267ac |  | note | Acceptance Criteria: Ensure relocation route is prepped and clear for relocation
label | 93b60acd-747d-5d2e-979d-d32ffa010e57 |  | note | Reference Documents: Work Procedure
label | f6c23272-afa0-54a5-9d68-c79ba45e2ceb |  | note | Inspection / Test Method: Inspect
label | 0a12dee8-0e1c-55c6-906c-38b5134f5291 |  | note | Record of conformity: This ITP signed, Route Map
label | 5f716c1e-6214-568b-8994-efe3caaefc33 |  | note | HP*
label | 2f23b183-a364-5192-aca8-5e22bd5efb1e |  | note | Responsibility: Fulton Hogan Engineer
date | 41aa9b4e-b852-5d10-ad00-f66337c3d25b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Removal of Structure
label | de4a5e26-d5ab-5565-9b62-ade1497a86c2 |  | note | Frequency: Prior to Removal
label | e2fec0f0-c495-5b75-bdff-87ac1ea0ddc8 |  | note | Acceptance Criteria: Ensure removal of structure is undertaken per approved documentation
label | e6f89419-d112-54a0-a261-db01bad88707 |  | note | Reference Documents: Work Procedure
label | f1018777-5902-5e83-b376-947e8a7ff9ce |  | note | Inspection / Test Method: Verify
label | 07083b1d-5006-52f4-936a-1ef9e53dd8b4 |  | note | Record of conformity: This ITP signed, Lift Plan
label | d127c9cd-8949-5153-b500-b90d16d9d566 |  | note | HP*
label | 05ec88c2-6411-5b58-b8ab-8a1675bab1a2 |  | note | Responsibility: Fulton Hogan Engineer
date | 5899864a-5b7d-57fd-bb28-a1a35754bb81 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Structure Laydown
checkpoint-status |  |  | checkpoint | 3.1 - Laydown Area
label | 400df3fb-9600-5f45-98f6-acbe341d7b02 |  | note | Frequency: Prior to Removal
label | 4a590cd4-98d9-52f9-a073-6ddbd51d9959 |  | note | Acceptance Criteria: Verify laydown area is ready to receive structure
label | d1bff902-8945-581c-8bbd-4255c603f370 |  | note | Reference Documents: Work Procedure
label | f4579d08-009c-57d8-acc2-0108c96cb117 |  | note | Inspection / Test Method: Verify
label | 8154b46b-2731-5aef-8557-35a25691cdb8 |  | note | Record of conformity: This ITP signed
label | a7899a9a-5ea2-5fc2-8915-b006d2ee36a1 |  | note | HP*
label | 6a3c4b43-c1c1-5ca5-b3ef-5530303aaa3f |  | note | Responsibility: Fulton Hogan Engineer
date | a075f219-18c0-55e8-9321-057a3b35c19c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Storage
label | 09543e02-b2c2-53ed-b6bd-5d86476c1afb |  | note | Frequency: Prior to Removal
label | d2b306e9-f378-52b7-803f-393df581c757 |  | note | Acceptance Criteria: Structures are stored in such a way as to prevent damage if required
label | 7ba802d7-e36b-5bcd-8e5b-0ec8986a755d |  | note | Reference Documents: Work Procedure
label | 78f469f6-11f8-5565-a224-6ea0b621cc12 |  | note | Inspection / Test Method: Verify
label | 9d9163df-e41b-548f-8b59-2cbcda9c5d63 |  | note | Record of conformity: This ITP signed
label | d489aa33-a9d2-5ca6-813f-ca40b8cb17bc |  | note | HP*
label | 4cefbda3-65c0-5a80-aa91-522b98219ee5 |  | note | Responsibility: Fulton Hogan Engineer
date | bd18d30c-af8c-5724-a67e-cb444e643db4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Photos
label | 4215aa14-3b23-5824-b251-9a909d9d940f |  | note | Frequency: Prior to Removal
label | 9c352a00-c8a7-5b9f-9f65-7761b76f67dc |  | note | Acceptance Criteria: Photos of stored materials
label | 79bac840-6d64-5880-9d2b-774148cf0365 |  | note | Reference Documents: Work Procedure
label | 69303c3d-88d5-5197-9aa6-6b0879e1cbb7 |  | note | Inspection / Test Method: Verify
label | 126eb712-6582-5738-854a-57c281491f24 |  | note | Record of conformity: Photos
label | 26d1fe8b-dcdf-5f79-a057-bdd8605e8852 |  | note | HP*
label | f9136fc9-784c-51ec-ac6f-36c286e3611c |  | note | Responsibility: Fulton Hogan Engineer
date | 017f885a-ea90-5c05-ae30-831eb18113a2 |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Closeout
checkpoint-status |  |  | checkpoint | 4.1 - NCR
label | f067902f-1607-561d-998d-182ca64ab090 |  | note | Frequency: Prior to lot closure
label | 9e33086e-8824-53f1-94d6-99dd0ebd1114 |  | note | Acceptance Criteria: Details of any NCRs to be recorded in CL01E (if applicable)
label | c2514d4f-1ebe-56da-b455-43f3e8de4200 |  | note | Reference Documents: CL 01E
label | e83734ba-d903-5178-bb6f-2701eca58fe8 |  | note | Inspection / Test Method: Verify
label | 47a09f95-8691-5651-b9c5-a8257d06f7b3 |  | note | Record of conformity: This ITP signed
label | d0da66fc-ed83-559c-9b7d-e577062815d9 |  | note | HP*
label | 66f6000c-6915-540d-876e-d21221fd2614 |  | note | Responsibility: Fulton Hogan Engineer
date | 1aeffe23-bbee-518c-a61f-a4dea0df3080 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Permits
label | 306194c8-223d-501d-8a43-a6bd622bd182 |  | note | Frequency: Prior to lot closure
label | 8ecc36b1-1eda-5da6-a7e6-006124f36362 |  | note | Acceptance Criteria: Close out applicable permits
label | 203ebe11-f315-54c4-9963-8be44f41e101 |  | note | Reference Documents: Work Procedure
label | 66804ae2-14db-5c3a-affa-dc7d168da0eb |  | note | Inspection / Test Method: Verify
label | cbf2c34a-8b51-5c62-b10c-0152432e94a0 |  | note | Record of conformity: This ITP signed
label | 9789f563-9fdb-5bbc-844b-a61c432c2cc2 |  | note | HP*
label | 8242a904-e71d-5d78-bc61-060b0ab88911 |  | note | Responsibility: Fulton Hogan Engineer
date | 25fb153a-9cba-5cda-8c02-d6bfe15f1c46 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 6aacb68c-77d4-5b2e-868a-a69ac7db723a |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | d0407496-5f56-5026-9969-d36cc2918732 |  | textbox | Print Name:
text | a97f2adc-ad57-50ab-819d-7a78a6c619b9 |  | textbox | Position:
date | 92ffca2d-80c6-5fc8-a028-bed8e009fad9 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-016 - Cement Treated Crushed Rock | itp |  |  |  | Yes | GT4-ITP-016 - Cement Treated Crushed Rock | 2240fd55-240a-48a6-9f16-9ad9fc4c1d27
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check that current revision drawings are being used
label | cf291b18-de52-5de9-ac1b-beb344c81988 |  | note | Frequency: Prior to Commencing Work
label | e263a7b5-a463-5963-b902-3825d5c5d6fa |  | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
label | f948ab12-a59e-5bf8-8451-260016540f51 |  | note | Reference Documents: IFC Project Drawings/ Drawing Register
label | bd48a409-e6e9-52a7-ba4c-d602b71fd389 |  | note | Inspection / Test Method: Document review
label | 616a30cd-2523-5f3e-a445-610bd272706a |  | note | Record of conformity: Latest revision IFC drawings
label | 7da88eec-fe08-56ac-908b-95e704a266fc |  | note | *FH
label | 63b26a0f-1d30-5c86-abcb-8adab3d3d833 |  | note | Responsibility: Site Engineer
date | c51fa852-37fa-5199-9e62-bc1a3bd3a9e4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place
label | 33b93d1b-71ec-5a81-8a12-8d4a237c314c |  | note | Frequency: Prior to Commencing Work
label | db3dfc38-93b7-56c3-a1c9-1923f1b5248e |  | note | Acceptance Criteria: All environmental measures to be implemented as per current EMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified
label | 978c9ec7-1bbf-555d-ae28-50cff2e4f478 |  | note | Reference Documents: EMP, Site induction
label | b1c1aad8-eb3c-5205-b789-770846e65574 |  | note | Inspection / Test Method: Document review & Site inspection
label | 2b738745-8021-5879-b57b-7ca09886197c |  | note | Record of conformity: ITP signed
label | b5bf32c8-f3a9-5f1b-9d3a-961fe96d5ae4 |  | note | *FH
label | 36f09ddf-2c3e-5f66-8c0d-bc3481d3275c |  | note | Responsibility: Site Engineer
date | cac76a4b-bf2c-582d-8363-e68a16cc230f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Traffic Management (When required)
label | 24747068-437c-5129-bedd-0fdac6e5a436 |  | note | Frequency: Prior to Commencing Work
label | c0d83f08-a67c-5b1f-9f67-53049e083a96 |  | note | Acceptance Criteria: Approved TMP
label | a7f5bbc3-736f-5837-b9a6-43ff7886b13a |  | note | Reference Documents: Applicable TMP
label | 43221b9e-be8b-5278-87b6-1659d16f5af0 |  | note | Inspection / Test Method: Document review & Site inspection
label | a994542d-2554-5e44-950d-86a5b5c4227f |  | note | Record of conformity: Approved TMP & MOA
label | 1e731bef-92bb-56d2-a6af-e99066f3d577 |  | note | *FH
label | 85de30f6-e78c-5491-9c85-ca0cc291bbda |  | note | Responsibility: Site Engineer
date | 8a1f970a-5df1-5ed3-97e4-4db233576baf |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Survey set out works
label | 35749df3-ccf7-518e-8418-f49289ad5a3c |  | note | Frequency: Prior to Commencing Work
label | 486437fb-8095-5497-884d-960d6d459307 |  | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
label | c082d46c-8e8c-5a66-9ed0-5d96633fe609 |  | note | Reference Documents: Applicable DWG
label | d2801102-ecea-54d2-9614-d9dc3238097b |  | note | Inspection / Test Method: Site inspection
label | 6bcc142e-8906-54ae-8450-b361a4a6a097 |  | note | Record of conformity: Survey records & marks on the ground. This ITP Signed off.
label | fcbd6caa-acb9-5a14-a924-3d67bd14a189 |  | note | SCP
label | e2c50ad8-a692-5ddf-9a54-26220812f551 |  | note | Responsibility: Site Engineer / Surveyor / Superintendent
date | 2b4a4838-685f-5515-979c-c8970cbcad3b |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Placement
checkpoint-status |  |  | checkpoint | 2.1 - Delivery Dockets
label | c53926de-0b01-5923-a589-e0e7f8ee512d |  | note | Frequency: Each lot
label | 371055ab-130a-5916-9728-abb61504ae11 |  | note | Acceptance Criteria: Where material is scheduled for measurement by loose volume in delivery vehicles or by mass, a delivery docket for each load shall be issued to the Superintendent at the point of delivery.
label | 1a8e7bcb-e3cb-51a4-bf2f-3289f5686a90 |  | note | Reference Documents: VicRoads Sec. 306.07 (b)
label | 8884a081-9ea2-52f7-90a8-ae12e69db902 |  | note | Inspection / Test Method: Visual and Measure
label | ad86069b-d7fd-5649-954b-6ebd3ae5c9ac |  | note | Record of conformity: This ITP signed
label | d5d17753-675b-529f-8bf7-52d94737c381 |  | note | IP
label | aa1d36a5-c053-501c-9c11-ca7cb088ed88 |  | note | Responsibility: Site Engineer
date | 3bebbe5e-4b5f-531b-82e8-880262e95627 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Placing of Crushed Rock
label | c2c5d71c-bdf9-57e4-a21a-3105b88b2023 |  | note | Frequency: Each lot
label | de86d94f-3d6f-5c80-9a53-d8d02bc97680 |  | note | Acceptance Criteria: Crushed rock to be a single layer 150mm thick constructed within the tolerances specified in Clause 306.03.
label | 07ca1ef9-5121-5bd9-b059-bd62bca735bd |  | note | Reference Documents: VicRoads Sec. 306.03, 306.11
label | 7c66bacc-95c6-526e-8be6-55f76f25e52a |  | note | Inspection / Test Method: Verify
label | 8d3bd9d2-55a9-57a4-a31a-4ed46601cd0d |  | note | Record of conformity: This ITP signed
label | d7100472-850c-5823-9bdc-d5a3fb161ad2 |  | note | IP
label | ecd16e80-8ea0-5c32-a28f-97066983dcb0 |  | note | Responsibility: Site Engineer
date | 259d7e2f-73e3-554a-8770-265d8947fdc9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Moisture Content
label | 858b91d4-4e28-5a1d-ad71-0c22472c6448 |  | note | Frequency: Each lot
label | 34cb0689-9f30-5e29-91e7-f2840a4cebd0 |  | note | Acceptance Criteria: The moisture content of the material at the time of spreading and compaction, expressed as a percentage by mass, shall be within plus 2% and minus 2% from the Modified optimum moisture content.
label | 7c47349e-4a08-5075-aa26-f5e6be34c05d |  | note | Reference Documents: VicRoads Sec. 306.05
label | ed0ed0ea-cb09-5166-8575-398a94445556 |  | note | Inspection / Test Method: Verify
label | e8b15f76-7ee3-54b4-9c02-5fc952dd2784 |  | note | Record of conformity: This ITP signed
label | 29b221c0-4c8e-57de-a25f-a4cbf3c7cea6 |  | note | IP
label | 0657ed55-3b97-58f0-b6c5-b295db2b996b |  | note | Responsibility: Site Engineer
date | 399772c5-b183-5b98-a7a5-c1e2c5b8200c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Water
label | a2feedd5-7506-50b5-a1b7-ae6d92993a5f |  | note | Frequency: Each lot
label | 3d03e4ab-fdb6-523e-9ba3-f7c9e4bc44d6 |  | note | Acceptance Criteria: Except for the purpose of curing, no water shall be added to the cementitious treated material.
label | e7d37df5-d5ee-5e0d-a373-e3259f4a4f5e |  | note | Reference Documents: VicRoads Sec. 306.06
label | b41e5b68-e6a9-53b8-b26c-ec70401e2229 |  | note | Inspection / Test Method: Verify
label | 2075d32d-ebcf-575e-8977-f5e8d0c162a6 |  | note | Record of conformity: This ITP signed
label | 2ca1f50a-aa6e-53b7-95ea-a2b6c7aadd1c |  | note | IP
label | 01edbb9d-39ee-58da-a918-e09097763431 |  | note | Responsibility: Site Engineer
date | d4ae502e-cf49-59cf-a42f-62e29ef735da |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Conformity with drawing
label | 7759f833-af0f-5fd8-b6bb-21934ab8bc7e |  | note | Frequency: Each lot
label | 7fe1ca9b-cf10-5406-a2e2-4b818f39c713 |  | note | Acceptance Criteria: Pavement subbase shall be finished to a smooth and uniform surface and shall, after compaction, conform within the following limits to the levels, lines, grades, thicknesses and cross sections as specified or shown on the drawings.
label | e75fb2ec-8bc8-5a52-bc97-350e4930fd37 |  | note | For Scale B Pavement
label | d0600d7a-5c22-5731-b9d9-c5b1396b1c21 |  | note | (a) Width and Alignment
label | 78cb2595-5066-51e7-8871-a165a7bed62f |  | note | ○ The width of pavement measured on each side of the centreline or design line shall not deviate by more than 50 mm from the designed offset when measured at a right angle.
label | cede793a-6859-51aa-8a38-1281d31d6849 |  | note | (b) Surface Level Requirements
label | dc8f9b3b-8ab7-506c-bac6-0b3415aadc30 |  | note | ○ Minimum Number of measuremnts per lot: 40
label | b5bff45b-ee7b-5144-beda-398828e66d68 |  | note | Reference Documents: VicRoads Sec. 306.03 Table 306.031, Table 306.032
label | faf30db0-a1ee-5d48-a1e3-f24e6f32dbbe |  | note | Inspection / Test Method: Survey
label | 15e984c4-ef6f-5258-b468-dd206e2ba187 |  | note | Record of conformity: This ITP signed
label | 8fcdf841-9430-528e-91aa-0b469f7aa89c |  | note | SCP
label | 9654da72-a5c7-508e-ad0e-0959c312e5d1 |  | note | Responsibility: Site Engineer
date | 2baf0e1b-6499-5172-b5a6-1d62c15a4ac3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Jointing
label | dd30af0d-6cbc-5d73-b0a7-9fb0efc923b2 |  | note | Frequency: Each lot
label | e26d08b3-088e-56c7-952a-a46fe945608c |  | note | Acceptance Criteria: The layout of joints shall conform to the following requirements unless otherwise approved by the Superintendent:
label | 96eff8f0-9f0b-52de-8cdd-28a3cb61f532 |  | note | (a) material shall be spread in such a manner as to minimise the number of joints;
label | b6f2d705-e424-5246-ad65-02e80a1cbe6f |  | note | (b) in any layer, transverse joints in adjoining paver runs shall be offset by not less than 2 m;
label | 9d9ca3c7-5307-59ad-b632-8b390a0ebcb3 |  | note | (c) transverse joints shall be offset from one layer to the next by not less than 2 m;
label | 2793a9e9-bc23-50cc-b54e-d7fda7969463 |  | note | (d) longitudinal joints shall be offset from one layer to the next by not less than 150 mm;
label | 51110ea9-99c0-5248-b531-55104c97bc19 |  | note | (e) longitudinal joints shall be located within 300 mm of the planned position of traffic lane lines or within 300 mm of the centre of a traffic lane.
label | f89256da-7f2e-5010-9ea9-ec62561db051 |  | note | Reference Documents: VicRoads Sec. 306.08
label | bcfaec3f-f774-5c29-960d-61b2e85b9de0 |  | note | Inspection / Test Method: Visual Inspection
label | 6c14716f-80de-5861-806e-21533327f9f9 |  | note | Record of conformity: This ITP signed
label | 585b9907-01c1-57d5-be38-2bd4c692c145 |  | note | IP
label | d957bad0-a9b7-550e-8f41-ee52a78d6e29 |  | note | Responsibility: Site Engineer
date | d9447a82-811d-5df3-8175-9523e8eb697a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Compaction
label | 043d4e6d-6b7c-5aa2-8b51-6fbf184979d5 |  | note | Frequency: Each lot
label | b58dc642-7ec6-5d0b-b5bc-f12f26d231dc |  | note | Acceptance Criteria: Compacted to at least 95% modified dry density ratio with a mean value of at least 96% modified dry density ratio.
label | 081c8e90-59d9-586a-b848-adae6598cb69 |  | note | ○ The cementitious treated subbase material shall be placed, trimmed to level and fully compacted within the maximum allowable working time specified in Table 306.091 depending on the binder type and the time of year the subbase is being placed. (Table Attached Below)
label | a7f05715-893d-5a87-912b-f9f1a4ae37fe |  | note | Reference Documents: EW-CE-DRW-406-001 (Rev D) VicRoads Sec. 306.09
label | 972c31ba-aee6-5edc-b43d-920b35ca5f5b |  | note | Inspection / Test Method: Test report
label | da188151-03c5-50c6-a038-ddbc8ae678cb |  | note | Record of conformity: ITP signed
label | 69b1f5c5-f733-53b5-8593-7fa17e10e7af |  | note | TP
label | e250050e-f185-5186-8b10-6185123e3cdf |  | note | Responsibility: Site Engineer
date | 32278647-6cd6-5fda-85df-27e6fba8cf1a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Curing and Protection of Compacted Layers
label | bc45f4d5-d8c9-5371-9239-ee7f6f9962ba |  | note | Frequency: Each lot
label | de1e8914-bd49-59a5-8dee-a5d270014dc8 |  | note | Acceptance Criteria: For Minimum Youngs Modulus of 500MPa,
label | c7fa7cf4-0a7a-5086-912d-1ea4f6dcab9c |  | note | ○ The surface of each compacted layer shall be kept moist for a period of seven days unless covered at an earlier stage with the succeeding layer or with an approved curing membrane.
label | 10932341-08fc-5a28-8d21-13ed1702cdc1 |  | note | ○ Construction or other traffic shall not use a compacted layer within 24 hours of placement without the approval of the Superintendent.
label | 5420a89b-0f35-55f6-96d5-f213543d62d4 |  | note | ○ The subbase shall be kept in good order and condition and free from contamination.
label | 8f21e95d-e708-50ab-8394-8f4cd0ddc91c |  | note | Reference Documents: EW-CE-DRW-406-001 (Rev D) VicRoads Sec. 306.11 (a)
label | 0c4692dd-4888-57e4-8933-259f8faf0747 |  | note | Inspection / Test Method: Verify
label | e02b91a2-6122-5582-b94b-4e2d84fb8ba8 |  | note | Record of conformity: ITP signed
label | 2de44f50-fd8c-5d23-bebc-227e58adc11a |  | note | IP
label | 7f848fb3-8c47-5868-acba-cb19c8b363eb |  | note | Responsibility: Site Engineer
date | d922ed66-d7ef-559c-8c74-9b530a0195fc |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Conformance
checkpoint-status |  |  | checkpoint | 3.1 - Test Rolling
label | eee7d904-5b9b-5e58-ae42-55364fccfd90 |  | note | Frequency: Each lot
label | 3587cff9-b653-5366-acbf-189a065aabec |  | note | Acceptance Criteria: Test rolling may be carried out in accordance with the requirements of Section 173 (Specifically Section 173.03) on the cementitious treated pavement subbase layer within the maximum allowable working time for the relevant binder and time of year as specified in Table 306.091.
label | df38a555-9da0-5894-a77f-461740923584 |  | note | Reference Documents: VicRoads Sec 306.10
label | 7f129e90-661f-51bf-8947-e2a2f37219b8 |  | note | Inspection / Test Method: Test Roll
label | 8cdf5376-4460-5f53-a8ca-ae33e00805ff |  | note | Record of conformity: This ITP signed
label | 2157d086-bfa6-5b9f-a1f9-168f9733a16b |  | note | HP*
label | 8ccf9301-946e-5f38-bc1e-f7ac68da4adb |  | note | Responsibility: Site Engineer / QAV
date | be268333-9f11-5849-ae39-93da21c9960c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Testing and Acceptance of Compaction (Scale B)
label | 87765629-8af0-52fd-b972-040d9981f7c1 |  | note | Frequency: Each lot
label | 5ae7559c-d640-5825-9b71-7a7a05779698 |  | note | Acceptance Criteria: The work represented by the lot will be accepted as far as compaction is concerned if the mean density ratio for the lot is not less than 96.0%
label | eab9ed9e-194d-5f0a-a8d3-e0e7b73d52f2 |  | note | Reference Documents: EW-CE-DRW-406-001 (Rev D)
label | 27ac6b67-b8d5-50e0-a4ea-8ef2ec5ae09f |  | note | Inspection / Test Method: Test point
label | 2f18b6ad-5487-52fe-94d2-7d8bf20bf295 |  | note | Record of conformity: This ITP signed
label | ce9ab979-dc0d-54a2-b465-a928f2bf69fa |  | note | HP*
label | b4b8e5bf-985b-549e-9d21-225845c9082a |  | note | Responsibility: Site Engineer
date | 393ffd2a-ecf5-58de-a1a1-0ca80fe1fc3c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Survey Conformance
label | 65b22e2e-fece-58ed-8f70-13144ff1ea64 |  | note | Frequency: Each lot
label | 9d4e6169-6f44-5327-97de-b7ad9a58d1b5 |  | note | Acceptance Criteria: Mean values of all level readings taken in the lot: +6mm to -12mm, Maximum Standard Deviation of 13mm
label | b365380d-697a-579a-8568-5b283bb0fbe6 |  | note | Reference Documents: VicRoads Sec. 306.03 Table 306.032
label | ef038073-c4ea-5686-8a62-0d3438448320 |  | note | Inspection / Test Method: Survey
label | 842e858b-8c6b-5d31-926e-d6f5399773a2 |  | note | Record of conformity: This ITP signed
label | fd3edb68-1394-5613-9ecc-1f1049e64c3a |  | note | SCP
label | 54c7491e-53d1-50a4-9144-619a801fcef7 |  | note | Responsibility: Site Engineer
date | 80f0d53d-e0ea-524a-ac14-929772c0a949 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Shape
label | e265378c-4fe3-562d-9003-d609b122c995 |  | note | Frequency: Each lot
label | a376fea0-1f5f-590b-b8e5-877971e0f6bd |  | note | Acceptance Criteria: No point on the prepared surface of the subgrade shall lie more than 12 mm below a 3 metre straight edge placed on the pavement in any direction.
label | 79250ad3-0726-5947-b64f-000cffd7a23e |  | note | No point on the surface of the cementitious treated subbase layer shall vary by more than 8 mm from a 3 metre straight edge, or 10 mm from a 6 metre straight edge, placed in any direction.
label | 0140f500-d356-528f-96ae-020b72f2acf3 |  | note | ○ Water shall not pond on the surface of the cementitious treated subbase.
label | cf70c5be-a3f4-5f70-b062-e13f8b5e33a2 |  | note | ○ Reference Documents: VicRoads Sec. 306.03 (c)
label | e4b31da0-1c45-5fd8-b5ed-a4dc68774f7d |  | note | Inspection / Test Method: Test Point
label | 5e1970b8-94e1-5434-acbb-cdcabfe39a61 |  | note | Record of conformity: This ITP signed
label | 85596e29-c362-5820-bf7d-8f885119376d |  | note | TP
label | caea527b-5012-5501-9a13-e19c64dac829 |  | note | Responsibility: Site Engineer
date | fbc83eca-5ef9-559c-a483-14349f1676d7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 13eefa15-0675-55c2-bf7c-3b664521a478 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 00101fc5-1612-59ab-86d3-d7e0462316c9 |  | textbox | Print Name:
text | 111eb441-abda-59e5-9613-97b7b1135b54 |  | textbox | Position:
date | c9d415aa-99fb-539b-a85a-b57fad3adb93 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-005 - Asphalt Placement | itp |  |  |  | Yes | CTN-ITP-005 - Asphalt Placement | 3acc7465-8e49-4478-898f-4c0baaf34ca4
checkpoint-group |  |  | section | 1 - Construction Works
checkpoint-status |  |  | checkpoint | 1.1 - Submission of Mix Design
label | a0c4232a-ada3-5e74-b342-e30d99b75dbf |  | note | Frequency: Prior to commencing paving
label | 039bf732-3637-5948-a58e-f5f585d44cd7 |  | note | Acceptance Criteria: No Asphalt shall be supplied until the mix has been registered and the superintendant approves the mix for use. Only use mixes that are registered by State Growth as 'General Mixes'
label | 592e43b5-e0c8-5600-8f84-c3d1c15fea48 |  | note | Reference Documents: Cl 407.06
label | 1e0a6236-66a4-57db-95e5-ded34bdc813d |  | note | Inspection / Test Method: Verify
label | 008bf1d9-4f2c-58f4-b7e1-cdf760a9c93c |  | note | Record of conformity: Mix registration & correspondence
label | a20d6b39-06d8-5b90-b516-f98ae9b356fd |  | note | HP
label | a16b556d-5203-596a-a55b-84077a1e5f1d |  | note | Responsibility: FH Engineer/ Asphalt Supervisor / QAV
date | ee4dff7a-cf09-51fa-9e8a-98941f7a730d |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 7e4ba150-bd71-58e9-9c81-0a8b6e786b82 |  | note | Frequency: Prior to commencing any activity
label | ec5e58ad-b635-536c-be83-fefa5691c764 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | 02c6e13d-34a7-57c3-9e8e-87003350eea2 |  | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | 1a730786-c11c-5762-b16f-8db8b10353ad |  | note | Inspection / Test Method: Visual Inspection
label | 0b27675e-1612-524a-bdff-1fc6a8b85d79 |  | note | Record of conformity: This ITP signed off
label | 35b47ce5-2508-5e4a-84cc-83e2d0bf734d |  | note | HP*
label | bcc15dd8-fdb2-5102-b9c7-b0b8a4558062 |  | note | Responsibility: FH Engineer
date | ca58188e-afe5-5d27-800e-a799ebf15ba9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Site Inspection and Base Condition
label | caca90a7-bbf1-5472-bc93-32e89c3c1f04 |  | note | Frequency: Prior to commencing paving
label | 1420f621-67c1-56b3-9494-2dd50a8d4054 |  | note | Acceptance Criteria: Base condition is acceptable for placement of asphaltic concrete.
label | 8b58e52a-e5b4-5ce4-a261-2eaaab92a9a0 |  | note | Reference Documents: Work Procedure
label | ed8ac413-475a-551d-b88f-299446545cc2 |  | note | Inspection / Test Method: Visual Inspection
label | f7d6b154-c7f7-578b-94d5-4c0ee0c96d62 |  | note | Record of conformity: This ITP signed off
label | 34c3f1c2-4acc-573a-9a81-8784c944ee5e |  | note | IP
label | 4aadfbdb-a094-5025-924a-bf67a30cf292 |  | note | Responsibility: FH Engineer / Asphalt Supervisor
date | f301b364-a24b-5c84-98e6-439a73695a15 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Ambient Conditions for Placing
label | dc2ddb79-97c2-5fa9-9acb-2c12629cf38a |  | note | Frequency: Prior to commencing paving
label | 3e91aef1-c75b-5eda-8826-80abaa3f9dd0 |  | note | Acceptance Criteria: The temperature of the pavement to be surfaced shall have a temperature greater than 10 degrees and no rain shall fall during placement of the mix and the surface shall be dry.
label | 96d75065-0d7d-5351-ab3a-386e5026271f |  | note | • Primer seal - no primer sealing shall be applied whilst the pavement surface temperature is less than 20 degrees or during wet, windy or rainy conditions, or when adverse weather conditions may prevail at any time during the work.
label | 1b48850b-4e5c-59e0-9d52-637d425ce090 |  | note | Reference Documents: C.9.13
label | a06fae9a-8218-55e4-a0de-b76b0db150f1 |  | note | Inspection / Test Method: Verify
label | fe0819b4-2441-5270-9db3-a603cff25933 |  | note | Record of conformity: This ITP Signed off
label | 3fc8b218-0cbc-591b-873b-aac91df1f976 |  | note | IP
label | 02489932-5e76-5698-9d19-e47307565cd2 |  | note | Responsibility: FH Engineer / Asphalt Supervisor
date | 60050fa6-0c5b-5c13-9ff6-5f140415ea9e |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Asphalt Placement works
checkpoint-status |  |  | checkpoint | 2.1 - Tack Coat
label | f60540c5-39ac-57f8-b9e6-46c6f2e5f59b |  | note | Frequency: Prior to commencing paving
label | b14f4600-30b1-5364-9299-18b39c8c3f8d |  | note | Acceptance Criteria: The tack coat shall consist of a diluted rapid-setting Anionic bitumen emulsion as specified. Application shall take place not less than 30 minutes nor more than 2 hours before placing asphaltic concrete.
label | 027f8410-f578-5f01-adac-28f98fbae4e2 |  | note | • The tack coat application rate shall achieve a residual bitumen of 0.1 to 0.2 litres per square metre. The actual rate of application will be selected by the Superintendant to suit the class of material.
label | 558d665b-2787-59c1-b381-e016ecc67b3d |  | note | • Any pools of tack coat which may have formed in surface depressions shall be brushed out
label | ef0e91c1-d730-5686-ae6e-80dfeef0ae25 |  | note | Reference Documents: EW-CE-DRW-406-001 EW-CE-DRW-416-001 C.9.12
label | 01a2b96b-9c01-578e-99c2-8d58a020ee96 |  | note | Inspection / Test Method: Visual Inspection
label | de10909c-2d3d-5edc-8156-978fff9d44a5 |  | note | Record of conformity: This ITP Signed off
label | f3385766-5c5b-56fc-865d-c82e55203f33 |  | note | WP
label | 52d68d31-bba3-57cf-a687-da8c721bdcd1 |  | note | Responsibility: FH Engineer/ Asphalt Supervisor
date | c9a64264-a75d-5875-9608-eb15945e205b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Prime Coat
label | b0d77d5a-829c-5342-899c-24b9d517225b |  | note | Frequency: Prior to commencing paving final layer
label | 20fe6b5a-1df2-59a3-a957-fa834a2b8953 |  | note | Acceptance Criteria: Prime coat to be applied at 1.0L per square meter
label | 6c0bb2ea-de52-54a1-85aa-d8a235ddd12d |  | note | • Primer sealing shall be carried out under favourable weather conditions and the prepared base course shall be sufficiently dry to permit adherence to and penetration of the base course by the bitumen.
label | c4c8e188-c6bb-5817-8e76-e902a67a9c09 |  | note | • Before primer sealing, the pavement shall be broomed free of all loose material and dust and any defects are to be made good. Should conditions require it, the surface shall be lightly watered immediately prior to the application of the primer.
label | c2920eec-20ea-555c-9fd0-891c1b91060d |  | note | • The primed surface shall be covered with 5mm diorite screenings at the rate of 80 square metres coverage to one cubic metre of screenings and rolled with a 6 - 8 tonne roller until screenings are firmly embedded in the primer.
label | b43a058f-388e-5466-9989-37845b3a007c |  | note | Reference Documents: EW-CE-DRW-406-001 EW-CE-DRW-416-001 C.9.12
label | 1c0f0fc8-2cb5-5382-9b48-6f7067e64ac1 |  | note | Inspection / Test Method: Visual Inspection
label | c61e0906-7a2a-5bee-8d12-70295161a683 |  | note | Record of conformity: This ITP Signed off
label | d064df48-b2f0-592f-b183-4a29625ddd03 |  | note | WP
label | 54e1c321-2653-5681-991b-39feb690bf20 |  | note | Responsibility: FH Engineer/ Asphalt Supervisor
date | c8f3e3bd-4b03-5290-b89c-ad302ce30189 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Commencement of Placing
label | 34672287-245f-54f1-86c6-4ac804512f2c |  | note | Frequency: Prior to commencing Paving
label | 30766ca9-7e97-530d-9310-2307fdcba81f |  | note | Acceptance Criteria: The placement of asphalt on the sub-base or granular base for a new pavement or for an overlay of an existing bituminous surfaced pavement shall not commence until the consent to proceed is obtained from the Superintendent
label | 12adbdde-65f2-5e9a-9de6-3bf378313d8f |  | note | Reference Documents: Work Procedure
label | c4a70600-c5a3-5bd2-bb5b-cc61d7a64043 |  | note | Inspection / Test Method: Visual Inspection
label | 43f2ed4e-6e81-542a-a9db-30f01cf26fd9 |  | note | Record of conformity: Hold Point Release
label | 0cb4c4a6-2e4b-5aa4-85dc-f67f952e9d52 |  | note | HP*
label | 6745b3d0-86a0-5651-8b33-8adaf13647fd |  | note | Responsibility: FH Engineer / QAV
date | 3da91206-9630-54df-9096-2b51f69bc520 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Delivery of Mix
label | 1489c6b8-fb14-51aa-b3a0-3f58afd2a085 |  | note | Frequency: Each load
label | 7632929e-4d53-5a21-9ad9-d47b3c9060a3 |  | note | Acceptance Criteria: The asphaltic concrete mix shall be placed at a minimum temperature of 140 degrees Celsius immediately on delivery to the spreader
label | 004e59dc-5e89-5e1e-b3af-3cd72da22201 |  | note | Reference Documents: C.9.13
label | 452f200e-2b9a-55d2-9d02-2dd437fcf17e |  | note | Inspection / Test Method: Visual Inspection
label | ec16706a-723e-5c7f-85a3-82f1cd807022 |  | note | Record of conformity: Delivery Docket /Asphalt Traceability Sheet
label | 883701c0-16d1-54c0-8a5b-f1c0bb335fc1 |  | note | IP
label | 0d8626d8-5a76-541d-ab57-c4448665583f |  | note | Responsibility: FH Foreman / Asphalt Supervisor
date | 9a5d3d94-1a47-5a18-87e1-882a81252348 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Layer Thickness and Level Control
label | 70e86356-e0d1-55aa-b879-622e5072ac48 |  | note | Frequency: Regularly during paving
label | b4e53762-5e5d-5d8a-9659-41b9aadfb89b |  | note | Acceptance Criteria: Thickness of asphalt layer conforms to asphalt thickness on drawings.
label | 9d8ee522-7a08-5a74-b5b4-f12a9c71093e |  | note | • The asphaltic concrete shall be placed in one layer by an approved self-propelled machine spreader, conforming to AS 2150, Section 12.
label | f27f7348-f0e1-51f8-a053-30ff0700e400 |  | note | Reference Documents: EW-CE-DRW-416-001, EW-CE-DRW-406-001
label | 2aee9b27-e4be-5b48-a29d-f0b1f6e6feb9 |  | note | Inspection / Test Method: Verify
label | ce5b668a-7209-50cc-ade9-3128e10f759b |  | note | Record of conformity: Dips using ruler or dip stick
label | 1b22a8f0-76f2-57d3-8312-6104efec471e |  | note | IP
label | 7fa0941c-3b8a-5ff0-ade2-8b243d0b9b56 |  | note | Responsibility: FH Foreman / Asphalt Supervisor
date | 80084584-c20a-519d-9d9a-62530071b46f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Asphalt Placement works
label | 7873c2c6-d2b3-5417-821b-b12ac2c13ffe |  | note | Frequency: Each Load
label | 9164be33-05fe-5fef-b50f-4bf7d3f23e08 |  | note | Acceptance Criteria: The temperature of the asphaltic concrete at the time of initial rolling must not fall below 120 degrees Celsius.
label | 80d5013b-fc12-5a1c-b622-6774243b9eae |  | note | Reference Documents: C.9.13
label | 8bca35d4-f7ae-5312-b7e0-e1687a4de3ae |  | note | Inspection / Test Method: Verify
label | ed23ecb4-8f7a-5eca-b5f6-62b04899cffc |  | note | Record of conformity: Thermometer
label | 309f79cc-2872-5a3e-a85d-44ff51358da0 |  | note | TP
label | dff943ac-2907-51eb-a1ff-6bc4e2a537dd |  | note | Responsibility: FH Foreman / Asphalt Supervisor
date | ab8e77a8-a3d8-5dc7-a6ea-1ba65f296613 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Surface Finish of Wearing Course
label | 040baf92-85c6-56c9-b66e-836be136ae12 |  | note | Frequency: During paving and after final roll
label | 353ef873-82da-5f90-b1d8-57d25695370b |  | note | Acceptance Criteria: Joints shall be in accordance with AS 2150 Section 12.6.
label | 69b2da6e-a357-5a4c-95ca-064faa6e6e49 |  | note | • Form any joints necessary and ensure that the finished profile is smooth and even over the joints without ridges or depressions.
label | 29126ad0-edd5-5cbe-8fe9-0c7f9b4cecf8 |  | note | • Joints shall be waterproof.
label | 6bbb5a2d-0043-5b7b-b5ff-74963a164b35 |  | note | • If the asphaltic concrete begins to shove or crack, in no circumstances continue with rolling until the cause has been determined and corrective measures taken. Keep drums and wheels of rollers wet with water and clean during all rolling operations.
label | 4ea0daed-20d9-5042-865a-bcf3b523cc0d |  | note | Reference Documents: C.9.13
label | 4ce6cecf-7975-5ecf-8449-fcfba045d7c0 |  | note | Inspection / Test Method: Visual Inspection
label | 57e8cae9-e43e-5e35-ade6-c1da418dc02f |  | note | Record of conformity: This ITP signed off
label | 5ac04877-9582-522b-aab1-b0e2d12e03ca |  | note | IP
label | 6616363f-23e2-55aa-8c15-d58c33719487 |  | note | Responsibility: FH Foreman / Asphalt Supervisor
date | b2fa31a0-dbdd-57dc-92e7-fa7dca9c2018 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Kerb and Channel
label | 6b7af1bd-4c87-5034-9fd2-2108a79ae24d |  | note | Frequency: During paving and after final roll
label | 4681f754-7c29-5d6a-bb85-5bcce4103895 |  | note | Acceptance Criteria: Where asphalt is placed against kerb and channel, The edge of the wearing course shall be either flush with or not more than 5 mm above the lip of the channel
label | ba6c7653-bd24-5f81-973a-bedaaa3ba2fa |  | note | Reference Documents: Work Procedure
label | 99ae73d5-ed7b-5964-9f9b-36738bfb9abf |  | note | Inspection / Test Method: Visual Inspection
label | 54352bee-d2fb-59fd-8898-7204cac5e3a3 |  | note | Record of conformity: This ITP signed off
label | a2d996f2-cefc-55e8-bc27-ed08542ad005 |  | note | IP
label | a4dc18e1-638f-575f-b0df-1b4814123ff2 |  | note | Responsibility: FH Foreman / Asphalt Supervisor
date | 25e8d7ad-02e6-5a8e-b755-66f439949829 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Testing and Conformance
checkpoint-status |  |  | checkpoint | 3.1 - Compaction
label | 4ddf6032-ede3-5448-8698-bd2e844fbe43 |  | note | Frequency: As Requested
label | 958b05af-768b-54a2-8b97-ca4532c773c2 |  | note | Acceptance Criteria: The density of the compacted concrete shall be not less than 97% of the Marshall maximum density.
label | 54255945-66b6-5da5-84cd-3670ea057bbe |  | note | Reference Documents: C.9.13
label | 3bcfd0d3-666f-5aee-8114-e6a28cc22f1f |  | note | Inspection / Test Method: Verify
label | 588331fe-b9e7-567d-bf60-356f92b38e79 |  | note | Record of conformity: Test Report
label | 4a2cad92-7008-5e93-9d72-4309f0769216 |  | note | HP
label | 04a618ae-51df-5d66-8099-dee73437f08b |  | note | Responsibility: FH Engineer/ Lab Technician
date | f6a566fd-7510-521c-88cc-8e7834f755f0 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - As-constructed survey and conformance documentation
label | 118a200c-e7b2-526c-be89-a8f284375d18 |  | note | Frequency: Each Lot (1 per day)
label | d34c2a7e-11ff-5727-ae00-0acaf076131f |  | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
label | fde37f6d-a7da-5500-a9b1-df86166e1001 |  | note | • Lot Maps shall include layer depth and finished levels at 20m intervals and conformation of ponding checks per lot.
label | 25411efc-ce31-5ec1-a1af-42cf1e9167b4 |  | note | ○ Tolerances
label | 2a30dea5-70d6-596f-b54b-8a8c460aab98 |  | note | • Width of prime: + 150mm or - 0mm
label | a43d59b8-d3f0-5465-af54-fadfefbc8ef5 |  | note | • Width of primer seal: + 150mm or - 0mm
label | 035b25c4-befd-5ee6-9e50-1aec883a24c3 |  | note | • Thickness: + 5mm or - 0mm
label | cd343bec-b79c-541a-9972-3c0ac4e7a6a2 |  | note | • Finished level: + 10mm or - 10mm
label | 8e2a1303-a4cc-5d36-9314-fa40ee8bed74 |  | note | Reference Documents: C.7.2 (5.), C.7.4 (Table 6)
label | fab65828-b10f-5f33-99fe-3bc3165d4735 |  | note | Inspection / Test Method: Verify
label | d587e8fd-c864-5f63-a71b-7d5a3bc7ead6 |  | note | Record of conformity: Visual match existing / This ITP signed off
label | efd47ec5-5c09-5f46-a591-5df0fa4bb28c |  | note | SCP
label | e4d0b90a-33c1-51f2-ad92-843b41e4f901 |  | note | Responsibility: FH Engineer/ Surveyor
date | 8f5678eb-2d81-5035-82ad-334603d72df1 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | cd63ed7b-6e61-56eb-8c86-73ce661165e0 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 6356b1fa-9e64-5050-b213-bc7aff4e6531 |  | textbox | Print Name:
text | e1e167e8-c176-5689-8a2e-d458c120c9fd |  | textbox | Position:
date | 1d86e99b-a3d8-547c-ac72-ad044a5c9e23 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-008 - Cast In-Situ Pits | itp |  |  |  | Yes | CTN-ITP-008 - Cast In-Situ Pits | 3d261362-b4fe-4108-af61-9a75f491599e
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check that current revision drawings are being used
label | 0365b6a6-c037-57a2-be99-9c91bdfd519d |  | note | Frequency: Prior to Commencing Work
label | e89b58a7-2fa2-567d-a948-1b26a2bb4b9e |  | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
label | 659bd08f-bf4b-5cb8-abcc-e957a8ab1fd4 |  | note | Reference Documents: IFC Project Drawings/ Drawing Register
label | 564e2dec-07c8-5e06-a8d5-37f8d2a3595b |  | note | Inspection / Test Method: Document review
label | edd0e0d8-3e9a-579a-88eb-459772ff14fd |  | note | Record of conformity: Latest revision IFC drawings, ITP signed
label | 3af84e3d-1142-51fd-957e-3a9b2628cbd9 |  | note | HP*
label | e483059b-35f6-5fdd-be37-e33fd920ed28 |  | note | Responsibility: Site Engineer
date | 3d9cea91-ff3f-54d5-b2ec-406a8133c962 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 34b600b6-c18a-5c25-9430-effbf71ef5b3 |  | note | Frequency: Prior to commencing any activity
label | 445a49cc-28c5-548b-82cb-5278af8a7129 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | de0db7b2-5c0e-5402-9181-3108cb508237 |  | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
label | 258a4831-adea-5763-93ea-2490c4901754 |  | note | Inspection / Test Method: Visual Inspection
label | 76b52c25-cb6d-5570-8ba2-fafa120dee18 |  | note | Record of conformity: This ITP Signed
label | 6fe92749-aa58-5985-8bbd-83f26c02a16b |  | note | HP*
label | 9d5a8f96-7499-592e-bee6-819b15f1fff5 |  | note | Responsibility: Site Engineer
date | ae1a3bc9-47d5-5452-a218-a801090ae931 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Material Conformance
checkpoint-status |  |  | checkpoint | 2.1 - Materials & source Approval - In-Situ Pits
label | 78bc5660-0fdc-5809-836d-0bc5f0dada14 |  | note | Frequency: Prior to works commencing, 1 per delivery
label | 8d657643-4c8b-5ed1-a6e5-eb67a8d788aa |  | note | Acceptance Criteria: In-situ Pit resources including bedding, reinforcing steel and formwork shall be as specified or as shown on the Drawings.
label | b2c5536c-b5a4-5d50-9fcc-a9bc9e80504e |  | note | Reference Documents: Work Procedure
label | e69b60fe-4d44-5c7e-b6b9-49aac3bc90df |  | note | Inspection / Test Method: Visual Inspection
label | d9cb0130-6391-5e80-a5fb-2a9b207edce2 |  | note | Record of conformity: Receival inspection checklist
label | 60ec4265-af74-53f5-8191-17a47380d214 |  | note | IP
label | 391ffe20-348d-511d-a7c3-4c89cae513ec |  | note | Responsibility: Site Engineer
date | 18312801-92a2-5882-ba09-43c1a4c197fa |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Materials & source Approval - Pit Covers
label | e305522b-c8a3-5927-ae7c-75369a39a1e0 |  | note | Frequency: Prior to works commencing, 1 per delivery
label | 6a0f3106-68a3-53c5-81d4-787904036d92 |  | note | Acceptance Criteria: Pit covers shall be either cast iron, precast concrete covers or gratings as per drawings and shall be constructed and fixed to pits in accordance with relevant Tasmanian Standard Drawings
label | c5ead115-c7b3-5e87-a6c2-8aabdee0ff39 |  | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.16
label | 289e1789-c3c2-57f0-a6ca-6f23f60391b4 |  | note | Inspection / Test Method: Visual Inspection
label | 2c2dce49-982a-54a4-a12c-ba71854786fa |  | note | Record of conformity: Receival inspection checklist
label | eaab9bf1-ae95-5e15-a67b-47da04235614 |  | note | IP
label | 3fac8975-5487-5b4e-968f-73d69fc196bd |  | note | Responsibility: Site Engineer
date | 515034ed-99d1-59d8-ab1f-c68a93f9bd89 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Materials & source Approval - Step Irons
label | 65e96e82-0d24-5196-a92e-e16059a6c6f5 |  | note | Frequency: Prior to works commencing, 1 per delivery
label | 3a62b53a-a48e-5136-bd26-7436e032b9b9 |  | note | Acceptance Criteria: For pit depths greater than 1200mm, provide 24mm galvanized hot dipped step irons or approved equivalent at 300mm centres measured from top of cover to invert level of the base as detailed on the drawings and in accordance with AS 1657-1992.
label | d5a967d2-7518-54e8-9275-a01dbb2c9cd5 |  | note | Reference Documents: EW-CE-DRW-526-001 C.5.17
label | fc69f96f-2253-5881-9183-1330edc5a7ed |  | note | Inspection / Test Method: Visual Inspection
label | c7075238-6ab8-598e-a25f-ffb4e674e301 |  | note | Record of conformity: Receival inspection checklist
label | a0ed7d01-4073-581d-a236-af5843744206 |  | note | IP
label | 59c9ae3d-d853-54b8-be15-7c916649bc73 |  | note | Responsibility: Site Engineer
date | 3c827b71-5c8e-5125-a31a-5714a6bcdca9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Source In-situ Pit Material
label | 4883883a-9faa-5b7f-84fc-e63292ae10a0 |  | note | Frequency: Each Lot
label | 075b6b48-4865-5d90-95fe-d1d01a436e3b |  | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation.
label | 3fb56b68-d59e-5bcc-aa1d-fd9257a9cbb1 |  | note | Reference Documents: C.5.15
label | 83891436-6977-5602-aad7-758dd6536e82 |  | note | Inspection / Test Method: Verify
label | daaabeee-44e3-5f4d-b2f1-0bddf93f5134 |  | note | Record of conformity: Mix Design
label | 38b9df4a-1575-5f01-ad5e-d75bb4e80740 |  | note | IP
label | b5077ca5-2cc2-5f0b-afc8-8eeda1c21504 |  | note | Responsibility: Site Engineer
date | 7d74da3a-b778-599e-83b2-74949656aa59 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Construction \ Erection of Formwork
checkpoint-status |  |  | checkpoint | 3.1 - Pouring Concrete
label | f7e59120-61dc-57a1-b5b6-bdad6c7dc312 |  | note | Frequency: Each Lot
label | 1a14eec7-047e-5ef6-a41c-8f1c089d899a |  | note | Acceptance Criteria: Excavation depth shall be as per specified or as shown on Drawings to accommodate structure including blinding layer / bedding.
label | e06266d2-c00a-5beb-93f6-ad5bfb50e1f3 |  | note | • Excavations for pits shall be trimmed neatly to size so as to give the exact thickness of walls as required.
label | a5ea8aaa-fec0-5557-9d75-10285e191ed6 |  | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.15
label | 5a25f090-ad2f-5a0b-b45a-848d5c4a767a |  | note | Inspection / Test Method: Verify
label | c2462ab3-5b10-5e29-bb99-eeda63e53b13 |  | note | Record of conformity: This ITP signed
label | a6bb2625-c262-50d3-a4a8-993993250d63 |  | note | IP
label | e0451ab0-38e0-51d0-8ab9-6ab48c4378ad |  | note | Responsibility: Site Engineer
date | d61e690f-c5a4-50f0-a236-580732840987 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Bedding
label | 15327582-5012-51ec-a0bc-12b3fb365f4d |  | note | Frequency: Each Lot
label | 1300c008-15b4-53c6-b9f5-f077c5e0358d |  | note | Acceptance Criteria: Pit base to be poured on 75mm min. depth of 75mm Class 3 FCR.
label | 81324bf5-d8b8-5fc9-8c1a-75bd526ec12a |  | note | Reference Documents: EW-CE-DRW-526-001 C.5.15
label | 138a9d78-2827-5d62-94a8-09a7e66f0f9e |  | note | Inspection / Test Method: Inspection
label | 427ed76f-6654-57c3-ba61-23107ed56a42 |  | note | Record of conformity: This ITP signed
label | 0068725e-e32f-5648-819e-0626a549caa5 |  | note | HP
label | 622cb62a-d361-50d4-a2d4-6d6c50ce3de3 |  | note | Responsibility: Site Engineer
date | 49544b50-50a2-57c2-b50b-ac4d30a5f255 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Formwork
label | c657f43e-ddcf-5256-ac3a-082bc3c3c810 |  | note | Frequency: Each Lot
label | c8dda0be-9771-5b9a-97da-e5e16b0bc158 |  | note | Acceptance Criteria: Formwork shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
label | 81b1dd80-4b77-5b72-b2a1-adc0538d80eb |  | note | Reference Documents: Work Procedure
label | 993b7855-3fd3-510b-abb6-541e68739108 |  | note | Inspection / Test Method: Verify
label | 97531949-31f9-502e-8789-c45f76534a3e |  | note | Record of conformity: This ITP signed
label | e7b0d00d-b1a3-53d3-a2d3-51444453332c |  | note | IP
label | 95150586-97dd-58bb-b0e9-4527529be88c |  | note | Responsibility: Site Engineer
date | 54145665-5e40-503e-8844-346910bae352 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Subsurface Drainage Accomodation
label | 757bd975-c34b-5ad3-83bf-4f93ee72f47d |  | note | Frequency: Each Lot
label | 68bad9af-0468-5d4c-924b-d6a65dbdebb6 |  | note | Acceptance Criteria: Form holes in walls to accommodate subsurface drains as directed.
label | 887cd8ab-8329-5976-9c5c-e56ee11d3330 |  | note | Reference Documents: EW-CE-DRW-526-001
label | dc5e7794-3b27-596b-86b1-235333a3ef3a |  | note | Inspection / Test Method: Inspection
label | 8c88fdee-edf8-5b99-91bd-4a61d5da686e |  | note | Record of conformity: This ITP signed
label | 70a5d4b4-b735-5610-8319-8c41b4027a81 |  | note | IP
label | d01790a4-ab2c-5563-9153-e3a19d59439d |  | note | Responsibility: Site Engineer
date | 9659077f-abc5-5e0b-b0eb-1cdd497846bf |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Reinforcement
checkpoint-status |  |  | checkpoint | 4.1 - Steel Fixing
label | eeee8823-9d67-5e9b-b073-b20ee38d4354 |  | note | Frequency: Each Lot
label | 0b9a3a64-9ea4-5114-bfc0-5f946288601e |  | note | Acceptance Criteria: Reinforcement type and design to be in accordance with reinforcement schedule on DRW-526-001 with a 300 min. lap
label | 635cf359-f8cd-5087-8dd3-58fe7e26e809 |  | note | • Reinforcing steel shall be bent and placed in accordance with AS 4671 and sufficient bar chairs shall be installed to ensure reinforcement is in the correct position.
label | 8b02a1f5-def8-5582-8d3a-d8f6e4b739a4 |  | note | Reference Documents: EW-CE-DRW-526-001 Work Procedure
label | 613798ce-33ea-5c8f-9e51-19988aa97019 |  | note | Inspection / Test Method: Verify
label | 86edfd3e-0311-5cbd-aeb5-404b2a8fc6ed |  | note | Record of conformity: This ITP signed
label | 7bfdfb93-83fc-5212-8148-d0bb0e88800b |  | note | IP
label | 08b146db-10ca-55a4-8941-9373857e3289 |  | note | Responsibility: Site Engineer
date | 8c07ca2b-aa42-548b-a6a1-ad6f483bf81f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Reinforcement Installation
label | 9a7a144e-cfff-56f0-bdf1-856b22bb602b |  | note | Frequency: Each Lot
label | 8068037c-eb2b-57ea-8c14-4b3eb384d7a0 |  | note | Acceptance Criteria: Pre-pour Checklist Completed:
label | 60eb353f-2537-58a1-9365-8834bb8c4d04 |  | note | – Position and spacing check and recorded
label | cf7b997f-0901-5370-b566-f022475cb4d4 |  | note | – Cover checked and recorded
label | 22ccfda4-0ce2-5ff0-af9a-b274498e00ac |  | note | – Reinforcing supports checked and recorded
label | 06b7b196-5092-5e95-84ef-b8bc8885ab14 |  | note | – Laps at required length
label | c40bf909-026a-5d8c-b1c8-b812be8a5871 |  | note | Reference Documents: Work Procedure
label | b781bf42-a6c8-5c77-b39a-88e91a98b088 |  | note | Inspection / Test Method: Inspection
label | 1c4ccef3-7ec3-59af-a434-b02afb138d04 |  | note | Record of conformity: This ITP signed
label | f0f17a7b-12d1-5ec9-8d33-1d25df694f45 |  | note | IP
label | d581b896-2e80-50b5-84ad-f2e5c5ed1cf4 |  | note | Responsibility: Site Engineer
date | f82a45ba-47da-543b-892d-01ab7876eb32 |  | date | Date Completed:
checkpoint-group |  |  | section | 5 - Inspections
checkpoint-status |  |  | checkpoint | 5.1 - Pre-pour Inspection - Pit Base and Pit Walls
label | ed9d8a6e-d8ab-5762-b2ec-0be0c339e6e7 |  | note | Frequency: Each Lot
label | 2c842551-3836-5b1d-a64e-3f29062f9921 |  | note | Acceptance Criteria: Concrete shall not be placed until:
label | b60054a3-c4bb-594a-b0a2-fbeea42fa1dd |  | note | (i) the evidence that the forms, reinforcement, any stressing materials and embedments conforming to the requirements of this specification and the drawings, has been reviewed by the Superintendent
label | 0c984e5c-149b-50c0-9908-8a806ca8cb6e |  | note | (ii) all foreign material has been completely removed from the forms
label | 91fd72d8-359e-5742-a3b7-4b12333ba65a |  | note | • Superintendent requires 48 HR notice for inspection.
label | 2edbf3dc-194d-5deb-b686-28e3dba5ab93 |  | note | Reference Documents: C.5.15
label | cab9c703-2dbf-535d-988d-054cf7fd428d |  | note | Inspection / Test Method: Inspection
label | 5beb74a9-af76-5e25-b22d-bd885fbaefaf |  | note | Record of conformity: Pre Pour Inspection Checklist Completed
label | 65422e32-b8f5-5ddf-92a0-e04f05253c19 |  | note | HP
label | 8acd1511-f7e9-59d5-bbac-a41843d30a85 |  | note | Responsibility: Site Engineer/ Superintendant
date | f700bc1c-870a-5073-b8b1-f3799a1f5f93 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 6 - Placing and Finishing Concrete
checkpoint-status |  |  | checkpoint | 6.1 - Pour in-situ Pits
label | 0f7ba03a-0539-5f65-a2e7-5ee4ea6f77a2 |  | note | Frequency: Each Lot
label | 7c11a96f-889d-50b6-8c31-a5537520709c |  | note | Acceptance Criteria: Pits shall be constructed to the detail shown on the drawings
label | 646658d8-9eaa-5849-90b7-68ade124e813 |  | note | Reference Documents: EW-CE-DRW-526-001
label | 2e3b37b5-a5b2-56c5-a751-266d436b85f7 |  | note | Inspection / Test Method: Inspection
label | ea15e7cb-7d25-5a58-a627-64109b2f0c83 |  | note | Record of conformity: Concrete pour record and delivery docket
label | e90afb25-ccca-529b-ab25-7f164cad70b8 |  | note | HP*
label | 2df0c5c1-6dc8-54cd-b417-25670dae22eb |  | note | Responsibility: Site Engineer
date | f56ea57e-5869-5dff-9f26-a8ec9afa0bc3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.2 - Finishing
label | 4d37c0f4-a012-53cc-b8d5-558453d4a213 |  | note | Frequency: Each Lot
label | d1117932-317b-524b-8529-9e44ea965563 |  | note | Acceptance Criteria: Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces
label | 74a1aeef-fd7c-5f9e-8fe8-98c70316a46b |  | note | • Concrete surface finishes to meet Class 4 requirements as per table 3.2.3 and 3.3.5.1 of AS 3610. (Attached Below)
label | 2b79d422-9352-53ce-bd18-bd9baf30d57a |  | note | Reference Documents: Work Procedure
label | a9f9bada-a56a-51af-b7dc-c7e89e8a1f30 |  | note | Inspection / Test Method: Verify
label | 4a94cbcf-17ad-5de1-b04a-59fdabb45c79 |  | note | Record of conformity: Completion of prepour inspection checklist
label | 88583bba-a322-58ff-9c4d-0b78b103d50a |  | note | IP
label | 67c7f229-1fe4-5bc9-a7ec-4a5d1dd0e79e |  | note | Responsibility: Site Engineer
date | 34bc0954-085b-514f-b271-7e3ed0a548c9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.3 - Installation of Pit Cover
label | 0988c0ba-6bdd-5c25-b7ec-25a6aed343be |  | note | Frequency: Each Lot
label | d2ed28ee-5709-570f-b86f-ebea91d68f7f |  | note | Acceptance Criteria: Precast concrete cover or cast iron concrete infill SEP cover to be installed as scheduled
label | 43ccdd4c-fa69-584c-b963-cc9f7796b54e |  | note | Reference Documents: EW-CE-DRW-526-001
label | 191875fd-1240-53fa-9bd4-717ab164940d |  | note | Inspection / Test Method: Verify
label | e8f510f9-89f9-5c2a-84f8-04f2d476ed27 |  | note | Record of conformity: This ITP Signed
label | 69a8532d-b34b-5d21-a696-d3d2d9b4cc72 |  | note | IP
label | b286b0eb-cf3c-5f4f-b94e-4cb3fcf8b003 |  | note | Responsibility: Site Engineer
date | de756b69-a7c6-5d3b-a11a-91054e6c9dc9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.4 - Concrete Testing
label | 1963fe79-9063-5a80-8d59-5d05c58ec1b0 |  | note | Frequency: Each Lot
label | 8994b029-6f29-531d-afae-da868e8e31d6 |  | note | Acceptance Criteria: Concrete Testing to be carried out as per specifications. In AS 1379
label | 6d96152c-9204-5367-bb94-a3ff95410e70 |  | note | Reference Documents: Work Procedure
label | 12e2aeab-d7f7-5680-bfe8-02bc856ea54c |  | note | Inspection / Test Method: Verify
label | 6883c5ff-83b3-570c-b10b-161fe79f7a65 |  | note | Record of conformity: Test Results
label | 73934e9d-3833-5e71-bed1-50089520717d |  | note | TP
label | 2ec7aef6-d926-5908-8774-9028cbcf451e |  | note | Responsibility: Site Engineer
date | b3c86552-5985-539f-91be-211e64380d8d |  | date | Date Completed:
checkpoint-group |  |  | section | 7 - Post Pour Details and Inspections
checkpoint-status |  |  | checkpoint | 7.1 - Concrete Curing
label | 564d6a88-73d8-57d2-9438-7334917cae60 |  | note | Frequency: Each Lot
label | 50c375ce-a080-58c4-938c-01dbc0a634b5 |  | note | Acceptance Criteria: Concrete to be cured as per project specifications
label | 0de7bfa9-e192-5529-ad31-e51ba3a6294c |  | note | Reference Documents: EW-CE-SPC-000001
label | 328652d3-0635-5f4d-84c2-22921ad54858 |  | note | Inspection / Test Method: Verify
label | b90db286-28de-57bd-909f-2ea6dba6c4c8 |  | note | Record of conformity: This ITP Signed
label | 574f0000-e60f-5142-84e6-2909e8e56e93 |  | note | IP
label | 9dc3dd8b-75e4-5f5f-930f-327a7a539253 |  | note | Responsibility: Site Engineer
date | a2320189-cd34-56aa-9562-41d62fa02f25 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.1 - Removal of Formwork
label | 9ab6cec4-c9db-5cdc-9847-87cb5a14dc71 |  | note | Frequency: Each Lot
label | 884dff44-6006-5a9e-984c-cd181609d329 |  | note | Acceptance Criteria: Stripping of vertical faces in accordance with AS 3610 as per Table C2. See Table C2 Below.
label | 7e0ba4cf-530c-56d8-bec9-ac1dd47a8ded |  | note | – – – – – – – – – – – – – – – – –
label | 2184b3fd-3fd6-5f3c-a7db-e79feb35adac |  | note | Table C2 Vertical Face Formwork Minimum Stripping Times After Casting
label | d47a2b6d-770b-5601-8ad3-afd24511d61f |  | note | Classification ¦¦ Average temperature (Greater than 20°C \ Between 12°C and 20°C \ Between 5°C and 12°C)
label | a8613d10-3d1b-5afa-a8da-1eaceefa6ade |  | note | – – – – – – – – – – – – – – – – –
label | 83860127-7c51-56f6-9caa-a84e48464915 |  | note | Class 1, Class 2 or Class 3 (see Note 1) ¦¦ 1 d \ 2 d \ 3d
label | 9c3579ba-cd4b-59f2-806d-27173f72bff6 |  | note | Class 4 or Class 5 ¦¦ 9 h \ 12 h \ 18 h
label | 82a5e0b1-f046-55aa-817e-e7a982c37697 |  | note | All ¦¦ A minimum of 1 d applies to the stripping of vertical faces where frost damage is likely
label | bfd21f43-16f4-5050-8fa2-0ceef25fdb59 |  | note | – – – – – – – – – – – – – – – – –
label | 359667b5-6db1-534a-96b9-4a1a6917c8d8 |  | note | Reference Documents: AS 3610
label | f3a83aa9-7c3d-5caa-83bb-f4366fc6269f |  | note | Inspection / Test Method: Verify
label | 4f48d622-0a1e-5b20-94fb-2a336cc00b6a |  | note | Record of conformity: This ITP Signed
label | c4971835-dd80-5971-aacb-e079b7ed5511 |  | note | IP
label | 5b51fb25-1d19-53bb-a871-541e2929b0c6 |  | note | Responsibility: Site Engineer
date | 689a8f5e-b7ac-5ec9-bc52-e31369d9cbce |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.2 - Allowable Tolerances Level & Alignment
label | ba6d0b14-b278-5a5f-9ab3-525c2ed35adb |  | note | Frequency: Each Lot
label | bc3dedf4-4047-5d67-a87b-54028d64fc1f |  | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
label | 0d4e56f9-897e-5ac7-bad3-d25cfb98f22c |  | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
label | d3165258-4a55-5e4b-bffd-707d81755790 |  | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
label | 453fb24a-3996-51ec-9ade-86e681e47b0e |  | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
label | b00d282c-1e91-5a73-ae0d-c4edf3611356 |  | note | • As-built survey completed for lot
label | 58c08823-90df-5039-a4da-f8b427a6cb27 |  | note | Reference Documents: Work Procedure
label | 18508920-f90c-553b-947a-27de3f6b6a07 |  | note | Inspection / Test Method: Verify
label | fdcd48ef-084f-556c-aab5-52234d8b7bcb |  | note | Record of conformity: This ITP Signed
label | 7a4c303d-66f6-5b92-bf50-c35ad3a2da97 |  | note | SCP
label | 8c381c18-79e8-5c1e-bdbb-d7ac0c76c2d2 |  | note | Responsibility: Site Engineer
date | acb22d1d-34f9-57e5-a8c4-88277a8397dc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.3 - Post-pour Checklist
label | 3afd463d-7e2f-5d70-b32f-acf74b3adac3 |  | note | Frequency: Each Lot
label | 78eeab88-43ba-58b8-87fc-6b01416a7ffd |  | note | Acceptance Criteria: Completion of Pre Pour checklist quality checks.
label | adde86a2-5147-5a5a-b04f-4ad8ba70f54e |  | note | Reference Documents: Work Procedure
label | 6ccd0e60-a526-56af-97dc-986b19c2a74d |  | note | Inspection / Test Method: Inspection
label | 9dd1fb26-0109-591c-a267-8cacbca3462a |  | note | Record of conformity: Pre Pour Inspection Checklist Completed
label | f6d75671-fecc-5894-940c-2a25f9bbe0da |  | note | HP*
label | d08e2db1-5f1d-50bb-a1d9-613685b3f0a3 |  | note | Responsibility: Site Engineer
date | 4d3f48da-cfb9-56da-bfb3-d48595ca22f4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 7.4 - Backfilling Around Pits
label | 523cbb36-7c7a-5b84-9235-6dba39442c7e |  | note | Frequency: Each Lot
label | 97194e9a-2394-54ba-9835-637f2c1a7e8d |  | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
label | 3b18ca04-e98d-5d77-92da-69dbd877e073 |  | note | Reference Documents: Work Procedure
label | 105c3c0c-9098-5b88-88ce-66dfe70343f7 |  | note | Inspection / Test Method: Inspection
label | f1a2eab1-ea9c-5230-aff6-853f28577b72 |  | note | Record of conformity: This ITP Signed
label | 2fa906c4-de20-5723-8911-a728142552b2 |  | note | HP*
label | 37f97d81-7d07-5cfe-b43f-6f9ed3d447e0 |  | note | Responsibility: Site Engineer
date | 8b41a2ad-cf70-5169-ae9b-06105eb305aa |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | d277cf9b-cd91-5a03-9d2d-932e4d3743fa |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 15d0984c-9276-5e59-9e7f-438d03d3d3f0 |  | textbox | Print Name:
text | af3961af-08ce-5798-ac9c-b9c92d02a77c |  | textbox | Position:
date | a3b35eed-ade2-545e-9289-e8e489c5c55b |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-009 - Unbound Flexible Pavement Construction | itp |  |  |  | Yes | GT4-ITP-009 - Unbound Flexible Pavement Construction | 4e3f6c53-b448-45dc-9cc1-2d96357d3dfa
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 5d7153d0-06d3-5aba-977b-fcad662e3e61 |  | note | Frequency: Prior to commencing any activity
label | 083bfe36-24c0-52e2-af90-7df9d913a036 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 0ee5686d-51fa-58d8-baa1-3369105cc36a |  | note | – using the correct and complete set of drawings
label | b4e78189-d8ba-56dc-93b9-0a67a6d0ae99 |  | note | – all drawings are the latest revision
label | 3ceb4fde-58cf-594e-9fbf-cb7531e8bfb1 |  | note | Reference Documents: Drawings and drawing registers
label | 4e740a8f-6218-5231-907e-bb6282bbd531 |  | note | Inspection / Test Method: Visual inspection
label | cc60060c-ee12-53d2-9de7-edeaf22d00b9 |  | note | Record of conformity: This ITP signed
label | 1d562dc1-8f26-5068-8eb7-38bb39865020 |  | note | HP*
label | 1c3eace7-8660-5930-ac2e-f007500f1afd |  | note | Responsibility: Site Engineer
date | 1d3fafe8-d524-5b84-bbd3-7b27c22d2dfd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | d38902b3-c4ee-5f2c-ba83-9404f3f22eb0 |  | note | Frequency: Prior to commencing works
label | 1d141e00-3c06-570c-a420-7bf41da8b407 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP`
label | e64051db-3586-5ee9-a089-f7a16a4ea596 |  | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | 8b4209a6-64f2-5aef-a4de-ee52c8b5fec2 |  | note | Inspection / Test Method: Visual Inspection
label | 909a61bb-5296-5a50-9054-c636029ce637 |  | note | Record of conformity: This ITP signed
label | 68658650-be52-5cf8-99d5-e8e62e047bac |  | note | HP*
label | a442c38b-2105-52db-a87e-f790e7266638 |  | note | Responsibility: Site Engineer
date | 8cc2f8ac-8b1f-59d2-a053-6ac1b054a93f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Plant and Equipment
label | 1b2a2f4a-9558-5961-a81d-33e6e60e37d1 |  | note | Frequency: Prior to commencing works
label | 178b7060-f162-5a6a-9fbc-53ab2d502d36 |  | note | Acceptance Criteria: Plant and equipment used in the Works are appropriate to achieve specification requirements and is inducted
label | 222decf0-50fc-5c77-ba0c-fd7b7fd08208 |  | note | Reference Documents: N/A
label | ba9b9516-61f6-53e7-96e0-470cc9437f92 |  | note | Inspection / Test Method: Visual Inspection
label | a4402dfb-4c2f-5529-8142-79cb35100197 |  | note | Record of conformity: This ITP signed
label | fc7ec349-d2fa-557e-87f7-42df68a7e205 |  | note | IP
label | 495969cf-d0af-54d6-b454-e8d4fbb4df22 |  | note | Responsibility: Site Engineer
date | 20a119a2-7a72-5d9a-9bf7-2b1f428228b5 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Placement
checkpoint-status |  |  | checkpoint | 2.1 - The commencement of construction of base and subbase
label | 7547365d-0343-55a8-b69d-b68f34f0db87 |  | note | Frequency: Prior to placing subbase
label | 6919dfe3-3169-5db8-8974-d3bd38013a5f |  | note | Acceptance Criteria: After the sub-grade has been compacted to approval, the crushed rock shall be spread in even layers of 150 mm maximum loose thickness.
label | ab957727-11b0-5c96-868e-175ad36fc63c |  | note | • The material shall be spread to produce the required consolidated thickness by means of approved mechanical spreader. The material shall be maintained within +/- 2% of OMC, with additional water being added if required during compaction.
label | 4e94ff1c-1eed-5019-b8cd-049d8637d64e |  | note | • Materials shall be spread without segregation of large and small particles, between approved edge boards or kerbs
label | 5119fed7-18ae-53cf-b7e6-be208c622b9d |  | note | Reference Documents: C.9.2
label | 6abff012-91a0-5658-aa79-4446a9d23962 |  | note | Inspection / Test Method: Verify
label | fc2255e0-a818-58e1-ad54-59e792c9af43 |  | note | Record of conformity: This ITP signed
label | 0e196c73-4e93-5792-bad9-b6aff05012ed |  | note | IP
label | a5619475-53a5-5b2e-b96b-edd7089162db |  | note | Responsibility: Site Engineer
date | 44779ffd-dd9c-5210-a527-9fc82c36f27d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Shape
label | fdc9e166-f1f8-5acc-88b5-d54efc610f17 |  | note | Frequency: Each lot
label | 4d5daa71-d0a4-5655-8cbf-baa97d1b8bfb |  | note | Acceptance Criteria: Rolling shall be performed in such a manner as to eliminate bumps and irregularities with the finished surface true to the required grades and cross-section.
label | ba014ccd-d73d-5831-a9f7-9092a5254738 |  | note | Reference Documents: C.9.3
label | f37f83ca-8997-5b14-a0ae-849ee0156655 |  | note | Inspection / Test Method: Verify
label | 72036ee9-e9e3-5721-a9f9-322868c7c4ab |  | note | Record of conformity: This ITP signed
label | a1ee398f-7fc3-524c-9887-46a8c9018a36 |  | note | IP
label | 22fa975f-f758-5441-a1b7-8f5f74aec7c5 |  | note | Responsibility: Site Engineer
date | 4dbac5f5-9c48-51b0-9cf6-c477789b7876 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Delivery Dockets
label | 343d4a9d-f604-506f-9be9-b67d4a7c7bff |  | note | Frequency: Each lot
label | ba02b1db-04e0-51c5-950e-a50fc67a8230 |  | note | Acceptance Criteria: Where material is scheduled for measurement by loose volume in delivery vehicles or by mass, a delivery docket for each load shall be issued to the Superintendent at the point of delivery.
label | 5fc4c725-1e3e-5dd3-bff3-50033d239635 |  | note | Reference Documents: Work Procedure
label | f785085e-b3ea-5894-b110-83ac0bf0fbc4 |  | note | Inspection / Test Method: Verify
label | 51e7a359-e385-53b2-9787-dfe558595d05 |  | note | Record of conformity: This ITP signed
label | 97eed60c-adbc-5ea4-929c-906899412b03 |  | note | IP
label | c8b8d687-96c9-52fc-9176-2c9144a9940c |  | note | Responsibility: Site Engineer
date | 2ea5c327-1224-5a4b-b474-381da9e609ba |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Layer Thickness
label | 18250d0e-cc1e-5688-9353-b2f83d416409 |  | note | Frequency: Each layer
label | c6dfd75a-9340-5041-a941-a1766665378f |  | note | Acceptance Criteria: Material is to be compacted to the overall thickness shown in the drawings (dependent on pavement type),
label | dff2ba0d-decd-5228-b389-7b4e7b6a7270 |  | note | • Subgrade to be within +5mm or - 30mm of design
label | 0d8a9525-ed70-5983-b38e-6afd96a9e54e |  | note | • Subbase to be within + 10mm or - 20mm of design
label | c5ce51b4-71aa-599c-a06d-ca2e78d2dc0e |  | note | • Basecourse thickness to be 0mm from design level
label | 17d69759-c720-5fa4-bbe4-2827af4b3c3a |  | note | Reference Documents: EW-CE-DRW-406-001, EW-CE-DRW-416-001 C.7.4
label | 44a66ea0-cc27-51f7-8014-0246794459b6 |  | note | Inspection / Test Method: Visual and Measure
label | 473fb4d0-b23b-5e7c-82a6-b7cb9d1f66a1 |  | note | Record of conformity: This ITP signed
label | b2f0503e-c9b1-53ce-a90f-764155affc7e |  | note | IP
label | 8022c632-010f-5954-8caa-232137d587ad |  | note | Responsibility: Site Engineer
date | cee956c6-af85-51ee-b08f-6b48530a8985 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Conformity with Drawing
label | 3645555e-d656-527d-9c52-b21bbf9bd664 |  | note | Frequency: Each lot
label | 85afdc98-0c27-5ea9-8701-caec2b0f7a50 |  | note | Acceptance Criteria: Width of each side of the pavement shall not be less than the specified offset width or more than + 300mm outside the specified offset width when measured at right angles from the centre line or design line.
label | f44609dd-a978-5935-b968-f4b577a22b8b |  | note | • Where pavement is to be constructed to the lip level of kerb and channel, it shall be constructed flush with the lip of the channel or not more than 5 mm above.
label | 3abfb819-e671-5e13-8a53-90feb7148345 |  | note | • Any material that has been compacted and then trimmed from the compacted surface to conform
label | 1ecd84e3-bd6d-5d98-957a-5b1ca6df3896 |  | note | Reference Documents: C.7.4 Work Procedure
label | 250d4534-1193-51c8-bb5d-b641bb25fb9d |  | note | Inspection / Test Method: Verify
label | 728ab8e6-3451-5443-aac8-3c847ba20cb0 |  | note | Record of conformity: This ITP signed
label | 00f6d732-6f88-5094-a239-66fe73c27a22 |  | note | IP
label | 03583a0e-12fc-5295-a033-e776c65c613c |  | note | Responsibility: Site Engineer
date | c3c71ca2-315f-5d66-836e-8b87daf407b5 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Jointing
label | 05e7f53b-a6ae-568b-97d5-155c4d27f0cd |  | note | Frequency: Each lot
label | 679214b8-b98d-50be-907d-44361360264f |  | note | Acceptance Criteria: (a) material shall be spread in such a manner as to minimise the number of joints
label | a2beea88-4093-57e4-ba43-03c7618a5a09 |  | note | (b) transverse joints shall be offset from one layer to the next by not less than 2m
label | 9581cf83-7fc9-51c9-ac7e-88719d417988 |  | note | (c) longitudinal joints shall be offset from one layer to the next by not less than 150mm
label | 7bbb8a42-5220-5a6e-8c66-51ec71f0d192 |  | note | Reference Documents: Work Procedure
label | 45cf0f0d-ef8b-56bf-b5e1-796d423c66f5 |  | note | Inspection / Test Method: Visual Inspection
label | e60a148e-9e0d-5d54-8fad-ad1fe141ed38 |  | note | Record of conformity: This ITP signed
label | cc45eeeb-5906-518c-9acd-4d66e172d02b |  | note | IP
label | 42b6048e-51d9-50a7-b8ff-e380da0ef775 |  | note | Responsibility: Site Engineer
date | 977927b9-5d9c-50cb-aa29-c7802bd5ebe0 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Testing and Conformance
checkpoint-status |  |  | checkpoint | 3.1 - Test Rolling
label | c52ead6f-d0e9-568e-b476-24f9ee2c19f2 |  | note | Frequency: Each lot
label | a9f96e39-c692-533f-a43d-ac9640254b4f |  | note | Acceptance Criteria: All pavement layers shall be compacted to withstand rolling and shall be test rolled in accordance with table 5 of section C.7.2 prior to acceptance of the layer.
label | 7457d6f1-b3bb-5c35-a8f3-e84af6ab44de |  | note | Reference Documents: C.7.2
label | 0cd5df29-373c-5b8a-86ae-95cc9dc4cef3 |  | note | Inspection / Test Method: Test Roll
label | 3da7c3ab-d777-50b6-b177-16bae9e5234f |  | note | Record of conformity: This ITP signed
label | b9180274-5ee7-5f4c-a302-e7b4f7c0060e |  | note | HP*
label | 91bfda13-5019-54ba-b01e-96fa8232e55e |  | note | Responsibility: Site Engineer / QAV
date | 9bcc95f5-f74c-5812-bdca-b08b22b550eb |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Compaction of road pavement
label | b6518bcf-656f-54ef-bf33-93b03ba6e8f4 |  | note | Frequency: Every Lot
label | 16a9c3ac-274c-5bcc-b4cf-af9ac0c24643 |  | note | Acceptance Criteria: The minimum compaction achieved shall be 100% of the Standard Maximum Dry Density in the base course, and 98% of the Standard Maximum Dry Density in the sub-base course
label | f04a9f57-a3e4-5fd2-b100-39f41e865835 |  | note | Reference Documents: C.9.4
label | 9502033d-f1e6-5f6c-a8d6-989ff65a84db |  | note | Inspection / Test Method: Test point
label | 47858a3a-188f-5c5d-9cdb-e3fa81abab9f |  | note | Record of conformity: This ITP signed
label | 25998cf0-0b2d-51a5-bd34-394150fed969 |  | note | HP
label | 53c9c37c-e6c6-5b7d-8b29-e53e69d66eb4 |  | note | Responsibility: Site Engineer
date | 5a5e1859-6dbc-5bef-8315-0ffe11b2f9b3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Completed Surface Level Compliance
label | 7e7d67ab-8110-5a52-8b11-e947531e8c3f |  | note | Frequency: Each lot
label | f91f31a4-bc0e-5e14-83c7-cedddae76e84 |  | note | Acceptance Criteria: Surveyed as constructed drawings to be provided showing finished contour levels.
label | dcdddc75-76fe-5d53-865f-8b8c54f99693 |  | note | ○ Spreading, scraping and consolidation of the various layers of the pavement shall proceed with each layer having a construction tolerance of;
label | f3a9ecd3-9a7e-547f-88ed-155851f060ba |  | note | • Subbase: + 10mm or - 20mm
label | 9fa23e74-f609-5296-b7a4-87a609fd1a92 |  | note | • Base: + 10mm or - 10mm
label | 31236767-a5d9-57c3-9c32-4d49b8730406 |  | note | Reference Documents: C.7.2, C.9.4
label | 3ebf6f52-987b-53f9-8a98-3579db58b654 |  | note | Inspection / Test Method: Survey
label | 3b34e359-19d9-5c42-a06f-0a18f5f9b558 |  | note | Record of conformity: This ITP signed
label | a8761064-e118-56e5-a7c8-d620a04958a0 |  | note | SCP
label | 77c0a8d2-86dd-5d39-98fd-4259714a806d |  | note | Responsibility: Site Engineer
date | 09eca7d5-28ce-5a6f-a1d7-29f54c6e5267 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Shape
label | 80a7da86-ac57-5f7d-9a43-af824c70b44c |  | note | Frequency: Each lot
label | 0fd39ec2-056e-5caa-bbbe-dc635d6b6156 |  | note | Acceptance Criteria: Layer to be finished to a smooth and uniform surface and after compaction and meeting the following tolerances:
label | 3d828167-f185-56fb-8fdc-18a89cf4b94b |  | note | • Crossfall: + or - 0.5% of design
label | 7b34c6e6-bc24-56b6-a6b7-6b2bae36ec06 |  | note | • Surface: + or - 15mm when tested with a 3m straight edge, laid in any direction.
label | 22623f6d-13a8-5005-8aff-bc2bd00dc0f3 |  | note | • Longitudional Grades: The gutter grade shall be + or - 20% of the design grade.
label | 64834a3f-7987-5508-a5c6-1589fbc01935 |  | note | Reference Documents: C.7.4
label | 39725ee5-72fc-5dee-b36f-ab41ab6f8e7b |  | note | Inspection / Test Method: Test Point
label | 8fb8f3a7-e478-5a8c-8af5-619500913a40 |  | note | Record of conformity: This ITP signed
label | c8702bc0-9c37-5ca7-aedf-6df61690a601 |  | note | TP
label | 36770c0d-14aa-5e1b-9231-d8112dd61793 |  | note | Responsibility: Site Engineer
date | 804c4e4c-7f17-5ef3-a176-d125ae951168 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | c2623af2-22ff-5802-a942-c5d400012d07 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | e27e4def-a14f-5efd-b343-8aa7307739a1 |  | textbox | Print Name:
text | 3cdb022b-d9ed-5125-bc20-975e9c2ad9ee |  | textbox | Position:
date | 2ee822bf-1945-508a-bfe7-913e3f16f9d3 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-003 - Service Trenching & Install | itp |  |  |  | Yes | CTN-ITP-003 - Service Trenching & Install | 5692b6bd-2570-4ca8-9480-0d71affdca35
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 98395e3b-5752-5346-97ab-cc8b46b51337 |  | note | Frequency: Prior to commencing any activity
label | 1cfeb314-6757-5c92-9386-4f55ac3c06f9 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | e9b7c459-9a19-51bb-a840-073b722d46dc |  | note | – using the correct and complete set of drawings
label | c609d7a8-5cfd-54f4-a281-e36b3d923575 |  | note | – all drawings are the latest revision
label | 13b668d2-d344-5009-b9cc-1202b9356193 |  | note | Reference Documents: Drawings and drawing registers
label | 4673e7cf-bdbd-5530-b5d0-5c801397662c |  | note | Inspection / Test Method: Visual inspection
label | e4106d42-5af9-5039-8b25-5632e7bfc3c8 |  | note | Record of conformity: This ITP signed off
label | 5e1fd4c6-11f2-531b-b509-a7aa5c2b5ead |  | note | IP
label | 514600f1-bf8e-5502-ae0b-12c435fb2049 |  | note | Responsibility: Site Engineer
date | 297f9b90-2e37-545e-9a00-03c7413d4f7a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 71ecd841-f4e9-57f9-b4cf-60d9af851dbb |  | note | Frequency: Prior to commencing any activity
label | c624d405-6cb0-5c81-9193-02306d8cab9d |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | 27391a8b-71f0-5a8d-ad60-a506dcdbc3df |  | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | 78443518-6dc6-58e9-90aa-65aea594c56f |  | note | Inspection / Test Method: Visual Inspection
label | 0cf1820f-a1fd-558f-bbf4-356d42d0773c |  | note | Record of conformity: This ITP signed off
label | bd3716d9-fa44-534f-9ad8-14fd3137bbf5 |  | note | IP
label | 9e343599-a312-580c-a136-4edea83fd1f9 |  | note | Responsibility: Site Engineer
date | e6aa4c5a-8c12-53dd-ab4f-cc2750aaf206 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Materials
label | d438faef-3cea-5e87-898f-819d14622e36 |  | note | Frequency: Per Lot
label | 34383b21-74eb-5cd8-b4c3-91ea7ac13a60 |  | note | Acceptance Criteria: Bedding sand provided over rock and above conduit
label | 90b49e8a-a542-540b-bdc4-49ff6dea13d9 |  | note | • 20mm Class 3 FCR for backfill
label | 394034a4-bfdb-5a25-8088-0a8f8a36d770 |  | note | Reference Documents: C.19, Drawings
label | 18eb9283-1e84-59dc-bf8a-9e51176a139b |  | note | Inspection / Test Method: Verify
label | 37085c4f-52c1-5d98-b58f-eda05cde889b |  | note | Record of conformity: This ITP signed, Recievable Inspection checklist
label | 0e906e1c-345b-5e5f-8ead-01dbc21083bb |  | note | IP
label | c6fd3ad2-1601-538d-a8a1-d946b846b5ed |  | note | Responsibility: Site Engineer
date | db5ebe70-6aed-5e48-be41-1b4c6c3638e4 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Construction Works
checkpoint-status |  |  | checkpoint | 2.1 - Survey set-out
label | c538adf4-e1b6-52ff-9083-1a22584924e6 |  | note | Frequency: As required
label | 8c4d0ae1-25f8-5b29-9c6c-6f6f15017c59 |  | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works will meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
label | 0a2a5ead-2f76-5d52-889c-2cbc89c3e4d1 |  | note | Reference Documents: Drawings
label | 5225c28d-8e9e-5eba-a675-e45b40f9bb81 |  | note | Inspection / Test Method: Verify
label | 9a03e515-6094-508e-86f6-284bb3907662 |  | note | Record of conformity: This ITP signed
label | d6067c3b-3d13-57c4-bdbf-6529d4f8fe0f |  | note | HP*
label | ea4fd987-23e8-51b7-a06b-b91c2b08589c |  | note | Responsibility: Site Engineer
date | fcaf231c-538a-5e39-86c0-9740ed2791f4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Excavation/Boring & Trenching
label | 5672df9d-8058-572b-a55a-76e4cef8a8ca |  | note | Frequency: Prior to Backfill
label | be0d3fef-0049-5b12-8be9-cdf62da2481e |  | note | Acceptance Criteria: Superintendent to inspect completed tench
label | d13d6708-30c7-5b4a-8606-2ac03a928397 |  | note | ○ Depth Requirements:
label | f37e45a6-6d07-5ef9-bd62-a32e28a2324d |  | note | • Where conduits are laid under carriageway pavements, the minimum cover from top of conduit to the pavement surface shall be 600 mm
label | f3599065-f450-580e-b446-49a54d4db2d3 |  | note | Reference Documents: C.19, Drawings
label | 3cfa710c-e4b2-58af-870d-bbaf0ad5adfd |  | note | Inspection / Test Method: Measure
label | 6ec625a3-49a2-5de6-af54-bfac892a98f8 |  | note | Record of conformity: This ITP signed
label | c543fb18-57ed-55c5-8393-4fd0545fac60 |  | note | HP
label | 11132222-b1b0-5f67-b0b8-a14df50b87ae |  | note | Responsibility: Site Engineer
date | 81e489b2-c3f9-56d3-98bd-7b91221a3926 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Installation of Conduits
label | 44bebb22-2832-55cc-b9e2-71d5909b9c2e |  | note | Frequency: Prior to installation of conduits
label | b054629e-ae5f-5723-85c4-b9c5fb56ff30 |  | note | Acceptance Criteria: All conduit installation works for electrical wiring and communications cabling shall be carried out by, or under the direct supervision of, appropriately registered and licensed personnel
label | 18ab69cd-5335-515a-94ab-895ac37cd9af |  | note | – 100mm bedding sand provided over rock
label | caa85590-0d84-5a9b-9f17-4a4f0dd79b10 |  | note | – 150mm bedding sand provided above conduit
label | 39c545f2-9e41-528f-ab64-8637c33c0e4c |  | note | Reference Documents: C.18, Drawings
label | 5e4d1fda-66cc-52a7-bf1c-b2b9e9df16e1 |  | note | Inspection / Test Method: Verify
label | d25bf0b7-c78a-507d-852a-be16ad6fd7f7 |  | note | Record of conformity: This ITP signed, Subcontractor competencies on salesforce
label | 3964a5ef-6a2c-58a3-a805-680963a8949d |  | note | WP
label | a84879ec-6b17-5a00-9fae-26fdcfb0c6e1 |  | note | Responsibility: Site Engineer / QAV
date | 21e481d2-a618-5a56-8841-de96d5f97f40 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Back Fill of Trenches
label | 2dde1a81-e64c-5935-adc3-07e44625d88e |  | note | Frequency: Each Lot
label | 94b92754-a9f6-5cb3-8497-e03ab7d8f795 |  | note | Acceptance Criteria: Place and Compact fill in no greater than 300mm layers
label | 1324cf25-c413-5630-9ffe-91153ce06123 |  | note | – minimum 300mm 20mm Class 3 FCR below pavement/ground level
label | 07ba2a96-5eff-5d68-8d46-3093e75fbb87 |  | note | – Where trench passes under load bearing zones maximum 200mm layers
label | 13bb0ea3-96b8-58a1-b81d-7975f821a11c |  | note | – conduits under area to be paved backfilled with select back fill to subgrade level
label | b84b18a9-2295-5509-999c-e9e820baf318 |  | note | – conduits under area not to be paved backfilled with select fill to 0.4m above top of conduit and common back fill above that
label | d1405dfe-86c9-54a0-900b-5e18567c98a9 |  | note | Reference Documents: C.19, Drawings
label | b88a5bd4-65a7-5e7c-9a59-1c177a2241ca |  | note | Inspection / Test Method: Measure
label | e09b6482-29b0-594d-bfd2-5495b28d9e46 |  | note | Record of conformity: This ITP signed
label | 93e8a315-f18e-502e-b992-00cf37e13770 |  | note | IP
label | 03a8e810-ada2-5b3a-acb7-257aea7a18e6 |  | note | Responsibility: Site Engineer
date | d000c1b6-e57b-51a4-8855-b85038c2f637 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Compaction
label | 066019e7-b05b-52ea-b026-17e953982a61 |  | note | Frequency: Each Lot
label | ec36d1bc-7ca6-5342-8edc-1d12a085a9a8 |  | note | Acceptance Criteria: Superintendent to inspect testing and compaction of subgrade
label | f8651d32-75b4-56ed-ab19-605d74c7c12a |  | note | • Post compaction falling cone penetrometer >7 blows per 300mm
label | 22fa0e08-4671-54f7-ac9c-692fa784323d |  | note | Reference Documents: C.19, Drawings
label | 94c988c9-1099-5bf8-ad55-3b01fb55fdba |  | note | Inspection / Test Method: Verify
label | 7b5e9c73-92cf-5d25-a13d-0740c9de7cfb |  | note | Record of conformity: This ITP signed
label | 447b1343-ab6b-5a9c-9183-46bd77119812 |  | note | HP
label | 3e481716-5326-5159-a513-0f840067f074 |  | note | Responsibility: Site Engineer
date | b5e88053-ae6a-5504-b35a-a54f5de99aed |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.7 - Compaction
label | 07cff7d5-6c1f-56ae-84a8-c97cb411666c |  | note | Frequency: Once, prior to use of backfill >40mm
label | ef556c82-f5c2-5cd1-a14c-bbd4ef538042 |  | note | Acceptance Criteria: Detailed proposals for the compaction of backfill materials of nominal size greater than 40 mm shall be submitted to the superintendent for review before commencing work.
label | 9e91a89a-65b1-5798-9eee-3defae7d9777 |  | note | Reference Documents: C.19, Drawings
label | 3ea95739-142c-5519-bdcd-a85632da1f15 |  | note | Inspection / Test Method: Verify
label | b32ee638-6efa-563c-be8d-93ccbdf74c72 |  | note | Record of conformity: Correspondence with superintendent
label | 9ca8c0ce-d56d-581c-b97b-94102fa00ee3 |  | note | WP
label | 6986eddf-9159-57cd-b917-5eaf079cdfdc |  | note | Responsibility: Site Engineer / QAV
date | 96065705-b353-5dd3-9b05-94742e2f95b0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Installation of marker tape
label | 7fd6b6ca-e2a7-5b8f-8573-fd98d202a009 |  | note | Frequency: Each Lot
label | f287f513-fb54-56f9-a824-76aff61cf044 |  | note | Acceptance Criteria: Marker tape is to be installed above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top.
label | fd3dcdd6-f42d-5224-b215-9b653ce35e53 |  | note | Reference Documents: C.19 TC-2204
label | a6f6e20d-8148-5f02-b509-5b36f2d764d8 |  | note | Inspection / Test Method: Visual inspection
label | a32e9cbb-1b4b-5c55-bf33-3c858dcdd674 |  | note | Record of conformity: This ITP signed
label | 4140dd07-076d-5aa8-896f-67bc1846f7b2 |  | note | IP
label | b7a34db8-2e21-5ec4-aabb-1c6b0f6ca668 |  | note | Responsibility: Site Engineer
date | e0d528d9-057f-59ba-b8bd-1bdb8b4e128b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.9 - Cable Pits & Pit Lids
label | 5e8739d1-b8d7-54d8-bae8-36c01a53a691 |  | note | Frequency: Each Lot
label | 849713c4-f8f0-5f27-873f-e265595c3c2c |  | note | Acceptance Criteria: Cable pits constructed and installed as per drawings
label | 11928fa9-eee9-5f5e-8f1d-6e118a0cd1c9 |  | note | • Reinforced concrete apron installed around pits that are in an unsealed area
label | 0f378afb-e330-5907-a86f-dbf6f7f04d4c |  | note | • Heavy pit lid provided where pit is located in a road pavement
label | d9f7ffd9-464d-5094-9edd-ade174ed555f |  | note | • All pits, junction boxes or terminal pits for electrical purposes shall be watertight
label | 27d02435-44c8-5df1-a166-f15f052ca0ca |  | note | • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
label | 5f7a860e-e77f-567e-8da1-5a4cce9a0e4e |  | note | Reference Documents: C.19, Drawings
label | 387176d3-1eee-5ede-8df9-aef44bca723c |  | note | Inspection / Test Method: Verify
label | ddbd0da3-984f-502d-b56f-9d57a4f3146d |  | note | Record of conformity: This ITP signed
label | ea29dcd7-f13f-5910-9e54-51b72bd5ee74 |  | note | IP
label | 4b6c98de-c392-50d8-b5bc-6e79f75ffb1f |  | note | Responsibility: Site Engineer
date | 70a9eebb-5e1b-52cb-8417-4345660fcfd8 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Completion
checkpoint-status |  |  | checkpoint | 3.1 - Cleaning of Site
label | 1798777f-b549-5f71-8771-ac3da583c161 |  | note | Frequency: Each Lot
label | c9ef86da-33c3-550e-9fe4-3aaa54b9680b |  | note | Acceptance Criteria: Surplus excavated material shall be removed from site. All affected areas shall be restored to similar conditions that existed prior to work.
label | 3101d30b-a0e8-5251-bd86-16c5e2429cde |  | note | Reference Documents: C.19, Drawings
label | df974b32-fb73-53cb-b2a4-37248e5d7ad4 |  | note | Inspection / Test Method: Visual inspection
label | bc0f030d-3127-5e7b-bb22-d7a4af581d9d |  | note | Record of conformity: This ITP signed
label | baf36d74-6abd-51a1-b09e-47906bef383c |  | note | IP
label | 5b6c54bb-f38b-5b88-b6f3-bd0527627e26 |  | note | Responsibility: Site Engineer
date | 8fea8110-9cfc-5847-88fa-93ece98b85a4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Recording/As Built
label | d6877817-692a-5189-a229-6f1190281e76 |  | note | Frequency: Each Lot
label | 7deba905-8418-5f07-bb5a-1cf585fa043c |  | note | Acceptance Criteria: Installed location and depth of conduits, and location of pits and pedestals, shall be accurately recorded on as-constructed drawings.
label | e1b15500-3633-5021-af6d-df4f95e9a016 |  | note | • Lot Maps shall be completed to show the extent of works for each lot.
label | 610ece33-e69f-56e5-90f6-3c4eefd00efc |  | note | Reference Documents: C.19, Drawings
label | 4626fffa-d47f-56c1-8200-d7a4689f768a |  | note | Inspection / Test Method: Verify
label | 3312e6ff-952b-5cb8-a193-4919bbe6ba24 |  | note | Record of conformity: As Built Drawing
label | e929ceb2-5189-5225-beb5-000c4d5b6f55 |  | note | SCP
label | 73db3806-678a-5124-8832-dce1515dd1b2 |  | note | Responsibility: Site Engineer
date | a8512c67-2996-5e48-834c-6832e82f7fc4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | f36cdcb6-a7fa-534e-b192-573a235bc8c8 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | ca918511-651e-5b12-973b-084cdc3f134f |  | textbox | Print Name:
text | e226e2c5-f172-5ad9-9cc4-38e88928cc41 |  | textbox | Position:
date | 1a6cecce-190a-53e8-8fef-8b2932522f56 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-015 - Container Farm Construction | itp |  |  |  | Yes | GT4-ITP-015 - Container Farm Construction | 6c4da8cf-3197-44a8-a451-b8a5533689cb
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | b8b9c150-909d-5c14-8867-2a60f3a629c4 |  | note | Frequency: Prior to commencing any activity
label | f1039d57-1bae-53e9-9a13-7fbf3f3ac546 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 7682e887-2033-52be-a8c2-da225d63a939 |  | note | – using the correct and complete set of drawings
label | 978175e5-45f6-56dd-96c5-6db2518e7d6e |  | note | – all drawings are the latest revision
label | e70d5b6a-eb58-5fd8-ba62-019a71c58824 |  | note | Reference Documents: Drawings and drawing registers
label | 3433ba6a-f7f6-5a4d-b16d-d86584217747 |  | note | Inspection / Test Method: Visual inspection
label | f66f55ed-8f7a-5151-9d36-5cf993648836 |  | note | Record of conformity: This ITP signed
label | ca67151e-bdd6-56ed-913f-e324743d7188 |  | note | HP*
label | a44344df-e14e-5d3b-978c-3fa359c8c8e0 |  | note | Responsibility: Site/Project Engineer
date | 863088fb-ac13-5c82-85a5-7c02f17697c2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | dee0c6de-0fc8-583e-8e08-d500c2a1e8a9 |  | note | Frequency: Prior to commencing works
label | 7b3b61dd-3e70-5996-8b05-878770a833e8 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP`
label | cb55b8ff-75a3-5239-b58f-dfca2dab7b57 |  | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | da584b1d-5c5f-5e2d-9e75-44d4d713caf9 |  | note | Inspection / Test Method: Visual Inspection
label | c037285e-5341-59ee-a869-2767030496b5 |  | note | Record of conformity: This ITP signed
label | 1dd9bcf8-6fdc-5174-ac2a-9797494abc86 |  | note | HP*
label | ae5228dd-7d42-58be-8657-1a80dca1cfda |  | note | Responsibility: Site/Project Engineer
date | 0e7a7c51-2354-518c-b641-ad9d955d6a6b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Plant and Equipment
label | 95a89a28-6df9-55c0-a0b1-aa7dcd6e74b7 |  | note | Frequency: Prior to commencing works
label | 50df320d-14d0-58b1-a5c0-c0bfabffd985 |  | note | Acceptance Criteria: Plant and equipment used in the Works are appropriate to achieve specification requirements and is inducted
label | 9f7c2a9e-52b2-57cc-afea-7ea2c7b00fd2 |  | note | Reference Documents: N/A
label | dc1a5fe1-a5ca-5dbb-94a1-a61e570025a4 |  | note | Inspection / Test Method: Visual Inspection
label | 8c946410-f7fa-5da0-b8b1-7b4edf16f5fd |  | note | Record of conformity: This ITP signed
label | a3ce0272-7fe1-5aab-8039-cc4c7f510501 |  | note | IP
label | b2d5e08e-09a9-5b69-b527-811393b18fe9 |  | note | Responsibility: Site/Project Engineer
date | cb42b359-afbf-59b3-bfb8-cdefc4ad73d9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Service Locating and Proving
label | 642c81b6-42e8-51d6-8163-68c61e2d3613 |  | note | Frequency: Prior to commencing works
label | 2a6a8eff-9015-5e2b-af36-9ae06916474e |  | note | Acceptance Criteria: The Contractor should familiarize themselves and all personnel on site with the location of all existing services on and adjacent to the site and ensure that all services are fully verified and evaluated against the proposed works.
label | 3ccd609a-654c-56c7-9252-86e25defc5ea |  | note | ○ All due care shall be taken to protect existing services, structures, and works in and around the site and adjoining streets
label | 6e9faf0f-4a69-5b90-976b-e08d5ee7513e |  | note | Reference Documents: Project Specification Section 1.2.1
label | b3fe7b4e-a585-511c-a030-eaa5f93445c8 |  | note | Inspection / Test Method: Visual Inspection
label | 49aa25e2-fd76-553b-9b07-870425c18599 |  | note | Record of conformity: This ITP signed
label | c16d37f3-668d-5bf1-8904-4bb89d3cbe71 |  | note | HP*
label | f0d17545-f810-5a49-bda1-ac3436af81f8 |  | note | Responsibility: Site/Project Engineer
date | 3a0230be-9ef8-505a-a039-9a38d061fbde |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Protection and Remoal of Services
label | 5cd8a538-94e6-5a97-8e2d-930be3fce447 |  | note | Frequency: Prior to commencing works
label | b6797ff4-dae4-5ed1-9c99-90d4ce233926 |  | note | Acceptance Criteria: Before demolishing and removing any part of the works with electrical wiring, gas or water pipes, conduit, telecommunications, or similar items, the Contractor shall notify the Superintendent and relevant authorities to ensure that these items are out of service and can be removed safely.
label | 65088927-d55a-5857-9c20-53d34f25a045 |  | note | Reference Documents: Project Specification Section 1.2.1
label | ecadb343-d850-51ca-9a7c-2789ae9400c1 |  | note | Inspection / Test Method: Visual Inspection
label | d68afe0e-b9e8-5323-9272-e9e459e38694 |  | note | Record of conformity: This ITP signed
label | b4e5d6d8-a7b9-54cd-b6d3-7db0808f0063 |  | note | HP*
label | 428ac2e9-9d1a-529f-a398-aea5e8a08d54 |  | note | Responsibility: Site/Project Engineer
date | 27d1e86b-d7f2-5722-9899-d05468ae9b21 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Clear & Grubbing
checkpoint-status |  |  | checkpoint | 2.1 - Tree Removal
label | 9db23b43-cb2c-5f6e-958d-fa5ce8565134 |  | note | Frequency: Each Lot
label | 2ec68a2f-d141-5455-83b9-69ad52a76409 |  | note | Acceptance Criteria: The clearing shall consist of removal from the area designated in the drawings of all trees, standing or fallen, and other vegetation, boulders and rubbish and shall include the grubbing out of all stumps and tree roots to a depth of 600mm below the natural surface or 400mm below the finished cut surface, whichever is the lower, and disposing of all spoils resulting from the clearing and grubbing.
label | e5d17181-31d1-5103-a26a-4dcb5265e603 |  | note | ○ Any holes left after grubbing shall be filled and compacted to the same density as that of the surrounding undisturbed soil.
label | aad4639f-43af-5e20-a6d7-5cda642c9b6d |  | note | Reference Documents: Project Specification Section 4.5
label | fd64b8aa-bfe4-56b6-81d2-9b0ae4fef589 |  | note | Inspection / Test Method: Visual Inspection
label | e275e6ae-d9aa-576b-aa1e-46a91b63ca15 |  | note | Record of conformity: This ITP signed
label | 4de521bf-11b4-58a1-b49b-d7dd4bd25895 |  | note | HP*
label | 24a446ca-6c88-5f5f-896d-9c5d26a905d8 |  | note | Responsibility: Site/Project Engineer
date | e42e8d52-fc21-585b-b66e-34591e13e093 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Mulching and Chipping
label | c43f9d5b-11e8-57f2-a954-0f4b6b7dce80 |  | note | Frequency: Each Lot
label | 4bffbb85-1db1-57b3-891e-0333495772f9 |  | note | Acceptance Criteria: All tree trunks, branches and stumps smaller than or equal to 400mm in diameter, including leafy material, shall be mulched (unless noted otherwise) and neatly stockpiled in a site to be determined by the Superintendent.
label | f0a65803-50cf-5135-9e22-5705d9c98a1d |  | note | Reference Documents: Project Specification Section 4.6
label | 0921c6ad-f9b9-5f4a-b3e6-fe024ffe82e0 |  | note | Inspection / Test Method: Visual Inspection
label | dcdb409a-6662-5d2a-92dc-67e47a362b74 |  | note | Record of conformity: This ITP signed
label | abed0f51-d8a0-5c39-9998-0672278664e0 |  | note | HP*
label | 2374fa48-d8e6-506b-a244-041b226eacee |  | note | Responsibility: Site/Project Engineer
date | 01e393bc-ab1c-5d06-8c29-723bc6dbdaa7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Stripping of topsoil
label | b295916c-e68e-5fa2-8195-11cda4d2af06 |  | note | Frequency: Each Lot
label | 2b846cae-b22d-52da-baa0-87633b542e6c |  | note | Acceptance Criteria: The existing topsoil shall be stripped from all areas to be earthworked, prior to the commencement of the earthworks, and stockpiled on site.
label | 510b5b07-52fc-51ce-9c8a-03729e8f6588 |  | note | ○ Topsoil is defined as the layer of surface material containing humus, roots, plants and organic material exceeding one percent by weight.
label | 03fa3a88-1ee4-5314-ba88-e50dc936532c |  | note | Reference Documents: Project Specification Section 4.7
label | 7e872fe0-5b07-51ea-bcad-57befd534a31 |  | note | Inspection / Test Method: Visual Inspection
label | 25f539e0-dc49-5f1e-8577-313db2904664 |  | note | Record of conformity: This ITP signed
label | afcc6e38-e135-5d8b-b6af-bc16bf70eb9a |  | note | HP*
label | 065300c6-36cd-58fb-ab0a-61271302a087 |  | note | Responsibility: Site/Project Engineer
date | a80a8d32-b081-5460-956e-56b491e9f06c |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Excavation
checkpoint-status |  |  | checkpoint | 3.1 - Earthworks
label | f7502675-99f2-5e42-9df9-3dfcbdacdac2 |  | note | Frequency: Each Lot
label | e28bf7a0-6124-5010-b71a-c0543d943ca9 |  | note | Acceptance Criteria: Excavation shall include the removal of all materials encountered below natural ground level, including all obstructions of any nature that interfere with the proper execution and completion of the work.
label | 499aef62-7479-5d18-8af2-009be6104701 |  | note | Reference Documents: Project Specification Section 4.2.1
label | 70b55db2-67b9-5274-b1e9-b83c78029fd6 |  | note | Inspection / Test Method: Visual Inspection
label | 4bd81092-bad3-572f-9593-8ac01be9f51b |  | note | Record of conformity: This ITP signed
label | f44b5947-bde6-535b-aff6-ed4ba95b4398 |  | note | IP
label | f12d0057-9b41-5c2e-a5d4-7da15515ad3a |  | note | Responsibility: Site/Project Engineer
date | 4218902c-8f8b-529b-a15e-0e237bb783c2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Subgrade Preperation
label | 2b787ef3-2105-5ea6-9cf2-4baa1c15f0ef |  | note | Frequency: Each Lot
label | c3822628-3e65-5b67-9cc4-05aa25430ac2 |  | note | Acceptance Criteria: The sub-grade shall be trimmed to an even surface free from loose material. Remove roots, boulders and other unsuitable materials such as silt or organic matter as directed by the Superintendent.
label | 2b1fde7a-9799-5bc3-870a-4ad4cdd715ca |  | note | ○ Grade depressions to drain to the edge of the formation. Where the subgrade is unable to support construction equipment or it is not possible to compact the overlying pavement because of a high subgrade moisture content the Contractor shall refer to the project specification for treatments.
label | 5ba1875a-2a12-5cd0-9742-345875de582a |  | note | Reference Documents: Project Specification Section 4.13
label | 7a3fe008-0a58-5a16-bcf3-8e14bb474611 |  | note | Inspection / Test Method: Verify
label | cc74a245-f2c3-5772-85b1-a6dd65098d9d |  | note | Record of conformity: This ITP signed
label | af9a8717-b0e7-59a8-8319-084ed2700fb5 |  | note | HP*
label | 3ec35b37-5f39-5a50-bea7-7061d994b123 |  | note | Responsibility: Site/Project Engineer
date | 3c5c9df2-0f44-59ac-88c5-a768a51354ad |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Survey Conformance
label | f459d0e5-9906-5a8d-b4d3-b80f4fc2c67d |  | note | Frequency: 1 per project
label | 071baf4e-2d08-5384-a575-5f3cfeed74f5 |  | note | Acceptance Criteria: The subgrade formation surface shall be finished within the following tolerances:
label | c3908d7e-efb9-53b9-b1bc-67ff5cb5591e |  | note | ○ Variation from a 3 m straight edge 10 mm
label | acbb2490-7328-525e-b826-4cafd144f572 |  | note | – – – – – – – – – –
label | c15a30d1-6d95-5bd0-b830-53cbc4a41c03 |  | note | Test/Record Frequency
label | 73629f5a-3ac5-5c58-9669-5c3e1955db3d |  | note | – – – – – – – – – –
label | 777242f5-b549-5609-9d50-7768a9f84125 |  | note | Finished subgrade level ¦¦ + 5mm or - 30mm (+0mm)
label | a80ff8a0-31f1-593b-b8cd-d090f97fe5d5 |  | note | Sub-base width ¦¦ + 300mm and - 0mm
label | c2216a2b-0e19-5ba5-a850-2d9188b24d36 |  | note | Finished sub-base level ¦¦ + 10mm or - 20mm
label | a3e9cda2-24e7-57c6-8429-8c2c5ccc6c1d |  | note | Basecourse width ¦¦ + 300mm and - 0mm
label | 0ad6e7a6-f212-562d-9f9a-16bcbcb9d5c3 |  | note | Basecourse thickness ¦¦ - 0mm
label | b6b8005a-50d3-500c-bbf2-1f2891d38ca1 |  | note | Finished basecourse level ¦¦ + 10mm or - 10mm
label | b0d9b4a4-614f-5fce-ba62-8381620248b1 |  | note | Thickness of AC ¦¦ + 5mm or - 0mm
label | 8ab0ba60-64e6-52ea-b2a6-b986abb957f8 |  | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
label | 1c48c4d2-4abe-52ff-9ebd-300ad43d7112 |  | note | – – – – – – – – – –
label | 79b20a9a-0147-57f7-a969-9ea184012e44 |  | note | Reference Documents: Project Specification Table 4.3
label | afe4bb52-9976-54fe-8a53-a41a8f614be4 |  | note | Inspection / Test Method: Verify
label | 939f9630-6ca9-5973-a23b-5a85b2aab71a |  | note | Record of conformity: Conformance Report
label | 8890adab-1991-54c6-93af-8186592010bf |  | note | SCP
label | 62274308-3a84-566b-82d3-8ee075383ca6 |  | note | Responsibility: Site/Project Engineer Surveyor
date | e3530280-bfad-54f8-9489-34833cf2799e |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Placement of Crush Rock
checkpoint-status |  |  | checkpoint | 4.1 - Placement
label | 2be8fcab-151a-5ff1-a27b-4d8a0b5cfc6b |  | note | Frequency: Each Lot
label | a766c93d-6316-5d2d-af86-ca444f3e0ebc |  | note | Acceptance Criteria: Once the sub-grade has been approved, crushed rock shall be evenly spread in layers no thicker than 150mm
label | 9135cd9d-aa5e-58d7-8f41-c13d911a8a61 |  | note | Reference Documents: Project Specification Section 6.8.1
label | 5bc901d8-256e-5e09-aa7c-4ddc7b84fbb8 |  | note | Inspection / Test Method: Visual Inspection
label | aefe3b38-edb0-59ae-8e10-017c6a51a277 |  | note | Record of conformity: This ITP signed
label | 7ced1f61-cb4f-5916-aebd-4b72f9e34eb6 |  | note | IP
label | 48618217-e466-51c9-b77b-f4b01d70f2bc |  | note | Responsibility: Site/Project Engineer
date | 3f65f320-89e4-5f86-8559-ee9bb57b492f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Material Quality
label | 1b68dac4-f60f-5fe4-b213-b4ea2a4bb363 |  | note | Frequency: Each Lot
label | 9eeac628-a9f3-51d3-a824-6abd68c1980f |  | note | Acceptance Criteria: The material should be spread without segregation and between approved edge boards or kerbs.
label | 05fd4fe9-8839-5669-bd08-578218d86dc8 |  | note | ○ The crushed rock should not be spread on waterlogged sub-grade, and any soft spots or areas with mixed materials must be dug out and replaced with approved material.
label | 9e3536fb-74ce-578d-bb3f-a16b2cff726d |  | note | Reference Documents: Project Specification Section 6.8.1
label | 44501160-5a42-551e-8429-9c4bc738c4dc |  | note | Inspection / Test Method: Visual Inspection
label | e19c4d4e-01cd-51e7-9166-0459eff139ba |  | note | Record of conformity: This ITP signed
label | ba4a6332-27dd-57e3-bd9f-7c4d368b10c9 |  | note | IP
label | 3a81b1ee-792f-5e6f-908a-b7b3b1214e69 |  | note | Responsibility: Site/Project Engineer
date | 8d39b5e0-eb84-5815-82ad-6451a82b1c7c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.3 - Testing and Proof Roll
label | ded87d32-1e73-5123-9ae1-768bd99cf698 |  | note | Frequency: Each Lot
label | a38b990a-4009-54cc-9341-90153923aecf |  | note | Acceptance Criteria: Rolling must be performed to eliminate bumps and irregularities, with the finished surface being true to the required grades and cross-section.
label | 7cf7aec2-bdb7-5b71-b74f-c7658eca1211 |  | note | ○ The crushed rock must show no movement under a six-tonne smooth steel-wheeled roller, and the minimum compaction achieved must be 100% of the Standard Maximum Dry Density in the base course and 98% in the sub-base course.
label | 0a1304a4-aa8f-568c-98d3-b2692171f01a |  | note | ○ The thickness specified is the minimum required.
label | 028249db-301d-5a3b-9726-b464ec4152a5 |  | note | Reference Documents: Project Specification Section 6.8.1
label | 4195e96d-ff9f-58bb-9529-299449e61f4d |  | note | Inspection / Test Method: Verify
label | dd9ca005-0a2a-5bd2-a677-96a1319c16dc |  | note | Record of conformity: Test Report
label | 07c5c72f-2bc7-5ef5-9604-cead1c16aa0a |  | note | TP
label | eb43c1dc-bd98-5bc4-9329-2284038dfa8f |  | note | Responsibility: Site/Project Engineer
date | 13824539-afc1-58ac-9abf-e2c20470a37a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.4 - Shape
label | a342a170-668d-5109-88db-1ff856474d56 |  | note | Frequency: Each Lot
label | 3a678a90-2566-5edc-aa59-1cba33a6587c |  | note | Acceptance Criteria: The shape of the road must be checked frequently during final shaping and compacting and corrected as necessary by grading under the direction of an experienced foreman.
label | de5ef2b5-1197-5370-b728-cf6352d83fd3 |  | note | ○ The crossfall, super-elevation, and smoothness of the grade must be checked using a straight edge and built-in level.
label | 9268de27-7ebb-5c65-9528-462a74134770 |  | note | Reference Documents: Project Specification Section 6.8.2
label | 2efc3695-d627-5fb3-aaaa-c976c95b73be |  | note | Inspection / Test Method: Visual Inspection
label | fbf79b38-3a38-58ca-a017-39cddb5394ad |  | note | Record of conformity: This ITP signed
label | 1d7061c5-0d89-546d-8c60-9cd0dcd2ab31 |  | note | IP
label | 06dcb92c-b82c-5da8-92b1-534878a9fb6a |  | note | Responsibility: Site/Project Engineer
date | 155b0501-c0b9-5efc-b812-d1e285733c87 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.5 - Conformance
label | 8335be9f-f841-51f4-96f5-4afb1b4d05dc |  | note | Frequency: Each Lot
label | e6c7b1a4-e7ee-55c1-aeea-07c45a9fc4e6 |  | note | Acceptance Criteria: The following construction tolerances must be achived by the contractor
label | 04a6867a-d792-52ad-9c6c-2157155bb9ba |  | note | – – – – – – – – – –
label | 82d6b080-e2df-5a48-a0e0-f8aa9ddb9eec |  | note | Test/Record Frequency
label | 69c89bad-32b5-5ddc-9ffc-372ef0d8f1ac |  | note | – – – – – – – – – –
label | 3ba0d6a6-6eab-5d11-8c29-62735fb5c625 |  | note | Finished subgrade level ¦¦ + 5mm or - 30mm (+0mm)
label | 4f730778-f72c-5018-af10-82c704dcd4a6 |  | note | Sub-base width ¦¦ + 300mm and - 0mm
label | 9d918ce1-4a36-59af-a2b9-4824abe32976 |  | note | Finished sub-base level ¦¦ + 10mm or - 20mm
label | fb895833-418a-59ce-8b10-3c706d94864b |  | note | Basecourse width ¦¦ + 300mm and - 0mm
label | 93083d07-fd34-51c1-83ca-62edbddc36dc |  | note | Basecourse thickness ¦¦ - 0mm
label | 0de2f310-91b9-5e51-8688-d7d62699a743 |  | note | Finished basecourse level ¦¦ + 10mm or - 10mm
label | 7e8b04ff-733c-589c-b4ec-2ffb59de5a28 |  | note | Thickness of AC ¦¦ + 5mm or - 0mm
label | 93b806c9-aadb-5f60-8efe-3f1b0377aa59 |  | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
label | 2748baa3-e53e-5092-9147-971d9c3255c8 |  | note | – – – – – – – – – –
label | b2bcb694-3397-5f2a-9e7c-8ec23656bf91 |  | note | Reference Documents: Project Specification Table 4.3
label | bbd3944c-c112-55ca-bad7-256db466dc0b |  | note | Inspection / Test Method: Verify
label | 32edc792-eb81-54d3-add5-6823845ed3b4 |  | note | Record of conformity: Conformance Report
label | 64987616-e6c7-5e6d-9ded-ecbadb8517f1 |  | note | SCP
label | 6e7514da-9b2f-54e9-affb-a3f63e36e5bf |  | note | Responsibility: Site/Project Engineer Surveyor
date | 1ce9f9ef-9322-54d2-b50b-78df95174b9b |  | date | Date Completed:
checkpoint-group |  |  | section | 5 - Asphalt Path Placement
checkpoint-status |  |  | checkpoint | 5.1 - Asphalt Mix Specification
label | 5dd0b0c6-8216-5fdf-92b7-9134bf5cf77c |  | note | Frequency: Each Lot
label | bbd4ec31-071a-5f44-a01d-5680a76c2047 |  | note | Acceptance Criteria: The bitumen grade is to be Class 170. The bitumen is to conform to AS 2008 and the current Austroads Guide to Pavement Technology Part 3. Aspahlt to be a 30mm compacted depth of 7mm NS type L asphalt
label | 4ea490d3-6625-5305-8144-e74a47014006 |  | note | Reference Documents: Project Specification Section 6.5.3
label | a0e54723-b77e-545f-a005-f7b89eb6fbc0 |  | note | Inspection / Test Method: Visual Inspection
label | bf43be89-f6d9-50aa-95dc-c1c8c2bde45d |  | note | Record of conformity: This ITP signed
label | 975a0389-9407-5dd8-b0ab-38d987d249bb |  | note | IP
label | 11e1b4a3-96fd-5775-9027-807d6b14ba77 |  | note | Responsibility: Site/Project Engineer
date | 327cb94f-8fb8-5432-aab5-726b424815a2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Placement
label | 25196335-49fd-5747-826a-009316df7665 |  | note | Frequency: Each Lot
label | ea553d3d-e98f-57fe-b18e-868a5ac0dcc8 |  | note | Acceptance Criteria: The temperature of the pavement to be surfaced should be at least 10 degrees Celsius, and no rain should fall during the placing of the mix.
label | 15d8c45f-aee4-5724-985f-4051f5eb2842 |  | note | ○ The surface must be dry.
label | 61da410e-0f77-5b6a-82bc-3bb22cfb07ee |  | note | ○ Asphalt should be placed at a rate that will provide the required compacted thickness shown on the drawings.
label | e74617a8-6148-5ed0-9b07-a0d01e88288c |  | note | Reference Documents: Project Specification Section 6.9.2
label | ede3dc99-fb80-5d29-a10e-9b65fc021456 |  | note | Inspection / Test Method: Visual Inspection
label | 8c5ac0a2-def1-5086-8c47-09646516c548 |  | note | Record of conformity: This ITP signed
label | 1c62eed5-ca63-50f7-a35d-6b67e62f539e |  | note | IP
label | f2705441-feec-5013-b58f-96082b747d12 |  | note | Responsibility: Site/Project Engineer
date | 6b47f7b2-875b-5fed-888e-d337d1f16142 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.3 - Jointing
label | 3be959db-6b6e-5a22-9546-f93ad308fa38 |  | note | Frequency: Each paver run
label | a5ae53d5-5744-503f-9f7b-7a37245707ee |  | note | Acceptance Criteria: Joints must be waterproof and formed as necessary to ensure a smooth and even profile over the joints without ridges or depressions. Joints must be in accordance with AS 2150 Section 12.6.
label | 6dcd35a1-13bb-5458-bebe-2a40683e8095 |  | note | Reference Documents: Project Specification Section 6.9.2
label | 5885fdc0-dac8-5f35-83a8-a0226b840d62 |  | note | Inspection / Test Method: Visual Inspection
label | fbf126c5-f41b-5a0b-8684-9d143d3bf096 |  | note | Record of conformity: This ITP signed
label | 6b598b2f-1e46-5d95-b382-ae866977cefb |  | note | IP
label | c33d2e9a-caf8-50ca-8537-e0dce0c1454e |  | note | Responsibility: Site/Project Engineer
date | 1833461a-5a4a-5c4b-aebf-71c3db83cb5d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.4 - Compaction
label | 87bbbcd3-2acd-5e28-a63b-89cadb8739a4 |  | note | Frequency: Each Lot
label | 163efb8f-0a48-5cac-9d4e-135f4e3e2665 |  | note | Acceptance Criteria: Rolling procedure to be confirmed by contractor on site.
label | 7965cb39-9a5b-5b2e-97eb-4c3d313b19d2 |  | note | ○ If the asphalt begins to shove or crack, rolling must not continue until the cause is determined, and corrective measures are taken. During all rolling operations, drums and wheels of rollers must be kept wet with water and be clean.
label | 2e0c5180-24c1-5a85-b6d3-be1e8c232e4b |  | note | Reference Documents: Project Specification Section 6.9.2
label | 8336ed67-e3b3-5456-92a1-95626aeed00c |  | note | Inspection / Test Method: Verify
label | 38f00a23-7a12-595e-92f6-bfcd3cf1d553 |  | note | Record of conformity: Test Report
label | 40ddff03-24ea-542b-b13e-a39010e90948 |  | note | TP
label | 7be6f566-0419-5c12-bf7f-3b05fc8e6c23 |  | note | Responsibility: Site/Project Engineer
date | bf49365f-1d71-5726-8c48-d14cbf0e29d4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.5 - Layer Thickness
label | f61fc9ab-b078-57c7-983b-7f2539e21f63 |  | note | Frequency: Each Lot
label | e61d7efd-cd4d-5641-bd89-e99c3c0c639f |  | note | Acceptance Criteria: Asphalt thickness to be 30mm with a construction tolerance of + 5mm or - 0mm
label | 9f81154d-5a59-5b5c-a08b-dcd51741272f |  | note | Reference Documents: IFC Drawings
label | 7145dcec-b520-59ca-8e90-484556979b8d |  | note | Inspection / Test Method: Verify
label | 9dfcd72d-a010-55bb-aeb4-81ffaaf2e8bf |  | note | Record of conformity: This ITP signed
label | d0dd06bf-211b-5d81-ab2d-806e549516ac |  | note | IP
label | a2201c7d-3dec-5c25-9e4c-1b80cde98767 |  | note | Responsibility: Site/Project Engineer
date | bb4291f2-00dc-533c-a949-b8701e5d214b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.6 - Tolerances
label | 9ba9013b-f250-5bd4-bea5-08b074ecd805 |  | note | Frequency: Each Lot
label | 98048b12-ac19-5a94-9099-adcb06153c0a |  | note | Acceptance Criteria: The following construction tolerances must be achived by the contractor
label | b11622ed-5cd2-5fc5-b3ee-b88317f0eee2 |  | note | – – – – – – – – – –
label | 504f2e35-9158-5e37-85ea-377f504f0b87 |  | note | Thickness of AC ¦¦ + 5mm or - 0mm
label | d229b064-1434-52b3-bfa8-97fa7fd0f75f |  | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
label | ea9db91e-62b0-5ef7-a89e-e882dc5d5bc4 |  | note | – – – – – – – – – –
label | 130fcd22-a538-5c04-9758-8ed7affe4e21 |  | note | Reference Documents: Project Specification Table 4.3
label | 59f91816-2ff5-5331-8d06-63b4228eefdc |  | note | Inspection / Test Method: Verify
label | fcc6895e-5865-5010-a836-20bd86b40127 |  | note | Record of conformity: Conformance Report
label | 145171d8-5533-5fef-ac4a-f6266c0bb115 |  | note | SCP
label | f1c08c99-eec8-5224-828a-749ea9fc7792 |  | note | Responsibility: Site/Project Engineer Surveyor
date | 69758d88-8eeb-5355-b55e-7aac9f515154 |  | date | Date Completed:
checkpoint-group |  |  | section | 6 - Concrete Ramps
checkpoint-status |  |  | checkpoint | 6.1 - Concrete Mix Design
label | a1e92ad0-cdb3-558f-9906-3c669d8ba289 |  | note | Frequency: Each Lot
label | bbd55d15-0331-50f0-a22e-509669cee763 |  | note | Acceptance Criteria: The concrete used must adhere to AS 3600 and must be obtained from a concrete supplier that conforms to AS 1379.
label | e31e801b-ef3c-5540-81b5-3baf9df1d6c4 |  | note | ○ It should possess a minimum characteristic strength of 25 MPa (N25), a maximum aggregate size of 20mm and a slump of 60mm.
label | 7e44a8f9-0f3e-5837-9201-636ea7f75dcc |  | note | Reference Documents: Project Specification Section 5.5.5
label | 2fff5386-c4ad-560c-bb46-3851bccc7b8c |  | note | Inspection / Test Method: Verify
label | a4b2b022-f608-5257-9bc4-8db1dc7991c8 |  | note | Record of conformity: This ITP signed
label | ec2175c3-2c30-5ae1-bddf-c78720ec21fd |  | note | HP*
label | 77425e8b-3d7d-5088-a426-57ba5514372d |  | note | Responsibility: Site/Project Engineer
date | fc268692-1c10-5420-bcc6-bdd3c3435937 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.2 - Reinforment
label | 54278865-8862-5afc-8100-9268106b3290 |  | note | Frequency: Each Lot
label | c9ebf277-ecd0-58ee-81d0-774717b4c9cb |  | note | Acceptance Criteria: Reinforcement to be SL72 Mesh as per the drawings
label | 2cccbfab-e896-5036-81e8-5a1746dc6f27 |  | note | Reference Documents: CV-130
label | d99bf0ed-004b-5f5d-a983-49e3d6b928ce |  | note | Inspection / Test Method: Verify
label | 1037451b-e8ac-5a80-82f8-e7dd01737a39 |  | note | Record of conformity: This ITP signed
label | 82e4525d-e6e7-575a-bf14-bba9278f21c8 |  | note | IP
label | 15469c2f-4142-5ed7-8682-98f039147ef9 |  | note | Responsibility: Site/Project Engineer
date | 3400806c-b741-51c6-870d-62f1bb44bddc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.3 - Placement
label | 01117ba7-838c-5488-92a5-470944f61229 |  | note | Frequency: Each Lot
label | ad844cc9-c367-5e50-901d-439ff5727e8b |  | note | Acceptance Criteria: Contractor to ensure concrete is adequetly vibrated during placement.
label | e413e90e-705e-5af9-a91d-e4e672ef5215 |  | note | Reference Documents: Work Procedure
label | 410384a3-f631-5353-89b0-3e13911b4d94 |  | note | Inspection / Test Method: Visual Inspection
label | b2840b0d-54f1-5d82-9bc3-889377affa5c |  | note | Record of conformity: This ITP signed
label | 88cb1043-a898-5c12-a549-a0e8b3ea655e |  | note | IP
label | 1809e0ce-68c3-5a3d-9192-21b141964c25 |  | note | Responsibility: Site/Project Engineer
date | 3a2b2c5b-8847-5721-a3cf-4ea4a81f8a78 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 6.4 - Tolerances
label | c87d545a-0b5d-5461-9302-b34ab183d3e7 |  | note | Frequency: Each Lot
label | e5fcf028-390b-54fb-92a8-afc6f539568f |  | note | Acceptance Criteria: Concrete to adhere to the tolernaces of a class 3 finish
label | a7b7d3d9-75b2-58a7-9156-110ef4634798 |  | note | Reference Documents: Work Procedure
label | 434bc447-d542-5b07-94d8-81b30f8045fa |  | note | Inspection / Test Method: Verify
label | c0ff09ed-bfd3-5549-bb8e-cc123f4dc017 |  | note | Record of conformity: Conformance Report
label | ba632028-7297-5c3f-800e-75fb4d50014e |  | note | SCP
label | 6f3a9872-8f92-551a-84b9-b6f4cb160ced |  | note | Responsibility: Site/Project Engineer Surveyor
date | 11048e5e-f12d-521b-9cb9-38f515b093d2 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 24d95d55-e9f0-5c99-acf3-3c4de57b5893 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | b1b7c6eb-961c-5912-930d-8676d19dbe9c |  | textbox | Print Name:
text | 75809418-c2a1-5e00-aa65-9e584d55dbff |  | textbox | Position:
date | 6586e8b3-7387-53e8-8c9f-de21217f1bee |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-011 - Earthworks - Cut, Fill and Subgrade Preparation | itp |  |  |  | Yes | GT4-ITP-011 - Earthworks - Cut, Fill and Subgrade Preparation | aec322a2-b1d6-492c-bc7b-0cb64026f1fd
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 8a753a8c-32ed-508a-a5e8-6e2bfe58c5b9 |  | note | Frequency: Prior to commencing any activity
label | c42f3869-07c8-5153-90ff-5e0143b3193a |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 2b0cf2c0-a866-5033-9758-b7369b3c7414 |  | note | – using Issued for Construction (IFC) drawings
label | cf519249-9729-5d79-bb99-9a5f378b4847 |  | note | – using the correct and complete set of drawings
label | e924bb3d-7a8b-5545-84c5-5904b538040c |  | note | – all drawings are the latest revision
label | d0b14467-b6b8-5722-b1b6-37f5c9fb519f |  | note | Reference Documents: IFC drawings and drawing registers
label | fb81552e-e241-5740-8f85-4ed3db28727e |  | note | Inspection / Test Method: Document Review / Visual inspection
label | d6c677cc-c64b-5f7e-9d68-ce1f3f102ddb |  | note | Record of conformity: This ITP signed
label | 4d49f17a-5390-5422-9a54-ac8c67665edb |  | note | HP*
label | b2881af2-af0c-5606-bf90-4be4641044f4 |  | note | Responsibility: Site Engineer
date | 8e24da28-cc5f-5d5f-9710-9dad3a0f1288 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | a5ef81ca-b524-5c2c-a4f4-a4f5d2a0cb95 |  | note | Frequency: Prior to commencing any activity
label | 6d192dcb-b22b-5113-af61-0ce10a2e0600 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: OHSMP, EMP, TMP, SWMS & WP. Access and egress inspected and assessed for stability.
label | 81e673ad-b2f3-58d5-9605-95352dd20cd0 |  | note | Reference Documents: OHSMP, EMP, TMP, SWMS, WP
label | d9d9e7a2-b9d7-5b56-ba2b-08bb5edb5812 |  | note | Inspection / Test Method: Visual Inspection
label | 62d4ab43-04db-5417-95a5-cda6c300e22d |  | note | Record of conformity: This ITP signed
label | ac5d067c-8d0a-5318-943e-78c75095adcc |  | note | HP*
label | e64cd76b-0cc9-5948-8cc5-49a3167bedb9 |  | note | Responsibility: Site Engineer
date | c1c13eec-0449-5fb6-8a32-582b5a246cfd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Survey set-out
label | 7edc15ba-478b-539a-8f22-7bbdb7b7a152 |  | note | Frequency: Prior to commencing
label | b0b5decc-6e94-5f3b-8dc2-e02a66350470 |  | note | Acceptance Criteria: Prior to any excavation, the general areas within the definded limit of works as part of the Early Works package, and site works within the contract shall be set out by suitable hurdles, pegs or markers.
label | 1b6f5ea3-e5a6-54c3-a49a-1bea0f2ec3f9 |  | note | • Levels shall be established and pegged from a common datum.
label | 520b5e53-21aa-525b-8207-b8b780b6f9cb |  | note | • All setting out shall be carefully checked against the drawings prior to commencement, and any discrepancies clarified before construction commences.
label | dbc6728e-ba1a-5ea7-bbf8-4b7d0e38e5ca |  | note | Reference Documents: C.2.3
label | b5123fb9-9568-5498-bd9a-1f0529608528 |  | note | Inspection / Test Method: Visual Inspection
label | 36326ea6-fe40-5b0b-9810-71981a10441c |  | note | Record of conformity: Survey records and pegs on the ground
label | 36bc7d3b-7776-5c3a-aa75-9d6b9b033687 |  | note | IP
label | 48fa4998-1e6c-570d-b1f8-c64742bbcc8f |  | note | Responsibility: Site Engineer
date | bb9b68a8-058e-5494-b3d0-6781a6e1b27c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Ground Penetration Permit
label | 5ebe2ab6-eef0-5a03-869c-506fe6f45d82 |  | note | Frequency: Each Lot
label | 0ad29418-fe60-552d-b4b8-a6ece47b2406 |  | note | Acceptance Criteria: A ground penetration permit must be issued prior to excavation commencing.
label | 2855f87f-2961-5219-ad35-b83439cbc040 |  | note | • Plant and equipment must be appropriate for the task.
label | d482a422-7721-52ae-a326-2ef568f27ef2 |  | note | • Excavation operations shall not disturb areas outside the limit of excavation.
label | 957b70f6-a0ce-5a32-a81a-043ced4f8963 |  | note | Reference Documents: Ground Penetration Permit
label | 41b81796-4c96-5c73-a7d0-62d8bc575fde |  | note | Inspection / Test Method: Verify
label | c93fc0d9-5c17-5ad3-bc34-c7eb7615da4b |  | note | Record of conformity: This ITP signed
label | 8bc60e1d-c7ab-54bc-b812-c43e2ad76e17 |  | note | IP
label | 92bfce06-f9ec-5ab3-856e-3c4cfcd8e455 |  | note | Responsibility: Site Engineer
date | f721063e-a74f-5fb7-a3a7-4d0807a29e9b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.5 - Protection of Services
label | a769e836-8113-5f83-9569-dc3a48e3d435 |  | note | Frequency: Prior to commencing
label | 5274e7a8-8d96-57a6-bf7c-b8a8090d614a |  | note | Acceptance Criteria: The Contractor shall and all personnel on Site shall familiarise themselves, under his direction, with the location of all existing services on and adjacent to the site.
label | a408c880-0a29-5d04-9216-ec2043021471 |  | note | • The existing services shown on the Drawings may not be representative of all services within the site of works. It is the Contractor’s responsibility to locate all services both in plan and depth to avoid damage and disruption to authority assets
label | 929fb532-55fc-5630-b7fe-cf8991c1733c |  | note | Reference Documents: C.2.4
label | 70bcff31-c718-5818-aef3-db968dd69f92 |  | note | Inspection / Test Method: Verify
label | 07fa7767-8708-50be-965b-b149e3aaa20e |  | note | Record of conformity: This ITP signed
label | 856f1b3a-3c55-5639-b251-4ef0720bc2ce |  | note | IP
label | 1a489b96-fb5a-5776-9f07-5f17b1ed9a00 |  | note | Responsibility: Site Engineer
date | baf66c69-f27c-548a-bcce-9453160e54ec |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Earthworks
checkpoint-status |  |  | checkpoint | 2.1 - Material Categorisation
label | ce83bdd3-7270-5799-a2e0-35357967c119 |  | note | Frequency: Each Lot
label | 8291658a-9709-5da2-a467-e35aa8f3406b |  | note | Acceptance Criteria: Prior to commencing excavation in any area and during excavation work, the contractor and Superintendent shall inspect and agree upon the type / category of material encountered
label | 3c035d91-1290-593c-b57f-2693fbd2d84b |  | note | Reference Documents: Work Procedure
label | 60216bfe-ee2b-570c-a243-958b3cdf6de1 |  | note | Inspection / Test Method: Verify
label | 9d9847ce-b410-5ace-8f48-ad2d970b4bb5 |  | note | Record of conformity: This ITP signed
label | 4d6477f1-1430-508c-b4dc-c95479a78e17 |  | note | HP*
label | 8edc43ef-10b6-54dc-b7e2-7b78b7af9347 |  | note | Responsibility: Site Engineer / QAV
date | 8916c340-f4ac-5142-96b0-00fb572ae6ad |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Stripping of Topsoil
label | fbd81d6c-c5e0-5989-a79d-24f9aca982b0 |  | note | Frequency: Each Lot
label | fb68dfbb-ec36-544e-8c48-d6349fd807e2 |  | note | Acceptance Criteria: Topsoil stripped to full width of the formation and placed in approved stockpile location. Stockpile shaped to shed water and stripped surfaces graded to be self draining.
label | f20f4fe0-865f-531e-a4f3-0a4700707d12 |  | note | • Spoil from site to be taken to 15-alpha in accordance with CEMP
label | d94ed560-57d2-56a5-8ffc-f802e7033118 |  | note | Reference Documents: Work Procedure, CEMP
label | 97e05e36-5e00-5dbe-9ee8-9bb66ae97487 |  | note | Inspection / Test Method: Visual Inspection
label | f507f5c2-ff06-5852-ac19-b4534b9fe3c5 |  | note | Record of conformity: This ITP signed
label | 4d5f313b-4091-5ecb-86bf-0efd9d212ab5 |  | note | IP
label | f9ee4709-0b47-58f8-b01f-3a8be41460ea |  | note | Responsibility: Site Engineer
date | 5515fcd0-8e6d-5a08-a1db-f35691e0a00f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Protection of Works
label | 29843573-7a90-5e7c-9b15-ef5792e0f692 |  | note | Frequency: Each Lot
label | df28280f-fa16-50dc-8817-bfc654ca5437 |  | note | Acceptance Criteria: Temporary earth drains shall be constructed where necessary to prevent water flowing onto the construction works and to take away water from the works. These drains shall discharge into a permanent outfall. Pumps shall be provided where necessary to dewater excavations.
label | 6c855eb6-94cd-56e4-9e28-44638e82b48a |  | note | Reference Documents: C.2.7
label | 1c6d4f7f-9dcf-576d-aed4-76d69951a4db |  | note | Inspection / Test Method: Visual Inspection
label | 3ea845ba-da52-5bcf-9ea5-7be7d604acef |  | note | Record of conformity: This ITP signed
label | d97ad8b1-c46f-58f7-a04b-f08fe2678473 |  | note | IP
label | e0f6094a-811f-5d4f-90e6-4d43109ef4b1 |  | note | Responsibility: Site Engineer
date | 5a4710ec-3357-5454-a5c5-e5aff38a2f50 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Unsuitable Material
label | 47ae15c4-7f2d-5e18-8379-4775258b96fe |  | note | Frequency: Each Lot containing unsuitable material
label | d486f079-9b24-5ce8-9874-6328c6482684 |  | note | Acceptance Criteria: Subgrade to be free of soft spots; if localised soft patches are encountered an additional 150mm of excavation, replaced with subbase material shall be undertaken with survey records showing extents.
label | 73d45e68-5733-5297-b6f8-2f89b712254c |  | note | • If multiple soft patches identified, contact Superintendent for assessment prior to undertaking further measures.
label | 9d725849-13d2-5575-b75d-de92ae055c79 |  | note | • Should subgrades become saturated any unsuitable material is to be removed and made good with type B general fill and/or lime/cement stabilized as required in order to maintain subgrades.
label | d4b06c43-1816-555a-87d9-b11e978cc00b |  | note | Reference Documents: C.9.2 EW-CE-DRW-007-001
label | a6b3f766-132a-51b9-995f-8b9092dfb4d6 |  | note | Inspection / Test Method: Verify
label | 0eff0246-f9ac-5f22-befc-94188a23dc8b |  | note | Record of conformity: This ITP Signed
label | d5762bbd-2319-583a-b3f6-9a7d755f832d |  | note | HP
label | ed904389-a493-595e-bd51-a437586c4028 |  | note | Responsibility: Site Engineer / QAV
date | 9ecc5999-c325-5aba-825e-f32b76898d92 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Subgrade Material
label | 0cdca440-cc9d-5c76-9c73-69109faccb68 |  | note | Frequency: Each Lot
label | ba4d507f-b661-57e5-be60-23e80f5997bc |  | note | Acceptance Criteria: The subgrade shall consist of a uniform type material, free of soft patches, oversize particles, topsoil, deleterious and/or perishable matter. Where the in-situ material varies then the Construction project manager shall direct any over excavation and replacement with approved material, either from site or off site to achieve a stable subgrade.
label | 1421df49-0232-5fb9-b28e-de5305ec528a |  | note | • The sand filling over the site is considered a suitable subgrade for new pavements and only minimal proof rolling will be require preparation for pavement construction.
label | 04cf0bbd-4c0b-5e55-b0a0-ed0c134fb8dd |  | note | • Note that sands will dilate if over compacted and minimal passed with a smooth drum vibratory roller are only required. Large rollers (>6 tonne) should be avoided to proof roll the sand and sand filling.
label | a1f0a703-efba-5966-ac97-843caa1f8cd5 |  | note | Reference Documents: C.9.2, C.3.2, C.3.3, C.3.4, 4.2 of 7345B
label | 07517649-cba3-5c88-8d78-a6abb09c4602 |  | note | Inspection / Test Method: Verify
label | 107e5d86-f6f8-56e8-9ba1-b76123dbd703 |  | note | Record of conformity: Test Report
label | 612e492e-09a5-52e3-999a-33a0abfe94ea |  | note | TP
label | ea179bad-d02b-5b28-a12b-92d45d9be69c |  | note | Responsibility: Site Engineer
date | f3bd84c3-32aa-5eb3-9d7d-ece03265841e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Placing of Fill
label | ecbf44ca-dd74-5d10-8581-5ae3f2fd7100 |  | note | Frequency: Each Layer
label | b62fb685-68de-5443-9201-cf3494488ceb |  | note | Acceptance Criteria: Fill to be placed in uniform horizontal layers of 200mm maximum depth and compacted in accordance with the requirements of AS 3798.
label | 6d00f8f0-6489-58b3-a9a0-29f010714fc4 |  | note | • All finished surfaces shall achieve a minimum compaction of 98% standard dry density.
label | 207ecbc1-31ef-53cb-aca3-15879f0f07b7 |  | note | • Type A material shall comply with the requirements of Table 1 in C3.2
label | 3493c0dd-4e06-5219-b33c-afb8fde5dae1 |  | note | • Type B material shall be in accordance with section C.3.3
label | 70e368c6-fa08-5e32-b5d2-d42724ead00f |  | note | • Type C material shall be in accordance with section C.3.4
label | a6937db2-95bf-514d-9cee-69b12262ccb4 |  | note | Reference Documents: EW-CE-DRW-007-001, C.3.2, C.3.3, C.3.4
label | 48e51951-5ad6-592d-a31d-cac80fe37adc |  | note | Inspection / Test Method: Visual Inspection / Measure
label | c77cb8cd-085d-5d6b-82b8-3f71e3dc80b5 |  | note | Record of conformity: This ITP signed
label | 7677fc8a-4917-51e2-a92a-afffd82b07ce |  | note | IP
label | 599fa68c-ce61-5aea-9353-7e2c1c4b9598 |  | note | Responsibility: Site Engineer
date | 52170da9-fcd2-5647-acc5-b504523d365a |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Testing and Surface Preparation
checkpoint-status |  |  | checkpoint | 3.1 - Test Rolling
label | 38fe66c5-a365-5625-9c69-ddb596598857 |  | note | Frequency: Each layer
label | a8134dee-e9f3-53c3-8030-ea60742b8dd8 |  | note | Acceptance Criteria: Test Rolling shall be undertaken in accordance with section C.3.8c and the Contractor shall advise the Superintendant when the proof compaction is due to be carried out, giving a minimum of 48 hours’ notice.
label | dba82d60-9c40-51d5-9ac1-a1ee817b527d |  | note | • The frequency of the test rolls shall be in accordance with table 5 in section C.7.2 of the project specification for the relevant pavement layer.
label | 7823000a-eed6-59fb-83b6-121f89372747 |  | note | Reference Documents: C.3.8c, C.7.2
label | 7bc9466a-6985-5eeb-96e1-d4ca5a480990 |  | note | Inspection / Test Method: Visual Inspection
label | 410cd629-83c8-5fb6-9293-c1045de4e018 |  | note | Record of conformity: This ITP signed
label | 6f665fc7-39b4-5854-9af6-f8234ad93085 |  | note | HP*
label | 440b7703-407b-5934-a7e3-d7d44c0dbd7d |  | note | Responsibility: Site Engineer / QAV
date | 2ea3970f-126b-5fc7-ae37-8c8c52fb8632 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Cut and Fill Tolerances
label | b4db88de-9d01-5c5f-9ff0-32cf4b146738 |  | note | Frequency: Each Lot
label | 4bff4cfc-b8df-5993-b25e-d2e22fb61058 |  | note | Acceptance Criteria: The design surface levels are the levels on the completed earthworks including respread topsoil where applicable.
label | e84e8e37-bcb5-5985-8701-1a5443b5c060 |  | note | • The completed earthworks levels shall be –
label | 242eea70-eda5-5a6e-9391-1ca2e072350e |  | note | a. within + 100mm to - 0mm of the design levels where there are no retaining walls; or
label | 184fac46-86fb-5cd6-ad90-7bcc8375cef5 |  | note | b. within + 50mm to - 0mm of the design levels where retaining walls exist, are proposed, or will exist in the future.
label | c3092323-6def-5742-bcb0-5c512d0d69f4 |  | note | • Where material layer thicknesses are specified they shall be –
label | 242c5769-63e2-5776-822a-1f89e214eb30 |  | note | a. within + 100mm to - 0mm of the design thickness for Type A1 – Structural Fill (Sand), Type A2 – Structural Fill (Gravelly Sand) and any other material described as ‘sand’ or ‘structural fill’; or
label | 5b73f172-382d-5519-8715-a97934c5aae3 |  | note | b. within ± 50mm of the design thickness for all other material types.
label | c0b0bcad-478f-5278-aa8a-13b47944a16e |  | note | Reference Documents: C.3.13
label | 8237b385-26cb-5fc8-b5c2-6e01f839ece0 |  | note | Inspection / Test Method: Verify
label | e7aa02ec-1f81-546d-877d-3af92f642aff |  | note | Record of conformity: This ITP signed
label | 2e6ff8ad-14b0-5eea-b64d-27b85c7d0a74 |  | note | SCP
label | 7803e90e-33fe-50bc-94a1-55fd212827d0 |  | note | Responsibility: Site Engineer
date | 4c214dd0-1010-5b4f-969a-a6a05ef42c53 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Subgrade level conformity
label | 3317ebf9-cefa-5d7f-9225-359144877b7e |  | note | Frequency: Each Lot
label | 0548c9cc-88e1-554b-8098-d97f5f0c5842 |  | note | Acceptance Criteria: Finished subgrade level tolerances to be + 5mm or - 30mm ( +0mm )
label | 54f6cf2d-d0e0-579b-acce-52069b2dfbe9 |  | note | Reference Documents: C.7.4
label | b44d117a-9934-5139-bf8d-b8ff6f0148c3 |  | note | Inspection / Test Method: Verify
label | 40095d68-8974-5eba-9fa1-d2d78add7428 |  | note | Record of conformity: This ITP signed, Survey report
label | c05a09aa-d417-590e-a8c2-0daf00fe7774 |  | note | SCP
label | 7937a92c-f105-594e-ad1a-76b09367f7d1 |  | note | Responsibility: Site Engineer
date | 4095b6d9-c51d-55de-80df-942b922fa99b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Fill Material Compaction & Moisture Content Requirements
label | 8a98538a-c85d-5d49-8283-586195fcc937 |  | note | Frequency: Each Lot
label | f84b1433-e624-508b-a4e2-636d1ecccf6c |  | note | Acceptance Criteria: Sub-grade shall be compacted to not less than 100% of the standard maximum dry density to a minimum depth below the surface of 300mm. The moisture content of subgrade is to be +/- 2% of Standard Optimum Moisture Content (OMC). Sub-grade to be formed to grade, crossfall etc. to ensure that an even thickness of pavement can be finally achieved.
label | aa651028-2dbc-5985-bd4a-59a8f712301b |  | note | • No further stage of construction to be commenced until the completed sub-grade has been inspected and approved by the Superintendant and the Local Authority.
label | 30868bce-3995-5b99-bcad-150316d4ce85 |  | note | Reference Documents: C.9.3
label | 26e90d24-44e1-5e7a-8d2f-dbb15edc8142 |  | note | Inspection / Test Method: Verify
label | b7499868-ca46-5e95-ac34-755ecf4177ee |  | note | Record of conformity: This ITP signed
label | e6fba524-2b9f-599e-b872-14920276fd01 |  | note | HP
label | f873c024-b288-56fb-9f49-1405440dbaed |  | note | Responsibility: Site Engineer
date | 6b207a5d-90ba-5e0e-bbf0-c52da94af63a |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.5 - CBR Testing of Subgrade
label | 29a388cb-b98a-5982-82cb-ca26558e807b |  | note | Frequency: Each lot
label | 228937c9-715f-5ef1-9b3f-447ce2674e68 |  | note | Acceptance Criteria: Contractor shall test subgrade for minimum California Bearing Ratio (CBR) at frequency nominated in Table 5 to ensure the site CBR conforms to design pavement assumption. The minimum site CBR is to be 5%, unless noted otherwise.
label | 1c8d5274-f171-57d4-addb-5fb231329bc0 |  | note | Reference Documents: C.9.2
label | 208d6a71-5ff1-5da1-9024-ec4fb5487904 |  | note | Inspection / Test Method: Test Point
label | a9872cad-fff7-590e-b59f-581e22e3cd85 |  | note | Record of conformity: This ITP signed
label | b2827fdd-77b8-52bd-ba03-c8dd3f172f83 |  | note | HP
label | 0b359fd9-c0ed-520e-a29e-6c806c4e873c |  | note | Responsibility: Site Engineer
date | 7eeb6b52-8272-5cfd-bae3-070be925b15a |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Final Inspection
label | 6854f9a3-6f35-52f7-b061-e423bfef5637 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | e5551857-a6b5-591c-92e0-8528bd121987 |  | textbox | Print Name:
text | 5497683b-28f6-5455-8f52-0d9d9cdccbe9 |  | textbox | Position:
date | 6cfc5d4e-dbcc-5606-bcb3-0606f9f8c04b |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-013 - Precast Installation | itp |  |  |  | Yes | GT4-ITP-013 - Precast Installation | ba7014f6-72dd-4544-8a5f-f69aeb6eb8af
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check that current revision drawings are being used
label | 753fafc5-2890-57d0-a449-ffe0d39f692d |  | note | Frequency: Prior to Commencing Work
label | 50636f26-673d-5673-b0d7-4e1d32c63643 |  | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
label | 7c33f1b4-013e-5ac9-b029-99596aa3c6c6 |  | note | Reference Documents: IFC Project Drawings/ Drawing Register
label | c01427ed-7fa3-5426-947c-69945bb8e4a2 |  | note | Inspection / Test Method: Document review
label | cea368b4-1c5b-54e9-89ed-db2475be692e |  | note | Record of conformity: Latest revision IFC drawings, ITP signed
label | f5d73643-05b4-5446-b65e-bdebb4879a44 |  | note | HP*
label | c4f0da0d-da6f-52f2-bca5-1b97c0ab7b48 |  | note | Responsibility: Site Engineer
date | 204cf5d4-10cb-59e3-8f2e-2bf6490aa9e4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 59a7d250-2c36-5e30-adfc-5efb9627b0ab |  | note | Frequency: Prior to commencing any activity
label | 0265309f-024c-55e3-9251-f1b219d88f65 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | 9d80ea24-0a0e-5683-a242-12eea23314eb |  | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
label | 6c372cc1-3ad7-5b71-8db3-3b3cd2c87992 |  | note | Inspection / Test Method: Visual Inspection
label | e7c5bfd9-065e-5111-a40e-4340404e2d32 |  | note | Record of conformity: This ITP Signed
label | f08ea14c-b56c-5fbe-a5cb-a01508ed445b |  | note | HP*
label | ee4ca9af-77b9-51cd-bd55-915c9003377b |  | note | Responsibility: Site Engineer
date | acd59700-bded-57c8-b46d-a57c7a54b6ff |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Material Conformance
checkpoint-status |  |  | checkpoint | 2.1 - Materials & source Approval - In-Situ Pits
label | d66fbf9b-abfc-5f83-81b1-3d301bcc7990 |  | note | Frequency: Prior to works commencing, 1 per delivery
label | e05de1c3-2afb-53e5-816a-d0379167105d |  | note | Acceptance Criteria: Precast item resources and bedding specified or as shown on the Drawings.
label | d40a0abb-07ee-52e3-bac7-121b938e0277 |  | note | Reference Documents: Work Procedure
label | dd9bb550-efe5-5590-a6d5-6d873a586ef8 |  | note | Inspection / Test Method: Visual Inspection
label | 99cc8658-a761-5aea-9323-7b722c519881 |  | note | Record of conformity: Receival inspection checklist
label | 3ae34192-c078-5e41-b522-dfebcc6d5094 |  | note | IP
label | e64b5df4-067b-520c-9da4-6bb73c89f1f9 |  | note | Responsibility: Site Engineer
date | c9f172e0-afc3-53ad-92e7-c179b84e7bf1 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Materials & source Approval - Pit Covers
label | d9391d45-e18a-51c0-a5d1-c947d159b314 |  | note | Frequency: Prior to works commencing, 1 per delivery
label | a9011844-9493-5f48-957e-3259a23d0f02 |  | note | Acceptance Criteria: Pit covers shall be either cast iron, precast concrete covers or gratings as per drawings and shall be constructed and fixed to pits in accordance with relevant Tasmanian Standard Drawings
label | 932e4624-b7d1-596a-82e9-0384bbf52954 |  | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.16
label | 484dcac6-12ba-5e4c-b4dd-0dd6cdf46023 |  | note | Inspection / Test Method: Visual Inspection
label | 5e7a1b0a-478a-5a81-bd9c-620c9a84373e |  | note | Record of conformity: Receival inspection checklist
label | f538f3ae-f108-5648-892d-a557bce7accf |  | note | IP
label | 72660bdc-11cd-59d0-bd18-bbbfa85bfd43 |  | note | Responsibility: Site Engineer
date | 634555fc-fd62-5393-adfc-b63b3df4012b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Source In-situ Pit Material
label | d41eb121-e754-54d3-a2cc-4e3760e21753 |  | note | Frequency: Each Lot
label | 855ba1ef-16b2-5979-9a22-4ebe9287cc30 |  | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation.
label | 129f4086-1178-5f45-85af-c9a57dfe3edd |  | note | Reference Documents: C.5.15
label | 7c9cd213-5141-5b2e-90bd-8207a1a835cf |  | note | Inspection / Test Method: Verify
label | 43c53560-f1cc-55e1-a40e-45d4e0024c7b |  | note | Record of conformity: Mix Design
label | 946479b3-6795-52a8-98a9-5e967c2ca2bd |  | note | IP
label | 8c5d7185-859b-5177-8b71-85019abe3af6 |  | note | Responsibility: Site Engineer
date | 16b87657-78b2-57fd-8ffa-2813cecfe1e6 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Installation
checkpoint-status |  |  | checkpoint | 3.1 - Bedding
label | 55edad19-f1d2-5948-9dc1-2f8c99d5db67 |  | note | Frequency: Each Lot
label | aca7bda1-ac72-5b4a-8ccb-d263f6e3e8f1 |  | note | Acceptance Criteria: Foundation and/or bedding as per drawings and specifications
label | 1bfba07b-ef98-52d2-992e-2c1bdd5b23ee |  | note | Reference Documents: EW-CE-DRW-526-001 C.5.15
label | b156478b-afeb-5540-b635-16821f4967e8 |  | note | Inspection / Test Method: Inspection
label | c7b270b3-105c-55f8-971d-94bf796ea456 |  | note | Record of conformity: This ITP signed
label | 26c2f9b7-565b-5b69-9e03-0e1b7606fd08 |  | note | HP*
label | 0a9413ba-6766-5570-b010-735f453ecb8a |  | note | Responsibility: Site Engineer
date | 0ebe8287-2ed0-5067-97dd-b8391b896506 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Installation of Precast Element
label | 9d1ccd08-1981-5091-8905-b1f1377f24dd |  | note | Frequency: Each Lot
label | b3c3993a-2491-5f31-8992-0ca605306800 |  | note | Acceptance Criteria: Precast element level and position confirm with the the deisgn drawings and specifications
label | 5e332f20-cefb-5ec4-96c7-43c3bcb10983 |  | note | Reference Documents: Work Procedure
label | 74ed33ee-4a77-57bf-af99-2414911c644b |  | note | Inspection / Test Method: Verify
label | c2c6250d-387d-53b1-9491-9aff4b630c4c |  | note | Record of conformity: This ITP signed
label | 3756c322-51da-5369-a20c-972027cbc43b |  | note | IP
label | 019540b5-68da-57e7-af3c-d5147b243152 |  | note | Responsibility: Site Engineer
date | 84cb347f-6a37-555e-ae80-fbc8161a9684 |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Cast Insitu Lids/Frames
checkpoint-status |  |  | checkpoint | 4.1 - Formwork
label | f073acf6-7597-5b68-b840-c437a5b18991 |  | note | Frequency: Each Lot
label | bc73d464-bfac-51f5-a5ae-f6174b96b0e6 |  | note | Acceptance Criteria: Pit lids / surrounds shall be constructed to the detail shown on the drawings
label | a7efe8b5-053f-51ba-804d-ad892c850dce |  | note | Reference Documents: EW-CE-DRW-526-001
label | e1e8b855-0697-5584-b44d-bd0ac69395b4 |  | note | Inspection / Test Method: Inspection
label | df11eee0-0d28-5b94-b634-35d32de130ec |  | note | Record of conformity: Concrete pour record and delivery docket
label | b8fb0c21-8ed1-5e22-b018-169a634a1bd0 |  | note | HP*
label | 93447cef-5b63-57bb-a83c-ce250c7c761d |  | note | Responsibility: Site Engineer
date | 68ebbcd3-c7b9-5189-984f-9eb571641e2a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.2 - Reinforcing
label | 4a2b279f-dd66-575d-9991-cc30c6599053 |  | note | Frequency: Each Lot
label | e08f56ce-8efb-5906-a3c6-f7ac9d2ed9e9 |  | note | Acceptance Criteria: Checks
label | 7c7faa7b-1c10-5d17-a5ea-6c6f78c2535c |  | note | – Position and spacing check
label | db8217a3-6eaa-52ab-ab9a-7efa96137aef |  | note | – Cover checked
label | 7355002b-7bc0-545f-82db-e75688c761d0 |  | note | – Reinforcing supports checked
label | 22668c53-a3f5-56c9-94ab-3bd639d97940 |  | note | – Laps at required length
label | 495e0379-4999-5925-a77b-37cfff358a95 |  | note | Reference Documents: Work Procedure
label | ef122e87-c3b2-5d00-b919-bb0c8f252470 |  | note | Inspection / Test Method: Verify
label | 141e00d0-4193-5881-aa63-b07648a8cf43 |  | note | Record of conformity: Completion of prepour inspection checklist
label | 0994d67c-02dd-5c24-b9d7-de133fdb823c |  | note | IP
label | 5fb0862e-45f9-59b0-b40c-075eeb97af2b |  | note | Responsibility: Site Engineer
date | 9e9c22cc-73cd-5ed4-9a97-cb66a5b7933d |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.3 - Concrete Pour
label | e97f2b53-2710-5a4f-adf1-9675722a8fa4 |  | note | Frequency: Each Lot
label | 625b28af-dd09-5ce7-ab2f-5e132389fbdb |  | note | Acceptance Criteria: Precast concrete cover or cast iron concrete infill as specified
label | ca4b47ca-b9c8-558d-95b4-0c258cf35375 |  | note | Reference Documents: EW-CE-DRW-526-001 AS 3996
label | aa959aa1-ffd5-58aa-9870-72dab3f35de0 |  | note | Inspection / Test Method: Verify
label | 9db2c58d-33e3-50a2-b682-7874e7f592cf |  | note | Record of conformity: This ITP Signed
label | 696f116e-4568-5631-a06a-d90d96ead30e |  | note | IP
label | 5144279c-531d-54f0-b834-2b621a51ea56 |  | note | Responsibility: Site Engineer
date | 464c29ae-5159-5b0d-8707-eb190100ad66 |  | date | Date Completed:
checkpoint-group |  |  | section | 5 - Post Pour Details and Inspections
checkpoint-status |  |  | checkpoint | 5.1 - Allowable Tolerances Level & Alignment
label | fd1e9255-ab08-50c3-9f2c-001ba8a31a68 |  | note | Frequency: Each Lot
label | 70c461e9-f9f1-5e0b-9aee-be8c196769b3 |  | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
label | f1dbd24f-9f3e-5ec9-ae20-927d09802857 |  | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
label | 777866b0-915b-5e3e-b1bf-0e8b63bb5e2c |  | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
label | a41ed93c-db2c-56e0-b6ee-b8fc0a204e06 |  | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
label | e90d4087-3829-5727-8229-95cb70ebf9e4 |  | note | • As-built survey completed for lot
label | 89ce1372-07d3-51eb-8650-7409aa66233c |  | note | Reference Documents: Work Procedure
label | e21f364e-b121-5426-b8ff-09a8877b8100 |  | note | Inspection / Test Method: Verify
label | f3bc41d3-d262-5e23-b17a-82e1d092a57d |  | note | Record of conformity: This ITP Signed
label | fa99de08-c9ad-5bfe-9ae6-52a833d69ae3 |  | note | SCP
label | c659276d-468b-59ed-883f-196cb1b2d030 |  | note | Responsibility: Site Engineer
date | 586e4ac4-edf1-59bd-b53a-d83c667688c3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - Backfilling Around Pits
label | 3c6fa6ba-407f-583b-8ae7-8d376870f628 |  | note | Frequency: Each Lot
label | d0f3dc6d-e4b7-5226-84e1-5af7be6612c4 |  | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
label | 63988e4d-1cb8-5434-97b9-a45d86ce17a4 |  | note | Reference Documents: Work Procedure
label | 80cd381b-74cb-5385-9894-eaa28d3a058a |  | note | Inspection / Test Method: Inspection
label | 34129f55-8527-5582-b253-f041d1ac1f28 |  | note | Record of conformity: This ITP Signed
label | 82947586-0aa3-5552-800f-e4c154e60fb8 |  | note | HP*
label | 6a49d771-fc66-515b-b026-9a73cb82dc34 |  | note | Responsibility: Site Engineer
date | 0757f158-078a-502f-9afb-6aaaef932992 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | af04b244-1f71-5088-8f02-1aee8fb2d4bb |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 27e28587-0ae1-5033-aed9-c49c050ff5f4 |  | textbox | Print Name:
text | 802b9a3c-b487-5f26-ae7e-6e281cae9de1 |  | textbox | Position:
date | fb767570-3e5c-538c-a294-1cea7ea57ca7 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-004 - Subsurface drains | itp |  |  |  | Yes | CTN-ITP-004 - Subsurface drains Rev2 | c3fe24dd-2a8f-4cb2-84ed-ef0ce32fa027
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 066c1c66-527e-5edf-85db-b4fa3d129d67 |  | note | Frequency: Prior to commencing any activity
label | 15294e71-81ba-5ec6-bd41-794da91f4ad4 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 836eacac-f35d-598d-8051-be285566b557 |  | note | – using the correct and complete set of drawings
label | 5e86b593-c5a2-5b00-9823-e46a71d6206f |  | note | – all drawings are the latest revision
label | 1ce295f7-92fb-5df3-8558-0c13e867b61a |  | note | Reference Documents: Drawings and drawing registers
label | 7231819a-e7ab-5f44-8dfd-9868b1ac515a |  | note | Inspection / Test Method: Visual inspection
label | 21a8c96d-5095-52bb-82c5-4034b0eea45d |  | note | Record of conformity: This ITP signed
label | 9f92c5a6-adb4-57fc-aa27-58d311622011 |  | note | HP*
label | 6ef9ea82-8d28-5828-a28d-693c2995d65a |  | note | Responsibility: Site Engineer
date | cb81760a-5d17-54e0-aeb7-90a4af7b75bd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | b4b69718-0ada-5175-bf8e-195d76c0ab86 |  | note | Frequency: Prior to commencing any activity
label | 64f982b5-547d-5b3f-89bf-042fafa0e0c2 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | cd8a8d99-c199-523b-ba1e-04f4f0f5d1bd |  | note | Reference Documents: PSP, EMP, TGS, SWMS, WP
label | b6698a67-4012-5785-83ec-7254f2a0c55f |  | note | Inspection / Test Method: Visual Inspection
label | 31e4b749-8803-5ce5-b474-3956bb3661ba |  | note | Record of conformity: This ITP signed
label | b5e67521-d4f2-5244-9ec0-fb3734ee817d |  | note | HP*
label | 2406c6f2-1f05-59bf-a570-6559757580d2 |  | note | Responsibility: Site Engineer
date | 3bc32fbf-ed50-5aa3-8acb-ed6a1368be8a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Material Classification
label | 6bb0979c-a500-5e4d-a787-81dade59b41f |  | note | Frequency: Each Lot
label | 31205855-17c8-53d0-b487-0591fffbb542 |  | note | Acceptance Criteria: Pipes supplied shall be of the category and diameter shown on the drawings
label | 8c278112-9fc3-556f-9648-afbea616fa34 |  | note | ○ Material shall be as indicated on the project drawings and / or shall conform to the following:-
label | 6da18bd8-1a07-527f-88cd-db7036ce1528 |  | note | • uPVC slotted spigot and socket sub-soil drainage pipes.
label | 10a172b1-69c0-5ef9-b464-e1fd6c4aa12c |  | note | • Fibre reinforced cement slotted spigot and socket sub-soil drainage pipes.
label | c5ff248f-b7f3-5192-b420-7e3b2fff5e39 |  | note | • Perforated corrugated polyethylene continuous tubes.
label | fb12a958-8449-55c8-9f28-b2dacedb74c3 |  | note | • Geo textile must be of A34
label | 57824b9c-5ef5-555e-a7d2-da0f81b571c6 |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.6
label | 6df6de4c-e44a-5338-bcd7-e47257668333 |  | note | Inspection / Test Method: Verify
label | 38e7c521-3d9a-563c-b3c5-01f0038a8b6b |  | note | Record of conformity: This ITP signed off
label | 63383860-ebed-5696-aabd-0e2e0e5ac0ae |  | note | IP
label | 69594c20-b21d-5cdc-929e-fb7b227adb18 |  | note | Responsibility: Site Engineer
date | b4402950-949a-5fb5-b378-f752076667c1 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Construction Works
checkpoint-status |  |  | checkpoint | 2.1 - Excavation Permit
label | ee206293-ff7b-53b4-bd93-9a5afe509338 |  | note | Frequency: Each lot
label | 34626b58-ac0b-5242-bc16-84f659b1a819 |  | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
label | 3f17533f-fe4f-55ff-944c-af14eb5bca07 |  | note | • Plant and equipment shall be appropriate for the task.
label | af0576a7-824f-5f19-9de1-0739ff79b5b2 |  | note | • Excavation operations shall not disturb areas outside the limit of excavation
label | e44d5cc5-62c0-5c31-b0bc-ddaa89f7399f |  | note | Reference Documents: Excavation permit
label | d938083f-d61a-591d-a0f7-f34372d42457 |  | note | Inspection / Test Method: Verify
label | 6c7ec06e-5a6e-5b17-ac72-bdc19b0761d6 |  | note | Record of conformity: This ITP Signed
label | 5048d548-5f16-5508-b9ba-28813e569702 |  | note | HP*
label | d531d991-8375-5407-98e6-0365f70c41db |  | note | Responsibility: Site Engineer
date | e182dd78-2243-5733-82d7-5331c3cc8730 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Outlets
label | db7cd0de-58ae-5b52-acbd-fbfd14f46adb |  | note | Frequency: Each lot
label | 9fca74b7-50b5-59d3-84dc-e70309b239b1 |  | note | Acceptance Criteria: Superintendent inspection of proposed underground outlet location. Outlets shall be installed through walls of pits, provided inverts are not below the top level of the outfall drain.
label | 039658fc-58e8-5256-953a-95e26b8ab753 |  | note | Reference Documents: C.6.2
label | 082dd875-647b-5013-8b42-25ce739e1dc0 |  | note | Inspection / Test Method: Visual Inspection
label | 00f8a321-ac06-5c91-a663-288052d39877 |  | note | Record of conformity: This ITP Signed
label | a274c574-5fe9-5f1d-b3ad-ecccaf1d5905 |  | note | HP
label | 201fdf7f-45d1-55cf-b893-25041fd4b40c |  | note | Responsibility: QAV
date | 9f04623b-9d0b-509e-bf37-d8b9e6635c21 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Excavation of Trench
label | 2f38a7e6-4789-53fa-a209-aff1ddd10aa2 |  | note | Frequency: Specification for trenching
label | 11beb9f4-8441-5718-9775-828ca6758d35 |  | note | Acceptance Criteria: Excavations for sub-soil drains shall conform to the requirements specified for excavation for services subject to the following specific requirements and modifications:
label | 1caf37e0-8d3a-5ec0-ad14-19f2e95fd0a8 |  | note | • Trench depth and width shall be as shown on the Drawings.
label | 9d9604aa-91a7-5535-829b-5dc4b90f3f33 |  | note | • Trench bases shall be uniformly graded to an even fall as necessary to suit whichever of the following is applicable:
label | 213bb479-554a-5941-93c9-b08b20700e56 |  | note | • Parallel with pavement or kerb and channel formation grade.
label | 1f7af9b0-73a3-5052-a917-715666c5b79a |  | note | • Parallel with overall grade of stepped footings.
label | 25d7b47d-c806-5b26-bdc4-263249c20061 |  | note | • Not less than 1:250.
label | 2a22d377-d1aa-50dd-9c7c-d156fd4157b5 |  | note | ○ If it is not possible to conform to any of the above requirements, the Contractor shall notify the Superintendent and await direction before continuing with the affected part of the work.
label | fb954c4e-9791-50f0-8eac-e739362a4bee |  | note | Reference Documents: C.6.1
label | bd6239be-a2a5-5329-a081-9e3015306a4f |  | note | Inspection / Test Method: Visual Inspection
label | 9699a788-de13-51f6-a4be-839088556fa0 |  | note | Record of conformity: This ITP signed
label | e30d51cc-9904-5da0-970f-d94093d61f13 |  | note | HP
label | b134ba3b-7e1c-5b41-a1d6-da1be3891e2e |  | note | Responsibility: QAV
date | b0779713-5ccc-5ffa-8d80-80b00811151f |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Bedding
label | 45d32243-3869-5c32-a7e1-4d5c0aa75a7d |  | note | Frequency: Each Lot
label | 810606ac-be84-5c0f-aa5f-de6019cbdee4 |  | note | Acceptance Criteria: The bottom of the trench shall be well compacted and evenly graded suitable material, 25mm minimum depth of 20mm Class 3 FCR
label | 1eb95854-4a74-512b-acfb-9ae876c30cca |  | note | • If rock excavation was necessary and if the bottom of the trench is uneven, all low and rough areas shall be filled, and solid rock outcrops covered with bedding material to a compacted thickness of not less than 25 mm.
label | 88f78ba3-46db-51bb-9e7a-ac8eba5beeca |  | note | Reference Documents: C.6.6
label | 7f791891-931d-5f13-8fb8-130aea980ca0 |  | note | Inspection / Test Method: Visual Inspection
label | 1943fd58-b7d6-5bec-8464-92ed18f1d9eb |  | note | Record of conformity: This ITP signed
label | 6e90e220-3cf8-5e88-82a9-a88e694e0877 |  | note | IP
label | d7b59c46-dbcb-52ff-975e-7f1828b48309 |  | note | Responsibility: Site Engineer
date | 7d734e67-2ae9-56f2-845a-c69cec12cd7f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Placing pipes
label | ceea5b4c-669d-544e-b84f-2be357aea98b |  | note | Frequency: Each Lot
label | 5e2c6a3c-0073-54e5-a28b-eff2d78c3046 |  | note | Acceptance Criteria: Sub-Soil drain to be 100mm Dia. PVC Class 1000 Agricultural drain.
label | f2f2a9e6-199a-541e-8789-6192226975f2 |  | note | • The pipes shall be laid true to line and gradient on the graded compacted bedding.
label | 176f374f-7d1b-507c-be2b-85c4841e5e21 |  | note | • Pipes shall be jointed to fit tightly by pushing the spigots firmly into the sockets. For pipes without sockets, special end jointing fittings shall be used.
label | 57d10afe-3d32-5095-9962-8466b44d5b0c |  | note | • Fittings shall be compatible with pipe material.
label | 9dae1d03-420a-50f1-abdc-1ab2cdd545cb |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.6.4
label | e523941d-d358-5177-9e96-6b22b32499c4 |  | note | Inspection / Test Method: Visual Inspection
label | ad7a8e2a-ca4b-5861-b0e0-1e99a367daca |  | note | Record of conformity: This ITP signed
label | 34f4b0da-8c21-595e-ad5c-a726f429074c |  | note | IP
label | b403f513-7a49-5bcc-a9a6-e2ceddd3fba5 |  | note | Responsibility: Site Engineer
date | ed4d8c78-c283-5053-9305-b766fa00266e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Backfilling
label | 12942b0b-54d8-576a-9eb8-d74ad450bc13 |  | note | Frequency: Each Lot
label | 04022310-23a4-5f89-adb0-a9dc5156f7dc |  | note | Acceptance Criteria: Superintendant inspection of Subsoil drain backfill prior to covering
label | 1d2fc924-48f4-54bd-8dab-f3954d8d74fd |  | note | • Backfill needs to to encase subsoil drain and cover upto 150mm over to allow for sediment collection.
label | 858383f0-6745-5622-b743-f18625bf69a3 |  | note | • Backfill to be 14mm screenings to subgrade.
label | 3c6dd8e1-4284-573a-b205-af1e3251e6f4 |  | note | Reference Documents: C.6.5
label | bed6fc06-2060-5093-b21f-9440f05f2899 |  | note | Inspection / Test Method: Visual Inspection
label | f9de70b7-2ca1-50dd-bf05-c5b6aeb6fd26 |  | note | Record of conformity: This ITP signed
label | 3fb0279d-65a6-555e-bf95-eac73414bb9f |  | note | HP
label | d7eba938-5900-5b41-8dcb-1aa5acfaa01b |  | note | Responsibility: QAV
date | 66ba9565-34ef-5420-b363-26fec86cda41 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Backfilling
label | 26841da4-db9b-50af-b431-caad4730c580 |  | note | Frequency: Each Lot
label | bb2ffcc1-1543-5ad8-958e-6369c43e47b9 |  | note | Acceptance Criteria: At full depth pavement joints 100ø class 1000 pvc pipe sub-surface drain type 2 with filter fabric around trench (150mm Overlap) with "no fines" concrete filter
label | b621b5c6-d8a3-55ce-b483-91795b9d5370 |  | note | • Material (with 4% cement & compacted).
label | 24e715df-e2e4-535d-8cb5-d62d4e03c37c |  | note | Reference Documents: DWG EW-CE-DRW-416-001 C.6.5
label | 14900efa-e10d-5359-b287-2f1fde2b708a |  | note | Inspection / Test Method: Visual Inspection
label | 59a3c80c-f157-53e9-a215-00b8e08488af |  | note | Record of conformity: This ITP signed
label | 4c5e342c-b8c4-5ee2-b9f9-971e85a8b1b6 |  | note | HP
label | 3b5e06e7-6434-5a0d-93df-9abb94e0f186 |  | note | Responsibility: QAV
date | f14b155d-fe58-5d9a-95b3-4e63700ecf84 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.8 - Access Points and Flushouts
label | f0ba6c71-ee8e-5e43-bd23-73909d0b668c |  | note | Frequency: Each Lot
label | 04c1e4b3-1891-5aaa-829d-e2c6eb12be88 |  | note | Acceptance Criteria: A flush out riser is to be located at the Back of kerb (BOK), comprsing of 100mm UPVC PIPE, capped.
label | a76daed8-ac7a-52a6-a449-7f693bd8a212 |  | note | • Minimum 200m intervals along road alignments, a single flushout points at high point or at locations within WSUD/Raingardens.
label | c43ed8cb-e32d-5fb5-8400-258f3681c94e |  | note | Reference Documents: C.6.5
label | 092e1d17-fa57-558c-a5e1-cfd09eb916ae |  | note | Inspection / Test Method: Verify
label | a54cceae-a483-5d49-bbfa-621f51593b20 |  | note | Record of conformity: This ITP signed
label | 57a09e43-32f0-55fa-a96f-aab8ab896a82 |  | note | IP
label | fffda4ce-135c-51c0-9bc9-8ee79b1c7b1e |  | note | Responsibility: Site Engineer
date | 040bf974-0cb5-5c9a-981a-e3602154a9c1 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Finishing and Commissioning
checkpoint-status |  |  | checkpoint | 3.1 - As-Constructed survey and documentation
label | 76652f08-9752-5e23-935c-12bc23450d03 |  | note | Frequency: Each Lot
label | 0fb1a4d0-a2bc-5777-a2bb-257a72d586f3 |  | note | Acceptance Criteria: The survey shall include pickup of location and depth of installed sub-soil drainage and location of any inlet/outlet/flush out points.
label | e8da6498-b1dc-55b1-866a-9c4d7fdb5300 |  | note | • Lot Maps shall be completed to show the extent of works for each lot.
label | a430d98a-0dc5-5152-8b29-0cd77c9eb516 |  | note | Inspection / Test Method: Review
label | 130b1101-761c-5a91-a2ef-6dadf861ff77 |  | note | Record of conformity: This ITP Signed
label | d11644e6-a9dd-569f-88eb-95d57ecdcdee |  | note | HP*
label | ac89ae7f-722e-5db6-8ac5-758c9c90fcb5 |  | note | Responsibility: Site Engineer / Superintendent
date | 735e2674-34af-50ef-beea-5f280b3c95fa |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | ab6d9a00-47ff-5710-96a9-f6c0cd0ef166 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 64d1a98d-a3bb-57f8-8193-f0b4befc4c7a |  | textbox | Print Name:
text | 0992cef7-ff5e-5402-be02-22926f0fa2a4 |  | textbox | Position:
date | 88ba982b-0bbd-5c6d-bca2-e223d216bbd5 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-007 - Concrete - Footpaths & Islands | itp |  |  |  | Yes | CTN-ITP-007 - Concrete - Footpaths & Islands | ca39093c-3d83-462d-b913-15092ddde6e5
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | cbf56c66-69f8-53a6-b3ac-6cf5bb84bf1e |  | note | Frequency: Prior to commencing any activity
label | d7f2356d-b1bc-5d32-8c56-e39d5ec15a1c |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 605159ba-9af6-5fa1-965c-663efd9d1104 |  | note | – using the correct and complete set of drawings
label | 87885be0-85d6-5adb-8e12-646a42452e12 |  | note | – all drawings are the latest revision
label | 6674f5fb-050b-504b-a132-17f702e63926 |  | note | Reference Documents: Drawings and drawing registers
label | a2f7e8e7-d708-52f2-9d10-25671128fc14 |  | note | Inspection / Test Method: Visual inspection
label | 64772304-fc46-5fe3-b7fc-2d5ca1b71975 |  | note | Record of conformity: ITP Signed
label | 5b38a067-8b42-59a2-a99d-9fc476725eab |  | note | HP*
label | 4de99b6f-41d8-5811-b784-c660f41ecbd6 |  | note | Responsibility: Site Engineer/ Site Foreman
date | 571cc039-c01d-59da-be2c-f09cd342119b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 9e4d7c0b-d7b0-5019-999a-3a99852e3e07 |  | note | Frequency: Prior to commencing any activity
label | f2c3d6e2-5653-58e6-b2b5-b13951ac7f50 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | d3dccbc5-e636-5cf6-b818-f6b55fc56415 |  | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
label | 5bcf9ffa-e7d7-53c5-92be-46c84ff3f511 |  | note | Inspection / Test Method: Visual Inspection
label | 988dd7b0-e766-5fa6-ab11-6360e427c1b4 |  | note | Record of conformity: ITP Signed
label | c8323074-83cc-5ffa-9a24-80f692c3f288 |  | note | HP*
label | 5f8ace94-de04-54dd-9d57-8ab7ef68d2d7 |  | note | Responsibility: Site Engineer/ Site Foreman
date | 88e9102f-85cb-5697-b901-e3370bea6d8b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Concrete Mix Design
label | b353f0a7-95e0-5d23-aaf5-233395b08da8 |  | note | Frequency: Prior to first concrete pour
label | 492dc1a1-1817-5d27-8c6f-705945ca7a19 |  | note | Acceptance Criteria: Supplied concrete pre-mixture for footpaths, needs to be in accordance with the supplied Early Works Civil Drawings.
label | ca529f55-6c75-5302-87f1-7a6c5108c5f7 |  | note | • Unless specified, then concrete used in this construction shall conform to AS 3600 and be provided by an approved pre-mixed concrete supplier, conforming with AS 1379.
label | b47521a8-21d9-5845-9538-d48f3bbdb368 |  | note | Reference Documents: C.11.2 Work Procedure
label | 6b081fa8-5389-52fa-a99e-fdd9c19178b6 |  | note | Inspection / Test Method: Verify
label | 1e007936-0ed0-5143-978b-4e9048d5100f |  | note | Record of conformity: ITP Signed, Mix design approval
label | 6f3218d9-7824-5201-9f1a-d5283fdab8f9 |  | note | HP*
label | e0beebe8-b3a5-5aee-afd4-05dcf2083d64 |  | note | Responsibility: Site Engineer/ Superintendent
date | f4529bec-267c-5064-a22e-a81d4a5a56b4 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Construction Works
checkpoint-status |  |  | checkpoint | 2.1 - Setting Out
label | 093475c1-86b0-51dd-b75b-16ec55d79d98 |  | note | Frequency: Prior to start
label | 8874302d-535b-5090-8541-016b4ac5b67c |  | note | Acceptance Criteria: Set out work in accordance with drawings.
label | 2a1b5ac1-e3ea-5c77-85c8-7d4d5815e746 |  | note | • The Engineer and Supervisor will review and confirm set out with the surveyor.
label | 5b289606-8c18-5172-aab5-e94a75446068 |  | note | • No survey/level pegs to be removed by any persons until completion of works.
label | 7f3dfcf7-2df8-53ea-b654-b719ade5598b |  | note | Reference Documents: Work Procedure
label | 8d9d349b-df72-5d94-83c9-b6ef2ef63067 |  | note | Inspection / Test Method: Verify
label | e4dad96d-aee5-518e-b657-65e8188c648e |  | note | Record of conformity: This ITP Signed
label | c14aa65a-dee3-5359-bef6-4f812365b836 |  | note | HP*
label | e6919ece-ed60-507f-9b54-6b5117be48eb |  | note | Responsibility: Site Engineer/ Superintendent
date | 66533def-ccb8-578e-b435-22268ce16ee3 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Excavation Permit
label | e4bb1142-0f2c-556b-8822-7e1fbe4e1b23 |  | note | Frequency: Each lot
label | 2d2acf94-9bed-57a7-b5fd-3cff3ac7461f |  | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
label | fab75ccc-4e3d-55ed-935c-0e21d093ef66 |  | note | • Plant and equipment shall be appropriate for the task.
label | b161363e-8540-5f24-9d99-ab05c5822611 |  | note | • Excavation operations shall not disturb areas outside the limit of excavation
label | 36553019-bc78-5bdb-af21-9377f59d4168 |  | note | Reference Documents: Excavation permit
label | ee923af1-091b-5289-aa78-cebbf18848c4 |  | note | Inspection / Test Method: Verify
label | 0726336f-f2be-5d18-9913-4d5e77ca524f |  | note | Record of conformity: ITP Signed
label | ef31f98c-c440-576d-87ba-ea9ea87cda69 |  | note | HP*
label | 5962ed19-991a-5423-a41b-a7a402ec614a |  | note | Responsibility: Site Engineer
date | 3c2c0021-6b2e-5889-8a47-29a7e19b5fae |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Excavation
label | 683c0e84-36cc-5dae-8ede-76cd87bdb4d2 |  | note | Frequency: Each Lot
label | 27faf44c-bbaa-57fd-9862-79e6f12c0721 |  | note | Acceptance Criteria: Excavation completed to required depth to allow placement of the bedding layer
label | db2dd32e-be7e-5165-9ac3-040286201b4b |  | note | Reference Documents: Work Procedure
label | c333110b-d6ca-5013-bba7-f74bfb380125 |  | note | Inspection / Test Method: Verify
label | 02aaa8ff-c7fc-5ff9-8518-11e7469d9e4b |  | note | Record of conformity: ITP Signed
label | c65635ad-03ae-5e3a-8726-1c0548b4e84b |  | note | IP
label | e3457cdc-fa09-59da-b85a-dfefee17783b |  | note | Responsibility: Site Engineer
date | a842d2ea-96da-52ae-b233-a8c333c6d37c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Formwork
label | 85b6f0c7-14a9-59d2-b9b2-1f1dea409f34 |  | note | Frequency: Each Lot
label | 0b7b7b7b-40cb-5559-a956-df4d44e07184 |  | note | Acceptance Criteria: Formwork shall comply with the requirements of AS 3610
label | 45491b1e-0524-56bd-8800-1293b9f7ed4c |  | note | Reference Documents: Work Procedure
label | 148c49ef-37ea-57a4-8a77-d238b3b38f3e |  | note | Inspection / Test Method: Verify
label | b591da3f-f5a9-56eb-87d6-53a580ec1398 |  | note | Record of conformity: ITP Signed
label | b44446b6-383f-5240-aa26-1e96373f1934 |  | note | IP
label | f7fe8929-08e6-5964-bf90-ce10032d53af |  | note | Responsibility: Site Engineer
date | 062dc9fd-c6bf-52ea-823e-af9694116aee |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Reinforcement
label | dca09716-2dbf-580d-b897-5101716e5dae |  | note | Frequency: Each Lot
label | e8155fc8-babb-5d55-b2f9-ab24bb797632 |  | note | Acceptance Criteria: Reinforcement must comply with the requirements of AS/NZS 4671.
label | 317a0b71-39a8-5c17-b6ea-d3652f00fef3 |  | note | • Concrete Infill pavement reinforcement to be SL82 mesh central.
label | dbccc8be-2797-5596-b8f9-e0c612669da8 |  | note | • Concrete Footpath Pavement reinforcement to be SL72 central reinforcement.If required to be stopped or cut either side of expansion joint (EJ)
label | b0a1f507-1c16-5dfc-b3ef-9b692ef97ffc |  | note | Reference Documents: DWG EW-CE-DRW-406-001, Work Procedure
label | 392a3afd-2094-5769-b5b9-276462381e0c |  | note | Inspection / Test Method: Verify
label | bca98dfa-7bb6-5b41-8764-8a478504b254 |  | note | Record of conformity: ITP Signed
label | 03b81ac0-e0c5-5131-9018-88561edc567e |  | note | IP
label | 774c49d0-81fd-529b-842b-96dd007f60c4 |  | note | Responsibility: Site Engineer
date | 70a23c65-6a24-59cb-ad2a-76df515a8804 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Concrete Placement
label | c5caf274-421c-529d-a558-924b23521690 |  | note | Frequency: Each Lot
label | ce3d417f-969f-5504-8cbd-957d8d2fe349 |  | note | Acceptance Criteria: The concrete, when placed, must be well tamped to remove all voids and to work fines to the surface for trowelling.
label | 67b9c837-03c7-5cb1-9799-69d0f0481433 |  | note | • Concrete Infill pavement to be 150mm depth N25 concrete
label | 9d3b7869-db60-5c73-8b02-8c68243f948e |  | note | • Concrete Footpath Pavement to be 100mm depth N25 concrete
label | 28c9de28-7983-5d4f-879b-8da617d46c72 |  | note | • Concrete shall be of 25 MPa 28-day cylinder test compressive strength.
label | b4c7b3fc-5546-5192-8216-371769261b2a |  | note | • The maximum aggregate size shall be 20mm.
label | 4ff95096-9ed9-5f5c-a218-067ae01e36ce |  | note | • The slump shall not exceed 65mm or be less than 25mm
label | 690ab3c4-8009-5a88-8b94-0b2dafd2f6aa |  | note | Reference Documents: DWG EW-CE-DRW-406-001 C.11.2
label | f8e8b4d6-6df9-5b00-80a8-7c5455985f66 |  | note | Inspection / Test Method: Visual Inspection
label | 89ec8d6b-5a68-5db1-a0de-f7172299afbd |  | note | Record of conformity: ITP Signed
label | c2ed0857-a2a1-509f-82f6-ad338b56351c |  | note | IP
label | b6c44129-66e8-5403-906b-6a6edcb8d332 |  | note | Responsibility: Site Engineer/ Site Foreman
date | 1afa34c3-339d-560b-a8eb-1116e10eaab1 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Surface Finish
label | 7aea4d90-78a1-5a12-ab56-e00ece3b228c |  | note | Frequency: Each Lot
label | e32c9a09-9b4d-5273-8d07-572f7855a8b7 |  | note | Acceptance Criteria: A brushed finish shall be provided to the surface of the slab with joints and edges polished smooth for 80mm width with jointing and edging tools.
label | 0fb397be-28d6-5f38-b6c8-54b2b94ece93 |  | note | • The alignment of the edge of the path is to be straight and true to line.
label | 2c7e1dce-4a19-587b-a7e2-a0d4de5b4146 |  | note | • Deviations from alignment or from specified width will not be accepted.
label | da098fdc-5f9b-5294-b8bc-9d5c6f71f91c |  | note | Reference Documents: C.11.5
label | 56b865c3-627b-5a75-9eff-030fb15bb880 |  | note | Inspection / Test Method: Visual Inspection
label | c645414e-40a0-58c1-9302-eed1efb8f99d |  | note | Record of conformity: This ITP Signed
label | 9187368c-aa47-579d-951e-b2199110438e |  | note | IP
label | 2299c288-061e-54b5-a0ae-90da6bee08d7 |  | note | Responsibility: Fulton Hogan Engineer
date | 823157be-5822-5e68-acfc-c853db04a052 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Joints
label | 37b8a10c-55cd-550c-818d-4099316b9806 |  | note | Frequency: Each Joint
label | f37e0e3b-514d-52f3-b6bd-bd462ef88d75 |  | note | Acceptance Criteria: Expansion Joint
label | 2c1d2e5c-501d-5f4b-98fd-41b52e617e75 |  | note | • A 19mm expansion joint shall be provided whenever rigid pavements abut fixed structures or at max. 15m centres to footpaths.
label | 315904f9-97a6-54ac-8b0b-4d1f624a01a4 |  | note | • An approved joint sealer shall be inserted in the joint and finished flush with the surface of the path.
label | c24b3eb3-c877-591f-84c7-2d2ad2609c06 |  | note | • Contraction Joints in footpaths and cycleways shall be constructed at 2.0 metre centres for footpaths.
label | a71ec0be-dc08-5da2-a0ba-108879d8b30b |  | note | • Concrete Infill Pavements to have Sawcut/tool joint at every 1200mm (DWG 406)
label | aad7358b-5c4c-557f-bdae-27437cdaac58 |  | note | Reference Documents: EW-CE-DRW-007-001 C.11.3 C.11.4 EW-CE-DRW-406-001
label | 02e10576-df21-59fb-9fa4-907ea1f3c9ea |  | note | Inspection / Test Method: Visual Inspection
label | 1db73c21-6a7e-5031-889c-9361b5fd9a5e |  | note | Record of conformity: This ITP Signed
label | b6648129-ea73-59b4-b3ae-c6ba0621c3be |  | note | IP
label | 3aa1cd31-bb42-5b3d-886c-804eea7f8794 |  | note | Responsibility: Site Engineer/ Site Foreman
date | a57edeb5-9ca9-5d79-a498-19615bb7e733 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.9 - Protection of concrete
label | 03694459-ee8e-5409-8d15-0921cd9626c8 |  | note | Frequency: Each Lot
label | 329f8b89-9bc5-5ecb-adc4-cdf72b59e7aa |  | note | Acceptance Criteria: The finished path shall be protected from damage by passers-by and with polythene film for 24 hours after completion if rainfall during this period is apparent.
label | 168634f0-0b4e-5739-9fe3-998f4dd8428c |  | note | • Barricade, warning signs and lights shall be erected to prevent damage of the footpath from vehicles and pedestrians for not less than 24 hours after completion.
label | 44267cf0-a3cd-563c-a4ec-8e36a981a51f |  | note | Reference Documents: C.11.5 C.11.7
label | 91418a13-f5b1-5c63-aa49-56b2d2115456 |  | note | Inspection / Test Method: Verify
label | f8688878-92fb-5a44-8348-2ec2e827d08b |  | note | Record of conformity: This ITP Signed
label | 5e15c259-861e-5f06-83c6-63f040f444bc |  | note | IP
label | 90ad2dfd-f5d5-566a-807a-dca44f2eb6cc |  | note | Responsibility: Site Foreman
date | 41f4c445-0625-505f-b5dc-fbae9be0cc44 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.10 - Curing - Pedestrian Footpaths
label | 509699da-a5b3-59fc-855c-9aad8561080d |  | note | Frequency: Each Lot
label | 0eadbc34-cb9a-571c-9736-98c541d5c214 |  | note | Acceptance Criteria: The entire footpath shall be protected against loss of moisture for a period of not less than 72 hours after placing by shrouding with polythene sheeting or by spraying with a curing compound complying with AS 3799.
label | 26e63a23-3253-5350-bdb2-92b81b0cdf66 |  | note | Reference Documents: C.11.6
label | 844d02e0-1825-527a-8d12-76cba04ebd68 |  | note | Inspection / Test Method: Verify
label | f42bd934-1bac-5a21-943a-6ec05fe739de |  | note | Record of conformity: This ITP Signed
label | f0f3ebed-5953-5eab-a4ae-5e0a2c23b6be |  | note | HP
label | 592ac158-ad86-5f90-8721-31607197b967 |  | note | Responsibility: Site Engineer/ Site Foreman
date | eeb91fbf-8d60-5c6c-816b-53b1fb63dccf |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3 - Completion
checkpoint-status |  |  | checkpoint | 3.1 - Carry out sampling of concrete - strength and consistency
label | bfdb1e83-d344-5831-95c6-8f66b52764c5 |  | note | Frequency: Each 50m3
label | 54817a57-a439-54a6-ac82-28f3f972c4e6 |  | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
label | 4b97bc5b-6bf0-5727-afde-7ec142083864 |  | note | Reference Documents: Work Procedure
label | 9c38001a-bab1-55ef-a85f-bd8dda2ea688 |  | note | Inspection / Test Method: Checklist
label | 0b843da9-4761-5568-80cf-8bda57d63ac3 |  | note | Record of conformity: ITP Signed/Test Records
label | 0bce7b53-001b-5971-a220-1c5379534c6f |  | note | TP
label | 8dd2e373-d340-5af8-8184-c6ec481fe30d |  | note | Responsibility: Site Engineer
date | 796400ab-0400-5f8c-9b11-f14894fbf647 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Backfilling
label | cebde716-1232-5d79-ba1d-6548375e5569 |  | note | Frequency: Each Lot
label | b9878b8c-3fff-59d7-a4b8-a03ddf8a36c8 |  | note | Acceptance Criteria: Contractor is reasonable to ensure the site is made safe and clean, this includes All cement droppings, slurry, etc. and surplus materials to be removed from site, cleaning of surrounding strcutres from conrere splats.
label | fdd2b651-98bc-5d0c-8190-faddbc8c9f26 |  | note | All formwork, pegs, stakes, etc. shall be removed after the curing of the path has been completed.
label | 9b693dc5-68d4-564d-8f31-f04409fd6ffc |  | note | Reference Documents: C.11.8
label | ac9e8543-5fa1-542e-9a8e-ccb2f1c7c99f |  | note | Inspection / Test Method: Verify
label | 5375f0b1-addb-5bd6-be49-2d0fbcc6e05a |  | note | Record of conformity: This ITP Signed
label | ab5e83b9-eed2-5927-9e28-f47e0cf6a5cb |  | note | IP
label | 5f4cdb24-33e7-562a-ab87-4e13974700b8 |  | note | Responsibility: Site Foreman
date | 0fa59125-dcf9-5713-9a78-1204b3100c44 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - As-constructed survey and conformance documentation
label | 8706a8f4-8585-5496-8513-e7a0af7e3747 |  | note | Frequency: Each Lot (1 per day)
label | a4a614e9-c267-5545-ad4f-0f93307e2aa7 |  | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
label | 7cafc3ce-554f-5bf7-afc1-8de6d70841fc |  | note | Reference Documents: Work Procedure
label | 2ac564aa-abd5-59ff-b89e-dd312d7304e6 |  | note | Inspection / Test Method: Verify
label | 852e0a4b-7539-5837-992e-3bb645cbe769 |  | note | Record of conformity: Visual match existing / This ITP signed off
label | 6752a650-068c-5516-bdcf-41bd86a8f42d |  | note | SCP
label | e0dbc542-c697-57b6-80d1-dfb2f4446ed5 |  | note | Responsibility: FH Engineer/ Surveyor
date | 37299b6c-c0e0-5513-a0c7-59a862cb0cdf |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 6073026a-d034-59f7-ba00-0b4340908cab |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | c8d40cce-4c4f-5f63-b2de-17869b0790b2 |  | textbox | Print Name:
text | a6bb869c-29ab-5f30-a0f0-7d869cf03550 |  | textbox | Position:
date | 11d737bc-3af2-5a81-aa0f-11bb64ce8005 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | GT4-ITP-014 - Electrical Works | itp |  |  |  | Yes | GT4-ITP-014 - Electrical Works | cca7e9be-f7b7-4ee3-8d09-046b4de3e61e
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Define physical bounds of a lot
label | 2013e2f3-bbef-50f2-be67-92f6d2567401 |  | note | Frequency: Prior to Commencing Work
label | 748d43b6-5e44-500f-a42a-45cf942c27d4 |  | note | Acceptance Criteria: Maximum lot size = Single run to the location of field equipoment. Multiple cables can be included in the lot
label | a0e85c32-8b8c-5011-aa9a-405d043fdbb2 |  | note | Reference Documents: Lot Map
label | 724fe329-fd7e-5c45-ba01-379a6d9333b5 |  | note | Record of conformity: Lot map
label | cec3ddc2-ff59-5266-a14a-b7a44023b5f5 |  | note | HP*
label | d5b2ea8c-0023-5826-8b14-408741c623a1 |  | note | Responsibility: Site Engineer
date | c9476cf8-2ada-5911-8107-927d2262a786 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Site Access available
label | 7efb809b-d0d0-5064-b301-9a762847ebca |  | note | Frequency: Prior to Commencing Work
label | 96b9e722-32af-56df-9e5c-39adc33c2772 |  | note | Acceptance Criteria: Confirm Site access to area with Supervisors. Confirm all safety procedures including car and pedestrian barriers are in place - as required.
label | 9d396dc8-3fa2-5ff5-a532-a7886719b86f |  | note | Reference Documents: Current safety requirements of the site
label | 2a7f83fb-1046-557d-96c3-2e5c0f982822 |  | note | Inspection / Test Method: Site inspection
label | 036bc5f7-7ada-5d10-a329-b07f729f9b82 |  | note | Record of conformity: Photos
label | 65cbc08d-5e26-5710-938a-802bd00e223a |  | note | HP*
label | 4d41ac6f-81a4-5146-9085-b41654aaed83 |  | note | Responsibility: Site Engineer
date | 8b7ff225-4ff6-5b25-aa15-8b5cd790bdfc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Underlying lot(s) conform
label | d784f2ef-34c8-5ee3-8091-155f8e374d5b |  | note | Frequency: Prior to Commencing Work
label | d1eab0ea-c582-5e8a-959a-ed920e618ad4 |  | note | Acceptance Criteria: Contractor to verify all underlying lots are closed, or lots open but acceptable to proceed with work. Confirm "Service Trenching & Install CTN-ITP-003" has been completed and signed off.
label | 50f4621d-ac83-5dd4-b7d9-a579fce709d6 |  | note | Reference Documents: "Service Trenching & Install CTN-ITP-003"
label | cfecc6b9-f13e-51b6-83be-61d0746210b0 |  | note | Inspection / Test Method: Site inspection
label | 7bf61edb-ec88-5506-b348-0790383f0e73 |  | note | Record of conformity: Previous related ITP completed and signed off
label | b96a172b-de70-5e59-91ea-da99120e0a41 |  | note | HP*
label | 2506b68f-d3c1-5f3d-be8e-2acee88fb7d3 |  | note | Responsibility: Site Engineer
date | dad6c3c9-feba-5e6e-820c-d17301551867 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.4 - Ensure current Termination drawing revisions and cable schedules are available
label | d6c648f4-cf1f-5226-9c71-458dccab805b |  | note | Frequency: Prior to Commencing Work
label | 961b9140-25eb-5aff-b10a-162074ebf5ce |  | note | Acceptance Criteria: Identify and use latest drawing revisions.
label | 8d71e1ee-13d4-51f2-8979-1eae12c47e67 |  | note | Reference Documents: latest relevent drawings
label | 299b8542-ba69-5337-a4d0-eff74573a17a |  | note | Inspection / Test Method: Document review & Site inspection
label | 7669a0d9-1087-500a-8172-22297ca08686 |  | note | Record of conformity: List drawings and version
label | 21ccce91-5541-5d76-ace3-01e2ad36f549 |  | note | HP*
label | c14f3774-f4f4-5179-90f5-75d1fbf11d2b |  | note | Responsibility: Site Engineer
date | 5e80bed5-2911-5a6d-a0c1-2ef4e4765238 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Subcontractor ITP
checkpoint-status |  |  | checkpoint | 2.1 - Receive completed FLE ITP SS107 - Fence and gate installation
label | 3edbf162-f9ab-5926-99bb-dbcca59d2dfe |  | note | Frequency: Per ITP
label | 39f8ab71-0c16-5676-9aee-74b626c3c00b |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 665ec274-54c1-51e8-8ac1-b249d182d7e8 |  | note | Reference Documents: Signed and completed ITP
label | 3d8df007-81da-52b9-98da-11119fd6e773 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 735a7ab7-f19b-5c30-8751-cd8868416afe |  | note | Record of conformity: Signed ITP
label | 2030c765-6366-503f-9abb-371f345ed1c5 |  | note | HP*
label | b2a46b22-f6a0-5e9e-b720-b87924bd5dde |  | note | Responsibility: Site Engineer
date | 52340157-9941-5dac-8309-fd6c03007acf |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Receive completed FLE ITP SS108 - Internal road
label | 393b8d37-2cc9-537f-bbf4-46bcd16bee07 |  | note | Frequency: Per ITP
label | 6967a878-fd24-5713-be3d-0ab8118ed0f1 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | a215ae1c-03c6-5faa-959f-59dce8f1c2b5 |  | note | Reference Documents: Signed and completed ITP
label | 68230d56-e1ac-5e78-93d1-0e526eac523a |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 3c85acf4-fcf4-54d0-9fc2-c5b987d6678b |  | note | Record of conformity: Signed ITP
label | ce117278-458b-57cf-a68c-44a3437c55cb |  | note | HP*
label | 94ac1357-8bbf-59cf-bf0d-e14bbe05d8f9 |  | note | Responsibility: Site Engineer
date | f184202b-602f-5ebf-9a27-880aecf9ccdd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Receive completed FLE ITP SS109 - Switchyard Surfacing
label | c53c41df-3363-58c3-b301-b0855ec9a97a |  | note | Frequency: Per ITP
label | d00121a5-54e8-55fb-925b-9274450a6fa3 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 9d1646ee-1741-5a29-8517-01eaacf29c2b |  | note | Reference Documents: Signed and completed ITP
label | 52f09c96-f4bb-5e39-85e1-0d0a4e2245b2 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | cb79c5fa-e087-5de2-a965-2444de374fdf |  | note | Record of conformity: Signed ITP
label | 1de0d2ac-da55-51bd-9abb-03a3e6b9dd27 |  | note | HP*
label | 3b4aabbb-765d-5d97-8515-1850653bcf2b |  | note | Responsibility: Site Engineer
date | 1b3e998b-7862-531d-82d6-ad6075178eba |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Receive completed FLE ITP SS110 - Stormwater Pipe Installation
label | b190e8af-088a-55df-ac95-ee677d1b8c99 |  | note | Frequency: Per ITP
label | 7bd7724f-b0f5-5def-96d8-394363f4c0aa |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | b069abf9-4b16-566a-a421-62907ff87e66 |  | note | Reference Documents: Signed and completed ITP
label | 78ba56f6-127d-563b-9c50-29d11b6657f6 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 2346005f-21a4-50ea-8235-a4e1345a0fc4 |  | note | Record of conformity: Signed ITP
label | a152ed43-ffa3-5742-929b-8582d76634bc |  | note | HP*
label | 7f5ff26a-0d04-5246-b261-544241e28b98 |  | note | Responsibility: Site Engineer
date | 094c2a3c-81b4-52a3-a5c2-da6bc22caa79 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Receive completed FLE ITP SS200 - Structural Steel Installation
label | 86c3db10-e271-567f-9375-92f2755f01c8 |  | note | Frequency: Per ITP
label | 5e89c2b4-9ec5-5a49-b7bd-2fc56e4c66cd |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | cb6ed715-bbe6-51aa-96e9-4bc1f221bcd1 |  | note | Reference Documents: Signed and completed ITP
label | f724d845-90f0-5350-a574-cc0faebef848 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 3e6bb671-afd4-5171-bb41-5b2c4d899d9c |  | note | Record of conformity: Signed ITP
label | 54bde4fd-4db5-5af9-8096-7a5c108b2bcc |  | note | HP*
label | 5b3263a3-4365-59da-bed3-7435cd59d04b |  | note | Responsibility: Site Engineer
date | edd9d119-8992-549f-ada5-a437539924f9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Receive completed FLE ITP SS301- Substation Earth Grid Inspection Checklist
label | 6ab9cd62-c13d-528c-a432-67ce5542245f |  | note | Frequency: Per ITP
label | 44c64ae0-4dc8-5a12-9cdf-515eab325928 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 05646d8e-2a19-5782-8e23-3c832f513358 |  | note | Reference Documents: Signed and completed ITP
label | a41b1dcc-fbf9-5c84-bfca-fda7622a1440 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 10c9c098-e537-5631-8ca4-4eaae21217ba |  | note | Record of conformity: Signed ITP
label | 27c99dae-e31d-5c38-87e8-30bb2351a3ca |  | note | HP*
label | 5c47bbea-ef0c-5e68-ac7a-305659901382 |  | note | Responsibility: Site Engineer
date | d1855bcb-de94-5bdb-bbb6-7d7df17bb02b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Receive completed FLE ITP SS302 - Current and Voltage Transformer Installation Checklist
label | f31c36b0-67e4-5bc3-adc2-da34d05a0fee |  | note | Frequency: Per ITP
label | 6d201c41-96de-5148-9466-2eadd990a45b |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 4dde1f37-0584-59fc-9ba3-afc182c64379 |  | note | Reference Documents: Signed and completed ITP
label | 7688600e-71f6-5df6-aa06-3af05e5c8160 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 2ecc9617-888a-573e-81a2-ff844634acaa |  | note | Record of conformity: Signed ITP
label | 2a67f1b7-dcfa-5148-8d76-0a38ddc70697 |  | note | HP*
label | 1beb2030-970e-5989-8ff7-15cd856446aa |  | note | Responsibility: Site Engineer
date | 91c217f3-bf2b-5b82-bf8c-7ceabdb90413 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Receive completed FLE ITP SS303 - Isolator and Earth Switch Installation Checklist
label | 4328a9e8-9843-5484-b262-3068aafa30df |  | note | Frequency: Per ITP
label | b943c5c7-1338-567a-bdbe-3e7d8e8fda2f |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | dea7810f-b6bd-5ea8-9878-e305f9f83833 |  | note | Reference Documents: Signed and completed ITP
label | c06cab17-75de-5199-9360-9c837b964564 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 71c2a502-1d93-5659-9d89-a4211ccae918 |  | note | Record of conformity: Signed ITP
label | da9d64e1-8a47-5e67-8c58-ffa6f3c62a2e |  | note | HP*
label | 902b46ef-a017-5105-ab3e-4aab69abe5a7 |  | note | Responsibility: Site Engineer
date | 1b227f69-f2e1-57a9-935b-0cc2f4aea9fd |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.9 - Receive completed FLE ITP SS304 - Circuit Breaker Installation Checklist
label | e4382413-78b6-5051-8ffd-6df6344ebfe7 |  | note | Frequency: Per ITP
label | ff25a0d0-2d28-5874-8413-fa3b93a85c74 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | f554dc23-bf63-5c4a-a278-bd164f6dd47e |  | note | Reference Documents: Signed and completed ITP
label | ec6bb70c-57f5-59ce-8660-2d41b6d27e41 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | f388f587-e88f-511e-ae10-5f5d3832cbec |  | note | Record of conformity: Signed ITP
label | dec847f1-9925-5158-b00c-bf2a18938147 |  | note | HP*
label | 44b04694-8072-5d6a-beab-62c54367069b |  | note | Responsibility: Site Engineer
date | d1101fac-d9bb-52d7-b280-f5983b7dece0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.10 - Receive completed FLE ITP SS305 - Post Insulator Checklist
label | e5dd62a0-ef3b-514f-b24e-f8f7bf18fbc4 |  | note | Frequency: Per ITP
label | d3122ff2-af1b-5cd8-8544-8bda731fa6d0 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 526632b2-0bb1-5535-a54c-e1c845fb430d |  | note | Reference Documents: Signed and completed ITP
label | 01d05049-8ee4-5252-a11d-91f3bd26ba76 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 19c2808d-f9da-5b1a-b5b3-bb1c288c1819 |  | note | Record of conformity: Signed ITP
label | a73d2557-b7e5-525e-aa30-68d1b4d2938a |  | note | HP*
label | 2c734f20-5ffb-5aba-acdf-9530ffb89f6e |  | note | Responsibility: Site Engineer
date | ffe47701-2e1f-5815-b75a-57d0879ae472 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.11 - Receive completed FLE ITP SS306 - Bus Bar and Clamps Installation Checklist
label | 4f7c4a8e-23ca-5193-963f-a55ec72860b9 |  | note | Frequency: Per ITP
label | 509db4fc-314b-59f6-8b56-3b7b87d7eb4e |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 77ddc562-7716-5250-9726-a36214c961ed |  | note | Reference Documents: Signed and completed ITP
label | 5747d405-83aa-5536-b2ae-7218b47b4a45 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | aa91afbf-78f2-5009-9f51-f713de9e0c4c |  | note | Record of conformity: Signed ITP
label | fa47f8b2-8b8a-5c74-8d63-6157e0eff216 |  | note | HP*
label | fa3069fb-4a06-54fa-b7f4-f8bc36e96053 |  | note | Responsibility: Site Engineer
date | 275a3bde-1296-5ed9-a9d0-b356b145bc68 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.12 - Receive completed FLE ITP SS307 - Control Panel Installation Checklist
label | 12e06f97-1982-544e-a79d-e2986a5d7d66 |  | note | Frequency: Per ITP
label | f410e722-2a4f-5c64-aaf3-30f29c0ef1a8 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | faa16c15-e881-532f-984d-1a7d7e4ec2bf |  | note | Reference Documents: Signed and completed ITP
label | 15aadd74-deb9-5021-9399-343d48bbc063 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | d2df3914-3248-5a16-b509-942b76ce7982 |  | note | Record of conformity: Signed ITP
label | b61348a8-dac2-55c5-abf2-6b4f5e1593f4 |  | note | HP*
label | faa2f9bb-e87f-5ea2-8fbf-74a64165fff6 |  | note | Responsibility: Site Engineer
date | 53c937cc-c61e-5393-a1dc-bea1ab3328fc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.13 - Receive completed FLE ITP SS308 - Lighting Mast Installation Checklist
label | 4fc3386d-ac7e-540b-b676-dcafec03f519 |  | note | Frequency: Per ITP
label | 7949a3e0-bc43-5bea-b13d-4d2193d15788 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 80da7b19-9061-55cc-a850-c21bda9da95e |  | note | Reference Documents: Signed and completed ITP
label | 220bf728-3eee-5ed0-ac7d-8a1052e6fcf0 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 57fd093f-c09e-5901-a526-336b3f88f54f |  | note | Record of conformity: Signed ITP
label | af27e2f2-50e1-5c83-b24b-249d8ed3fabf |  | note | HP*
label | fa83c492-0fd2-53a2-a050-a055c71ab848 |  | note | Responsibility: Site Engineer
date | 137717a2-911b-5fd3-872d-2b7c61897c26 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.14 - Receive completed FLE ITP SS309 - Low Voltage Cable Termination Checklist
label | 34ff7a40-afff-5a59-bfba-9989ead2c3f0 |  | note | Frequency: Per ITP
label | e01b78ef-3414-5010-bfab-6d64bc66ca99 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 2ead78e1-4688-5c15-a0d0-bd86c8ba6448 |  | note | Reference Documents: Signed and completed ITP
label | 23b81137-69b8-53c5-9e7f-21eafd7018e1 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | b4193d9a-296d-536c-bd76-87d4cffbdf36 |  | note | Record of conformity: Signed ITP
label | 7c912d8e-7b2d-5ea2-ae94-9cce2e251b07 |  | note | HP*
label | 41f4dbf0-9b21-59c0-a562-a12c50a3630e |  | note | Responsibility: Site Engineer
date | 67b03e41-861c-5c45-b429-9e432ef77289 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.15 - Receive completed FLE ITP SS310 - Ductor Test Results (Insulation resistance DLA/DDF)
label | e914c482-305b-575e-b891-ac9c6cb58f21 |  | note | Frequency: Per ITP
label | 81305a37-26e4-586a-988a-9cea02cf6465 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 6bfeb68f-709a-58d2-91c5-1bf5b2483016 |  | note | Reference Documents: Signed and completed ITP
label | 3a850046-094f-52e2-8e92-0003c4b7c5af |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | ad7af829-8bad-5ba1-b2ef-1e51681461fb |  | note | Record of conformity: Signed ITP
label | 51dafac2-ef29-512e-ab22-706843ba6c89 |  | note | HP*
label | 4cad94c0-aac6-5bb7-8451-55f6b0126399 |  | note | Responsibility: Site Engineer
date | 3b9701af-8fae-5392-a42f-c9b197248b22 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.16 - Receive completed FLE ITP SS311 - Marshalling Box Installation Checklist
label | 54457018-03d3-569f-aefe-45c0c6c56209 |  | note | Frequency: Per ITP
label | 17094e0f-f9f2-5123-b923-09a5e394f723 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | fa04ef50-532a-53f9-906c-63a5acde5ba4 |  | note | Reference Documents: Signed and completed ITP
label | 7df36cd2-64c8-5e99-bf5d-fce6c9b09035 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 204c31be-eaee-5b29-9a02-77dcb7e3fe56 |  | note | Record of conformity: Signed ITP
label | eaa816af-c9cf-531e-b991-61f6bc4f9490 |  | note | HP*
label | a4eb368f-8f70-50a3-aa4d-4a7147261d33 |  | note | Responsibility: Site Engineer
date | eee55797-822f-507a-a0fd-0aed3e9344ee |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.17 - Receive completed FLE ITP SS312 - HV Cable termination
label | e9c1b1b0-ca22-573a-865c-ef82b7ef1591 |  | note | Frequency: Per ITP
label | f2cb88aa-44ce-56a9-acc2-e51e8a8f3bc4 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | d30c7852-99d0-5967-a331-6471ae3e9f4e |  | note | Reference Documents: Signed and completed ITP
label | 1314cd95-e43b-5452-8f20-301c79cab5a4 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 6a37c35d-ff80-5627-8c89-328645657a18 |  | note | Record of conformity: Signed ITP
label | 190c46b5-031f-5435-b4b9-5956c6e3105e |  | note | HP*
label | 0a5ef813-4297-57ba-820e-2538ec8a8fc9 |  | note | Responsibility: Site Engineer
date | 92178d88-77ad-5a8f-943e-caf305d1df88 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.18 - Receive completed FLE ITP SS313 - Light and Power in Substation Building
label | f5b93aba-9d25-539a-91d8-1d58f08bdd5f |  | note | Frequency: Per ITP
label | a26e0431-7e47-5c42-94fa-5e819ea37e27 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 3380a5b3-99f8-5779-b464-65cd87f5ae63 |  | note | Reference Documents: Signed and completed ITP
label | f6d0be86-6293-5be0-b747-725ebdad0c48 |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 839a762f-bc35-53fa-8475-24992e8f008f |  | note | Record of conformity: Signed ITP
label | 1048d948-83e6-5694-a303-1e80223b0788 |  | note | HP*
label | 7323686b-da43-5b37-8e98-548814905aaa |  | note | Responsibility: Site Engineer
date | 6d53d406-12f8-591d-b366-7ef5c97b7ab7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.19 - Receive completed FLE ITP SS314 - Field Cable Installation
label | 21881c0d-bf93-575d-bb26-1599816b58f9 |  | note | Frequency: Per ITP
label | 4dae6fcf-9c94-506a-99fe-00467a062b18 |  | note | Acceptance Criteria: ITP per lot package satisfactorily completed
label | 44df8283-fb87-5059-89ce-fd91b0359761 |  | note | Reference Documents: Signed and completed ITP
label | 080e9573-be59-5092-a1fa-1e60ea14312f |  | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
label | 09351a5d-1073-5835-acbd-16fe74fd1f15 |  | note | Record of conformity: Signed ITP
label | 47d000ea-bbe5-51d1-84aa-ab9be92b9a45 |  | note | HP*
label | cbd2164e-981d-5316-8188-2d441803703c |  | note | Responsibility: Site Engineer
date | b48c413a-3ca1-5c1f-be0a-d8548af34cd1 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Final Inspection
checkpoint-status |  |  | checkpoint | Final Inspection
label | 95942443-6527-56a2-b5ea-a4842155354c |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | e429ccfd-dac4-56fe-98e5-c732c36bfacf |  | textbox | Print Name:
text | 34591ab1-ca50-5d59-bbbf-8840503e32e9 |  | textbox | Position:
date | ff7e91c2-5747-5459-8d8c-d06032683757 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-006 - Concrete - Kerbs | itp |  |  |  | Yes | CTN-ITP-006 - Concrete - Kerbs | e85f2eeb-47f5-48bc-a8dd-42bbe1c81c83
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 6bc2627d-b68a-51e5-9331-09568c1fcee1 |  | note | Frequency: Prior to commencing any activity
label | e68e70fd-c9f9-5f97-965e-b5c7f7d43539 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | 592d64f8-da8a-56cf-93a9-29d276d11722 |  | note | – using the correct and complete set of drawings
label | fe1c427f-d980-5cc9-8a9a-3674a36ddcdc |  | note | – all drawings are the latest revision
label | dbe797c4-c4a9-5123-b62b-b23b3646ea80 |  | note | Reference Documents: Drawings and drawing registers
label | 276c8c6e-56b5-5182-8762-705fad5b6df4 |  | note | Inspection / Test Method: Visual inspection
label | 4cd24f43-70f0-587b-ba43-3afdb6a0515f |  | note | Record of conformity: ITP Signed
label | ce1a1e5d-f5d7-5c0d-bf01-0da4a2871b6c |  | note | HP*
label | 7576be38-e928-57ce-8fc2-94fa0f45c5fe |  | note | Responsibility: Site Engineer/ Site Foreman
date | 6b901fae-9703-5b92-83ff-b861bd15bbbe |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | f227fe21-cad2-5ea8-862d-3896e811f8a0 |  | note | Frequency: Prior to commencing any activity
label | 36bb38cc-a950-58a2-b4a9-06b5ebb2c053 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | 1d855601-1f3a-571f-95a8-502541529f29 |  | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
label | 22240516-5b91-5c33-998f-3c9d45ca3626 |  | note | Inspection / Test Method: Visual Inspection
label | 6f45956d-8c18-5d5f-ae99-2a3cf51ef81d |  | note | Record of conformity: ITP Signed
label | 91196b51-1d20-5cb0-9cdc-0459d77852dd |  | note | HP*
label | fcf145e8-faf3-576c-80e2-75374e776380 |  | note | Responsibility: Site Engineer/ Site Foreman
date | 5bae8926-4ff7-5ffe-b54b-cc20126b435f |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.3 - Submission & Approval of Concrete Mix Design
label | 8048a345-828f-5c3b-b2e2-cf8e8746992c |  | note | Frequency: Prior to first concrete pour
label | 9f14af47-f1e7-5fde-ab1a-e5d327cfe82b |  | note | Acceptance Criteria: Supplied concrete pre-mixture for kerbs, needs to be in accordance with the supplied Early Works Civil Drawings.
label | dff6203a-ed6c-5f2e-9b79-37759e7b5e5f |  | note | • Unless specified, then concrete used in this construction shall conform to AS 3600 and be provided by an approved pre-mixed concrete supplier, conforming with AS 1379.
label | 1316f3dd-d3a1-539a-82c8-d87cc71f6da2 |  | note | Reference Documents: Work Procedure
label | b1a174c9-e3eb-59b5-ae85-a10d9909e87d |  | note | Inspection / Test Method: Verify
label | 86e5a73e-990d-5788-a769-6745c3d55ba2 |  | note | Record of conformity: ITP Signed, Mix design approval
label | 7072a401-80e2-5edd-8011-ff68bc644edf |  | note | HP*
label | f78745ef-6ff9-544e-ab72-1d9b0e7a705a |  | note | Responsibility: Site Engineer
date | ee7c135c-4f37-5a43-aff5-e72183342674 |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Construction Works
checkpoint-status |  |  | checkpoint | 2.1 - Setting Out
label | 54b8b1ea-b316-5b54-970e-f61c904d86ef |  | note | Frequency: Prior to start
label | 478072df-c6e4-5cf1-abe9-1186e7de3fc9 |  | note | Acceptance Criteria: Set out work in accordance with drawings. The Engineer and Supervisor will review and confirm set out with surveyor.
label | 1ed4587b-7f34-54e2-9720-d7d64b56eb95 |  | note | • No survey/level pegs to be removed by any persons until completion of works.
label | 562de5d2-361d-536f-b1ba-8beb4f7b82c4 |  | note | Reference Documents: Work Procedure
label | 7af114df-cd16-5dfc-8b3c-80b9fd7abb62 |  | note | Inspection / Test Method: Verify
label | d246376e-deba-5a99-a0ba-ecd797fbc190 |  | note | Record of conformity: This ITP Signed
label | a63b9227-b5db-528e-b51d-b772d98f6ea9 |  | note | HP*
label | 72625d76-2192-54ff-9b66-27bd6f0ca9f4 |  | note | Responsibility: Site Engineer
date | 0052341f-22c0-550a-b80c-925c46387563 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Excavation Permit
label | d1d25bd6-19d7-54a6-8f50-b8ce637bbaab |  | note | Frequency: Each lot
label | fcd2257b-1600-5727-9cd1-d840bd1c9389 |  | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
label | 0e01218f-4aba-5f5e-b8a0-9b361a202c5b |  | note | • Plant and equipment shall be appropriate for the task.
label | 69731834-fe31-5c4b-a306-73d1589b779a |  | note | • Excavation operations shall not disturb areas outside the limit of excavation
label | 4d4bed5f-953a-526e-b80c-05de6848f366 |  | note | Reference Documents: Excavation permit
label | 6c8ef806-b49e-527d-baf4-69567d6ba908 |  | note | Inspection / Test Method: Verify
label | 96b129c0-1e40-5167-8d99-bd5be858980d |  | note | Record of conformity: ITP Signed
label | 2f5c1060-10f7-5093-b413-4720650bbe69 |  | note | HP*
label | 81eab740-5fab-5cf3-8b96-8a803df50fdf |  | note | Responsibility: Site Engineer
date | 1b2a0207-1b40-5871-88ad-c80fb59b37c7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Excavation
label | d069f4cd-9c3d-561e-93cc-a09c934d8a61 |  | note | Frequency: Each Lot
label | c48ca525-9511-5765-82d5-172ab018d139 |  | note | Acceptance Criteria: Excavation completed to required depth to allow placement of the bedding layer
label | 8b403a4a-d38c-523b-a424-ba76f6bb58d6 |  | note | Reference Documents: Work Procedure
label | 02c4ebbe-baca-5a49-881a-b2f9c4193732 |  | note | Inspection / Test Method: Verify
label | ad263e66-5dfd-51e8-9dff-27805dd08da2 |  | note | Record of conformity: ITP Signed
label | 041da8b2-ffde-5dfe-bd49-3c1f26924130 |  | note | IP
label | 02772cd6-474b-5f17-88e3-ecb6b2d9c9f3 |  | note | Responsibility: Site Engineer
date | 04d503b3-c9f8-5d37-925a-d9098819c4b0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Concrete Placement
label | c161e847-4e8e-5c5c-b7bc-72645c79a493 |  | note | Frequency: Each Lot
label | 2ec29804-1b35-5273-8b9f-428e788c5712 |  | note | Acceptance Criteria: All kerbing shall be constructed from 32 MPa 28 day cylinder test compressive strength concrete manufactured in accordance with AS 3600 for 10mm aggregate. Slump tolernaces to be in accordance with a 50mm slump.
label | c9696e45-eef9-5b22-bc6e-7eb602a72801 |  | note | • Kerbs to roads shall be constructed of extruded concrete kerbing. Kerbing to smaller radii than can be placed with the extrusion machine used shall be cast insitu to the same cross section as that of the extruded kerbing, except that the cast insitu kerb shall be 100mm deeper than the extruded kerbing and shall be embedded firmly in the road surface to the extra depth. The outward appearance of the extruded and cast insitu kerbing shall be identical.
label | 20debf66-34f7-575f-9d88-fa65de172f33 |  | note | • Where required match all new kerbs to existing level neatly, ensuring minimum 1 in 250 grade, saw cutting and reinstating pavement in front of kerb to fall to new kerb level.
label | 9515d6a4-a67a-5aa3-a6c6-a234db0cba52 |  | note | Reference Documents: DWG EW-CE-DRW-406-001 C.10.15 C.10.16
label | adc7eed9-9dec-5052-a6d6-a0096ad281e1 |  | note | Inspection / Test Method: Visual Inspection
label | 64643445-c15c-5081-b76d-c8db93a65688 |  | note | Record of conformity: ITP Signed
label | f522e62f-9063-569b-a249-9206fa3ff3e5 |  | note | IP
label | acfc8aa2-1242-5534-bdab-fed18dfec392 |  | note | Responsibility: Site Engineer/ Site Foreman
date | 43b6c8a4-7eaf-5f50-af9a-d1eba100bdcc |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.5 - Pram Crossings
label | 6d788f4b-983c-5acd-b011-0188b063ed6d |  | note | Frequency: Each Lot
label | d2223f8a-c9b4-5d52-bd57-b05f479f1e3e |  | note | Acceptance Criteria: Ensure that pram crossings are constructed in accordance with requirements for access and mobility and with dimansions as specified on DWG-416-001.
label | 22fec6a5-031a-5093-943e-21c0d36114c2 |  | note | • For pram crossings within concrete kerb refer to Figure 24A of AS 1428.1
label | 0b579ea3-90fc-5d98-9f03-3022f8741565 |  | note | • Kerb ramp allignment in accordance with Clause 7.7.1 of AS1428.1
label | b0ccec83-ab12-5662-9101-b01e2550a757 |  | note | Reference Documents: Figure 24A AS1428.1 DWG-416-001 Clause 7.7.1 of AS1428.1
label | 707db4a4-504e-5653-8fb8-e99e99f4c48e |  | note | Inspection / Test Method: Verify
label | ad5bc0b6-23d0-5c77-99f2-c850cbd57974 |  | note | Record of conformity: This ITP Signed
label | 2eb700f6-ec50-561e-9535-9ee7caee6c82 |  | note | IP
label | fee18d8e-8c0f-5d37-a2aa-aecf55b45ae9 |  | note | Responsibility: Site Engineer/ Site Foreman
date | b35628aa-41e6-5eec-8f50-9758bc4ba9f9 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.6 - Joints
label | 1216963f-f896-5d2b-8a27-40d003f5d067 |  | note | Frequency: Each Joint
label | aed659aa-5e84-50a2-befc-3389bd70e48e |  | note | Acceptance Criteria: Contraction joints shall be constructed at 2.0m intervals, at sides of entry pits and at tangent point of sweeps by complete separation of adjoining sections of the kerb immediately after extrusion.
label | d8740c1a-6c93-5591-af53-6627a5dac51d |  | note | • Joints shall be 3mm wide, clean cut and made vertically through the concrete at right-angles to the direction of the work.
label | f9a01c19-c8b6-5b57-a1de-084372f9dac2 |  | note | • Where kerbing is laid by machine, joints shall be formed in a manner which doe s not cause damage to the adjoining concrete during cutting and to a depth which will prevent cracking elsewhere. In general it can be expected that the cut should extend to at least one-quarter of the depth of the section.
label | 92c67de2-a9c4-55ce-9b0f-812c25d2e18a |  | note | • Where kerbing is cast against fixed forms, contraction joints shall be formed by means of a 3mm thick steel plate cut to profile which shall be withdrawn before final finishing.
label | 54178e08-f2ac-5ace-a5f0-0ea0a8b84fb1 |  | note | • Expansion Joints shall be constructed at every third contraction joint not less than 24 hours after placing. The expansion joints shall be formed by the sawing of a 10mm gap that completely severs the adjoining sections of the kerb. The gap shall be filled with approved joint filler after the Superintendant and the Local Authority have inspected and approved the cut joints.
label | 960b2ced-4137-5c6b-9f58-ccc87622205b |  | note | • All existing pavement adjacent to proposed kerb or proposed joints shall be saw cut in a neat line to the satisfaction of the supervising engineer, and to have 300mm overlap.
label | c6e5f499-8174-55e3-ad20-c5b513d1cc45 |  | note | Reference Documents: EW-CE-DRW-007-001 C.10.17 C.10.18, EW-CE-DRW-406-001
label | 1723d25e-ae08-5202-93e3-c7550f58d6fd |  | note | Inspection / Test Method: Visual Inspection
label | d4268ad1-7913-50dd-ac91-3af33952246e |  | note | Record of conformity: This ITP Signed
label | 361ed21d-8842-5dbe-ac03-185e08ffd6e1 |  | note | IP
label | 38e2594f-c555-59c9-a174-bd674186d3d6 |  | note | Responsibility: Site Engineer/ Site Foreman/Superintendant
date | 57be2c84-46b6-5cb0-a069-3edd7300a89c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.7 - Protection of concrete
label | f5e0cae5-404b-5dcf-8587-7d9ffcdf1983 |  | note | Frequency: Each Lot
label | 74846088-a6e6-53ad-b5ec-050aac32be9a |  | note | Acceptance Criteria: Kerbs shall be always protected from bitumen overspray by adequately covering the kerbs with polythene sheeting or similar approved material
label | 762b2047-2082-5de4-8c5f-e9496a1a96ee |  | note | Reference Documents: C.10.20
label | 8008ee3e-5f3c-569c-bcc3-f295ab765ffd |  | note | Inspection / Test Method: Verify
label | 3600a1a9-b118-5ea0-877e-c0f8e6501fa3 |  | note | Record of conformity: This ITP Signed
label | 6e31b5c7-ed5a-5f28-b16a-925633adb330 |  | note | IP
label | 96dcff23-9b1b-5bcc-8510-7c3c8d8f5fdc |  | note | Responsibility: Site Foreman
date | 6d4048b4-b789-515f-a146-59cdccd2149c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.8 - Curing - Kerb
label | 781a0d91-6f89-5db4-9d1f-783ddba080c7 |  | note | Frequency: Each Lot
label | c7418c08-3d64-55e5-81e4-80501ae55dab |  | note | Acceptance Criteria: Within two hours of surface finishing, all exposed faces of the completed kerb shall be protected against loss of moisture for a period of not less than 96 hours after placing by shrouding with plastic sheeting or by spraying with a curing compound complying with AS 3799.
label | 6fe9bc8c-7ec3-59c8-9299-a2fc5ab144f4 |  | note | Reference Documents: C.10.19
label | 23afed14-a4eb-5426-9eaf-36e64b5e28dc |  | note | Inspection / Test Method: Verify
label | 5934998e-d492-5d73-93fd-7a4b1dd53927 |  | note | Record of conformity: This ITP Signed
label | ea512a6c-b76a-54ec-97a0-70402ec1fefb |  | note | HP
label | 1dbb753d-46eb-56a4-9b67-f9497620bac9 |  | note | Responsibility: Site Engineer/ Site Foreman
date | e943788e-142a-51d0-980a-5a1286dc7583 |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3 - Completion
checkpoint-status |  |  | checkpoint | 3.1 - Carry out sampling of concrete - strength and consistency
label | 89d55ccf-abb2-5040-8426-aff8c7f453bd |  | note | Frequency: Each 50m3
label | 07c2ccc8-fc89-5609-8e13-26d1556f74ee |  | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
label | a4650249-ec8e-5e37-8ff8-d04116608d15 |  | note | Reference Documents: Work Procedure
label | a4fb7309-7518-5c5e-a306-f58a9976da82 |  | note | Inspection / Test Method: Checklist
label | d044aac1-cd60-5f39-bfb5-b2136c00947d |  | note | Record of conformity: ITP Signed/Test Records
label | 52f89a72-15d7-5f5a-864b-e297c6eb1ed8 |  | note | TP
label | 89aca801-4b49-5ffa-90ee-efd67be0ea53 |  | note | Responsibility: Site Engineer
date | 1726d9e8-991c-5a12-824f-8ee25e370b35 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Tolerances
label | 4d15bbb3-0892-5b71-8fef-24045c2dfb8e |  | note | Frequency: Each Lot
label | 469d35bd-0af8-529f-b304-7f3ecbe742f1 |  | note | Acceptance Criteria: Tolerances
label | 7fe01eb8-b8bf-5870-bea1-199d620d4794 |  | note | • Surface: + or - 5mm when tested with a 3m straight edge
label | 92ee1ac6-1ed0-50d7-b614-2ea02ede4b40 |  | note | • Level: + or - 5mm
label | e0167938-5614-524a-ab01-ed3fcfeee838 |  | note | • Line: + or - 10mm
label | e275fc16-cdb5-5721-9a63-339a5942a47a |  | note | Reference Documents: C.7.4 Table 6 (9.)
label | f9128b71-fe7f-590c-802b-db35eb74fd54 |  | note | Inspection / Test Method: Visual Inspection
label | 55d6eadb-12e7-5cfd-a323-8e72230e9322 |  | note | Record of conformity: This ITP Signed
label | 37ff4087-53a6-5f04-82a9-76cec7cc80fc |  | note | IP
label | 16d01c81-9890-5953-9b96-8516a1d6133b |  | note | Responsibility: Site Engineer/ Site Foreman
date | 84faaa19-d3c1-5b0b-a84a-540098335703 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Backfilling
label | a6d9ecdf-8e30-547b-9845-85940b5bdd0a |  | note | Frequency: Each Lot
label | 3e138461-7640-534a-bb54-70e8f45ea866 |  | note | Acceptance Criteria: The backfilling to kerbing shall be placed as shown on the drawings after the curing and acceptance of the kerbing. The backfill material to be a similar material to the locally occurring topsoil, free from debris and compacted adequately to accommodate the driving of rubber tyred domestic vehicles.
label | b008edc1-4db9-53b5-990e-2e0f912dec93 |  | note | • After curing, no earlier than 3 days, backfilling shall be completed as per the below:
label | e580f41a-953d-53e8-80e0-f80ebadf0fda |  | note | – Topsoil compacted in layers < 150mm
label | dfabbe1f-5acf-5c44-abf4-7393ef47b35a |  | note | – Width ≥ 300mm behind edging to top of edging
label | 2ae84d6a-e57e-54e9-83a6-a7b833f97b58 |  | note | Reference Documents: C.10.21 Work Procedure
label | a2755bf7-a454-5a83-bafb-41421537cc65 |  | note | Inspection / Test Method: Verify
label | c0df8566-a597-5804-9537-691580eaff53 |  | note | Record of conformity: This ITP Signed
label | ba55f374-1b41-55b6-af5c-5bdc5fe51214 |  | note | IP
label | 93b53a16-46a9-5205-a0d3-22a951471ed0 |  | note | Responsibility: Site Foreman
date | 8ca3a5ae-46a7-565c-b4fe-ed4bafc4daf0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - As-constructed survey and conformance documentation
label | f6c33b34-7b46-5986-9d21-ebc64597a63f |  | note | Frequency: Each Lot (1 per day)
label | 48eb2d8c-4a91-531f-9753-e240f5dc98a8 |  | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
label | 597efca3-8985-5951-ad5c-70f9518a198e |  | note | • Lot Maps shall include Width between kerb at 20m intervals, contraction joints, expansion joints and Curing Certification per lot
label | 19ccbdec-680b-5b59-bbcb-5aad5db26824 |  | note | Reference Documents: C.7.2 (7.)
label | 85d93da7-5a9c-5555-b80b-ad199ee5e33a |  | note | Inspection / Test Method: Verify
label | 4a920fbf-590e-50be-b359-e38ec9858886 |  | note | Record of conformity: Visual match existing / This ITP signed off
label | f17aad63-d817-54a4-b618-88c3a5ea2a35 |  | note | SCP
label | fba831f9-9187-5140-9f62-b006c5835a98 |  | note | Responsibility: FH Engineer/ Surveyor
date | 479b487a-9990-54d0-ad02-7f501a5179a8 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 85a997b9-9b77-5a36-9a94-2597a01ecbd5 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | b0997bee-2b1f-5af0-9585-c1f73f2f43e5 |  | textbox | Print Name:
text | 2e3d7c0a-9a95-5695-876e-6c85c74c3792 |  | textbox | Position:
date | a580c0b3-6171-565f-bfcd-ca590c23c585 |  | date | Date:
holdpoint |  |  | signoff | Sign ITP
checklist-sectioned |  |  | checklist | CTN-ITP-002 - Stormwater Drainage | itp |  |  |  | Yes | CTN-ITP-002 - Stormwater Drainage Rev2 | fac7423d-0df4-4bcd-857b-389bc7621734
checkpoint-group |  |  | section | 1 - Preliminary Works
checkpoint-status |  |  | checkpoint | 1.1 - Check for correct documentation
label | 6dab3b26-99db-572f-979d-63406946fd43 |  | note | Frequency: Prior to commencing any activity
label | 22fa997d-079d-5a5d-8fe3-33671d402341 |  | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | e7f67501-d056-5416-a39a-3b2500806bc9 |  | note | – using the correct and complete set of drawings
label | e79ee5db-69cd-5233-b254-e335db3bfc8b |  | note | – all drawings are the latest revision
label | 34952ec4-41eb-553f-ac16-843983d1ef89 |  | note | – Conflicting documents: The project specific drawings to superceed the specification
label | fcee553b-5215-57a9-8310-f8c7d9fb20cc |  | note | Reference Documents: Drawings and drawing registers
label | 6b3901dd-0f21-524e-875e-5d3502235b6c |  | note | Inspection / Test Method: Visual inspection
label | 21fed605-0bea-555e-adc0-09016919bf89 |  | note | Record of conformity: This ITP Signed
label | 7f5e0ffb-8aaa-5045-b085-8f164a26ad34 |  | note | HP*
label | 5cadc6d8-a615-5745-919b-3eb9208d84ea |  | note | Responsibility: Site Engineer
date | 8f5fbcae-037b-5fae-aef8-f1145ecea79b |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 1.2 - Implementation of all measures and controls
label | 2bd0cb53-3be3-54c2-b096-4c42a84d45f4 |  | note | Frequency: Prior to commencing any activity
label | 28b5f892-53af-5f90-a4cc-caa7bd4fa3f3 |  | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
label | 5242e189-f739-58d1-af5d-da3762e1e075 |  | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
label | f6005bc6-a342-52fd-ac29-edcd99d03c5f |  | note | Inspection / Test Method: Visual Inspection
label | 787d3172-a218-58ac-ac35-bfe896bce5e7 |  | note | Record of conformity: This ITP Signed
label | 2e44080d-9265-5bce-aa0c-c987c9596a49 |  | note | HP*
label | c29fc1aa-1c86-5b23-8310-8f3923b3d4bd |  | note | Responsibility: Site Engineer
date | d9997bae-e6f2-57d1-958a-eba1c754e90f |  | date | Date Completed:
checkpoint-group |  |  | section | 2 - Procurement of Materials
checkpoint-status |  |  | checkpoint | 2.1 - Precast Reinforced Concrete Pipe Supply
label | 45310c4b-cd1d-516b-bdcf-ed8f754cd19d |  | note | Frequency: Prior to works commencing, 1 per delivery
label | 3fc29c85-717f-558c-b2e8-27cb68f69307 |  | note | Acceptance Criteria: Pipe class and size and endwall type as per stormwater drainage details and pit schedule
label | 5f9306c5-428d-52ff-9408-461d27bc26d1 |  | note | • All concrete pipes shall conform to AS 4058 and subsequent amendments
label | 1f302658-835d-5614-a5f5-d3350b33d269 |  | note | • All concrete pipes shall be spigot and socket rubber ring joint type
label | 4848b494-3d47-5685-8a10-9cb35c708792 |  | note | Reference Documents: Drawings C.4.2
label | 526a384b-cf9c-5b53-9d81-dd1b86b80b69 |  | note | Inspection / Test Method: Verify
label | eb59256a-1274-5f18-94fa-f4586e9cd066 |  | note | Record of conformity: This ITP Signed, Order acceptance certificate
label | 36334f13-42eb-56ce-8c9e-26123d80be72 |  | note | HP*
label | ef3a3e28-d267-5cc5-a8ae-030fd7a117c8 |  | note | Responsibility: Site Engineer
date | d91310f9-5a6a-55bb-9ffd-6647c659cb2a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.2 - Precast Reinforced Concrete Inlet and Outlet Structures supply
label | 54eb03ed-ceca-5afb-85a8-540e0872a2e2 |  | note | Frequency: Prior to works commencing
label | 0b8ced43-f231-5395-9a4a-01fe9eded662 |  | note | Acceptance Criteria: The supply of precast inlet and outlet structures shall conform with stormwater drainage details and pit schedule
label | 329effb5-e8c4-5760-9813-c25f63165658 |  | note | • Concrete shall conform to AS 3600 and shall be supplied by a concrete supplier conforming with AS 1379.
label | 57148c15-f3be-53e3-a3d0-aca07d2aa229 |  | note | • Concrete shall have a characteristic strength of 32 MPa and maximum aggregate size of 20mm.
label | bc7b2f1f-321d-568b-b432-e37b8e8de95e |  | note | • Concrete strength shall be tested in accordance with Section 20.4 of AS 3600.
label | a83deab7-ceaf-5e84-84ee-51b6d30cd484 |  | note | • Steel reinforcing shall comply with AS4671:2001
label | 3fc918c9-9aa3-57f2-b482-81565d7390e6 |  | note | • Structural steel shall comply with the requirements of AS 4100.
label | 2450b7d3-9a83-56cc-8f00-76007c0ff4cd |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.4.6a C.4.6e
label | 043e1c90-6d7d-5fb2-b382-d29ffdd3c414 |  | note | Inspection / Test Method: Verify
label | 8b2f842d-7982-5532-9fb1-a758477f32f2 |  | note | Record of conformity: This ITP Signed, Recievable Inspection Checklist
label | 662b85b6-2035-5cd6-b5e1-09d4f74d5eaf |  | note | HP*
label | a911915e-e856-5934-b561-beed3bbdaebd |  | note | Responsibility: Site Engineer
date | 62b92bbf-eccd-5a02-8933-83ffaf749ca7 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.3 - Bedding and Backfill Material Specification
label | 16b03644-ebae-5063-98c0-faefed6ae3b1 |  | note | Frequency: 1 per drain line
label | c98b4ecd-de77-5751-915b-afb24c6f94e0 |  | note | Acceptance Criteria: Bedding and Backfilling of trench to be in accordance with drawing EW-CE-DRW-526-001
label | 620f8440-30e1-57ae-a3cb-c75e27a6d694 |  | note | • Bedding shall be 75mm Class 3 FCR compacted to refusal using hand held mechanical equipment.
label | c6dfcce5-42b9-5707-b800-ce9a04f07ee3 |  | note | • See section 4.3 for details
label | 6df43e6f-de22-505c-979a-707dd79a609e |  | note | Reference Documents: 'DWG EW-CE-DRW-526-001 C.5.4 C.5.20
label | 8c1881c3-0d14-504d-80e6-b172d70d2281 |  | note | Inspection / Test Method: Verify
label | 460143c2-02c2-5d9b-99fc-c88f141a0a27 |  | note | Record of conformity: This ITP Signed, Quarry test report
label | 96932845-8c6a-58dc-b7e1-a69c3d1ac530 |  | note | TP
label | 6b28fef1-55ee-560d-a7f9-f78600e63bad |  | note | Responsibility: Site Engineer
date | 3e2f910e-c1a7-52b3-b9d0-4e17d51e65e0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 2.4 - Setout of Works
label | a6a23b2f-9bfe-5b06-8a44-ec98125f1051 |  | note | Frequency: 1 per drain line
label | 2a0b9af4-de72-5c18-94af-83bbb93705ec |  | note | Acceptance Criteria: Position of culverts confirmed with the superintendent prior to commencement of excavation
label | 541f7c15-ab48-5af3-8d2b-3e685cb588b8 |  | note | • Minimum 3 profiles access and headwall/endwall
label | aee9c528-0b67-53cd-a942-cc406dd29e5f |  | note | Reference Documents: Drawings
label | b92c5c5f-ff1c-528d-af05-7c29a48f26ea |  | note | Inspection / Test Method: Visual inspection
label | 494eded2-c9f6-5050-9736-2f768931c62d |  | note | Record of conformity: Survey records, pegs on ground & this ITP Signed
label | 438a35fc-ec03-50d4-91e0-8367a7ba57fa |  | note | HP*
label | 5df24450-b0fa-589e-b3c5-be24793110e0 |  | note | Responsibility: Site Engineer
date | 9a882aa8-6dee-5c7f-96b4-73ed6dc76226 |  | date | Date Completed:
checkpoint-group |  |  | section | 3 - Installation of Underground Stormwater Drainage
checkpoint-status |  |  | checkpoint | 3.1 - Excavation for pipe
label | a18a35ee-1c00-5a2f-88eb-d9da29ef9d7b |  | note | Frequency: Each Lot
label | cdf9b7bc-ee94-5e88-b695-29a7a2cc565f |  | note | Acceptance Criteria: The line of cut for each side of the trench shall be marked out on the surface before excavation commences.
label | 40c0b681-046a-5dea-aa6a-65638dfe098a |  | note | • Trenches shall be kept free from water, debris and falling earth.
label | 567e1d65-b5e2-58d9-9fdf-1426cc9320d9 |  | note | • The final trimming of the bottom 150mm of trench excavation must not be carried out until immediately prior to concreting or placing of pipe bedding. Excavation must be completed for a minimum of 10 metres length ahead of pipe laying.
label | 4fd4a38a-846d-5cf3-baaf-bbafe8aa0fd5 |  | note | Reference Documents: Drawings C.4.8b
label | e6adfe58-588e-5c1a-937b-4f55b5e61b18 |  | note | Inspection / Test Method: Visual Inspection
label | 290d76ff-5c14-50aa-b4a4-11d73018cbe7 |  | note | Record of conformity: This ITP Signed
label | bce85242-dee6-5ca4-af9f-ef66e0df2da1 |  | note | IP
label | 6d0a1678-8fea-5664-ab83-264e7b75ff3d |  | note | Responsibility: Site Engineer
date | 51f4550d-e32f-55ca-8853-4b5cdff8b1d0 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.2 - Trench Inspection
label | 3b3ce360-549c-5c60-a216-5e089a4d0a20 |  | note | Frequency: Each Lot
label | 152ce3fb-8317-5480-8b45-427499f23bfd |  | note | Acceptance Criteria: Superintendent shall Witness excavation prior to bedding or laying pipes, confirm pipe is placed at correct alignment
label | d8a8e3fa-1c04-5643-a862-080bcc9de5d9 |  | note | Reference Documents: C.5.20
label | b46400ae-5ad5-5d17-9933-998c680e7a2c |  | note | Inspection / Test Method: Visual Inspection
label | 2f0a143a-6168-5b7c-8198-deeaa66f8a4b |  | note | Record of conformity: This ITP Signed
label | ec856e1e-8272-5f83-89b7-badac082e1fa |  | note | WP
label | 9cacfe14-88b5-5600-8133-48a7d43a2314 |  | note | Responsibility: Site Engineer
date | 61ee8cf9-f8e8-5936-9abd-a20e82bf019e |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.3 - Trench Base Preparation / Bedding
label | f877edc8-1aef-56a6-b9af-bcc19dd2af6e |  | note | Frequency: Each Lot
label | 66c0e54a-af0f-5360-ad69-a2c7ccb2a35e |  | note | Acceptance Criteria: Trench bedding shall be 75mm Class 3 FCR compacted to refusal using hand held mechanical equipment for all plavement types.
label | 6e200539-7095-5fc0-90dd-d5b0b1ced77c |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.4
label | f66ab937-b4da-58f9-9bcf-024eb358538a |  | note | Inspection / Test Method: Visual inspection / Measure
label | 3ff6836c-7784-5ca1-8f96-040678918e90 |  | note | Record of conformity: This ITP Signed
label | 24d308f2-ad7a-59c2-8969-fe00ec29a8df |  | note | IP
label | 69994507-61cc-5ea3-ad8f-411f4185d53c |  | note | Responsibility: Site Engineer
date | 9f1bd57c-5728-5512-87f3-c0364b672d69 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.4 - Haunching
label | cef2d575-8e51-50a8-a989-e96048efe533 |  | note | Frequency: Each Lot
label | e8325800-95f0-5b48-a069-b06535464b7b |  | note | Acceptance Criteria: Huanching layer to be placed reaching a height equal to 30% of nominal pipe diameter
label | d9026870-e386-5b24-91d8-6299c8f96d14 |  | note | • Haunch Zone to be compacted to refusal using hand held mechanical equipment
label | c7a77029-2878-59dd-8cf5-f255eaa56ae4 |  | note | Reference Documents: DWG EW-CE-DRW-526-001
label | edb5d190-d673-55cd-9311-ffea709594ea |  | note | Inspection / Test Method: Visual Inspection
label | 2934b60f-ff12-5bbb-825d-21b3dd3f72bf |  | note | Record of conformity: This ITP Signed
label | 5476e40b-9e14-5749-bf2e-b815de765521 |  | note | IP
label | 374598a0-9cd3-5a59-b81c-a4dbe0c51af2 |  | note | Responsibility: Site Engineer
date | 1fb37e64-44ad-515e-90af-d67814278608 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.5 - Laying of pipes
label | 0190c18d-3c22-5bdd-aea0-873ff0f97327 |  | note | Frequency: Each Lot
label | 0acadd22-802d-524e-bbfe-eb177f9b34d1 |  | note | Acceptance Criteria: All pipes shall be set in a straight line between access chambers or between access chambers and headwalls.
label | 512a1cef-0844-50a7-94fe-1193ae0cfe6b |  | note | • On inspection by the Superintendant, any pipe not placed in a straight line shall be replaced at the cost of the Contractor.
label | 68809eab-f711-50ea-86b4-000be27e12ce |  | note | • Pipes shall be set in an upstream direction unless otherwise approved by the uperintendent.
label | 5ca5a711-f535-5eab-b5ee-6ff0965f4d98 |  | note | • When laying rubber ring jointed pipes the first pipe in every run of drain shall be firmly staked in position before the remainder of the line is laid. At periods of delay in laying the ends of the pipe shall be adequately fixed to prevent joint creep.
label | 46e67c17-7372-5c0c-b734-dbeebbc71360 |  | note | Reference Documents: Drawings C.5.1 C.5.5
label | fe2d0fb5-095c-59b7-b513-f67d523ede9f |  | note | Inspection / Test Method: Visual Inspection
label | 75a6871f-ae6d-5c10-833f-b822c4076505 |  | note | Record of conformity: This ITP Signed
label | dbd20ccf-4dcb-51ab-8f55-f149bd3da1f8 |  | note | IP
label | c1e46e21-8511-5c4b-a7de-4a98c6b94304 |  | note | Responsibility: Site Engineer
date | 7a980c96-d938-586e-a016-894d4a149d07 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.6 - Jointing
label | fb675360-9ad9-5f5b-ab48-170ae7a36868 |  | note | Frequency: Each Lot
label | 39f9b538-519d-5b02-a3eb-8b98a180fe29 |  | note | Acceptance Criteria: Pipes shall be jointed with rubber rings.
label | bfacb6e7-5b32-575a-aa43-bc56a7c43f34 |  | note | • Both spigot and socket shall be carefully cleaned of all dirt and foreign material. A clean rubber ring shall be used, accurately guided and centred on the socket and forced into place using appropriate lever tools where necessary.
label | 9e1f0948-1c8e-560e-a07a-c8e9a5122f49 |  | note | • The joint shall be checked with a gauge to ensure that the rubber ring has travelled uniformly home. Defective joints shall be immediately remade.
label | 1d7f62c1-21be-5f54-abdc-61aafd82e290 |  | note | Reference Documents: C.5.6 C.5.7
label | f6d1e92b-1f94-5153-ae54-8e462860cd84 |  | note | Inspection / Test Method: Visual Inspection
label | ddb1ed73-bef2-5428-9b8c-c40ff6f6e0c7 |  | note | Record of conformity: This ITP Signed
label | 48879e23-1974-51c1-a36e-44be189f3601 |  | note | IP
label | 72589baf-714e-5628-aa53-acfcd871d700 |  | note | Responsibility: Site Engineer
date | c5302075-fa13-5e23-b498-a3f8d7c072da |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.7 - Drainage Pits
label | 4cacea9d-7c8f-5a13-8cf2-b78fad982415 |  | note | Frequency: Each Lot
label | c03d4d31-e754-581f-aacb-1a087ee1118f |  | note | Acceptance Criteria: Drainage pits shall be in accordance with the stormwater drainage details and pit schedule.
label | 69cb7191-9557-546d-a7bb-e7744b871099 |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.15
label | 9caacee1-1fc8-533a-8f1e-742064cce534 |  | note | Inspection / Test Method: Visual Inspection
label | e9831100-905f-5f73-b327-674b64fd8258 |  | note | Record of conformity: This ITP Signed
label | 24f67e78-b951-5bad-92bc-e49d4849886d |  | note | IP
label | d159f8ca-68a8-547d-a97d-39e792a0ed31 |  | note | Responsibility: Superintendant, Site Engineer
date | e927428b-116a-53d7-a462-a739dcea1d8a |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 3.8 - Tolerance
label | 6cb9e26e-d734-5c22-96d5-7dcfd62c0a71 |  | note | Frequency: Each Lot
label | 98e50bfd-f053-5b2a-ad3f-38226c241ae4 |  | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
label | a58c1c28-1f0b-5921-98f2-09898f18d615 |  | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
label | 5436ea0c-d297-5dff-bbe3-1028e5b069b7 |  | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
label | 5c9e4d31-b208-500f-92b6-75d00d453950 |  | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
label | 6ee7ac2e-4883-502d-b174-367fd3c19c18 |  | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.21
label | 4fadc63b-f800-5a89-a756-cbfb5c9ca552 |  | note | Inspection / Test Method: Verify
label | a6d1d835-baa1-5d82-8ee5-3012ed861470 |  | note | Record of conformity: This ITP Signed
label | c75eaadb-e039-5e06-add9-4c827572b1ce |  | note | SCP
label | e1349975-f51b-52cf-a9cd-6290424979c4 |  | note | Responsibility: Surveyor, Site Engineer
date | c3a016ca-0bb2-50ec-948a-c99f60e38728 |  | date | Date Completed:
checkpoint-group |  |  | section | 4 - Backfilling of Stormwater
checkpoint-status |  |  | checkpoint | 4.1 - Inspection Prior to Backfilling
label | 428e2b20-7b81-58f9-9a29-a1ec94ca1e29 |  | note | Frequency: Each Lot
label | b9e538a0-23e8-5933-9ca6-5e64bf60b83a |  | note | Acceptance Criteria: Inspection by Superintendant of installed pipes prior to backfilling.
label | 17bb23cb-b30a-5946-8d21-f64738fb6bc6 |  | note | Reference Documents: C.5.20
label | c2c93aca-2b8c-5800-8b58-261d70192145 |  | note | Inspection / Test Method: Visual Inspection
label | 7c303d3f-4187-5a94-bcec-59b21c6c0346 |  | note | Record of conformity: This ITP Signed
label | 11130f9f-de1d-5fdb-8c50-5e4ea383b009 |  | note | HP
label | 30772680-efd7-59e7-bb3c-ddeefddad23e |  | note | Responsibility: Superintendant
date | f48d209a-0196-5764-b3ee-2674851f1f3b |  | date | Date Completed:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Filling
label | 82680afc-e8a2-597a-a53f-b51add2c2374 |  | note | Frequency: Each Lot
label | a64cc744-a59b-5991-b70b-34107ccf872a |  | note | Acceptance Criteria: (i) Under Landscaped Areas
label | b7b683b9-2455-5a7c-a466-71b1b50d3e43 |  | note | • Excavated backfill to be 200mm above top of pipe
label | 92a22720-769b-50cd-92eb-76f67047cee5 |  | note | • From 200mm above pipe to 150mm below surface - Excavated material compacted in 150mm layers to the density of the adjacent soil.
label | 261deb6a-21df-5159-8276-908106eaf570 |  | note | • Final 150mm - Topsoil
label | 62467eac-cc79-59fd-a5ea-8636c33472e0 |  | note | (ii) Under Any Pavement
label | 5586684f-a707-5691-af85-0ef721f80658 |  | note | • Haunching to 30% of pipe nominal diameter
label | 4f7368f6-f737-5789-8a27-a04361fd5ecf |  | note | • Backfill material to the base of the pavement
label | 13379fdf-8454-5b18-b5fa-c6f86f7c24b8 |  | note | Reference Documents: DWG EW-CE-DRW-526-001
label | 42a9f3f4-3da7-5d0c-803f-c5f3ad4ec81b |  | note | Inspection / Test Method: Visual Inspection
label | 7b2dded2-8e8c-5678-9db7-60953a98bc58 |  | note | Record of conformity: This ITP Signed
label | 1e0d372b-07ff-5f4a-a1db-158539064f51 |  | note | IP
label | 7a9f5725-ad62-584f-b57d-b5f556d1ec7e |  | note | Responsibility: Site Engineer
date | b6c0475d-a2e5-50f7-bd91-09a78d42346c |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 4.3 - Testing and Acceptance of Fill Materials
label | 839eaa79-d0a4-5c71-a390-8249879d6e36 |  | note | Frequency: 1 per layer per drain line. Test at each layer, near access chambers and along line.
label | 17b5c274-580e-5c4a-960d-26177f88de60 |  | note | Acceptance Criteria: Bedding and backfill materials shall be placed and compacted in layers not exceeding 150mm loose thickness and shall be assessed for compaction and moisture content.
label | 1c6590d1-a8c0-5af2-a671-c9fa8daefa1e |  | note | • Bedding shall be compacted to refusal using hand held mechanical equipment.
label | ac8aa0ed-85aa-59b0-97ad-8b91a84e4a48 |  | note | • Backfill material with nominal size < 40mm after compaction shall be compacted to a mean density ratio of not less than 97% CDR.
label | fe7cf077-c588-58ee-9254-e3eaf6ac0a42 |  | note | • Backfill material with a swell equal to or greater than 2.5% shall be maintained at a mean moisture ratio of 92% between the completion of rolling and the placement of the overlying layer.
label | e91c6bcf-b9dd-5a43-9f25-15e2ba17527a |  | note | Reference Documents: DWG EW-CE-DRW-526-001
label | b92d8a68-ca21-510c-b47c-ed49e8a3a4c5 |  | note | Inspection / Test Method: Verify
label | 10af9105-de28-5933-a026-8c7755a5e213 |  | note | Record of conformity: Compaction Test Result OR This ITP Signed
label | 1248edf6-02e7-5e35-afd6-6083121f8fd4 |  | note | TP
label | b1c4e032-f594-5ba3-9dc4-ff2bfcca3e2c |  | note | Responsibility: Site Engineer
date | 31198d0f-c691-54c9-b59a-1ee2ccf5ecfa |  | date | Date Completed:
checkpoint-group |  |  | section | 5 - Finishing and Commissioning
checkpoint-status |  |  | checkpoint | 5.1 - Finishing and Rendering Pipes
label | 3a3cfbf2-42f5-5214-bece-9fb1313396bc |  | note | Frequency: Each Lot
label | 0c5d1670-51d7-5c32-ac78-c5d51cfd0674 |  | note | Acceptance Criteria: All stormwater inlet and outlet connections shall be cut trimmed neat and finished with cementitious mortar.
label | 8cfd4156-9557-5f4b-b3c9-116e5e805efd |  | note | Reference Documents: Work Procedure
label | 7e8903a4-9893-5265-934e-62ffb571488b |  | note | Inspection / Test Method: Verify
label | 9a833394-20f0-5ac1-830c-dbb1b3254a86 |  | note | Record of conformity: This ITP Signed
label | 24364968-127b-5e2a-b297-762cd920baa2 |  | note | IP
label | ff694b32-7b02-5e34-8880-ce31a8cd63f8 |  | note | Responsibility: Site Engineer
date | 1d4dc3ff-87f4-53b7-877b-e357c751d4d4 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | 5.2 - As-Constructed survey and documentation
label | bbc3e1ed-78dd-5b93-9782-f268c824ebbe |  | note | Frequency: Each Lot
label | 3dd0b7a4-0277-597c-a03e-a908f411f4ca |  | note | Acceptance Criteria: The survey shall include all invert levels at access chambers, entry pits, headwalls and endwalls, centre to centre distance of pits, distances from centre of pits to headwalls or endwalls, size of pipes, types of pipes and bedding, location of pits in relation to adjacent boundaries, reduced levels of access chamber and entry pit covers.
label | f8435ac8-4ed7-540d-a7e1-2b05800bdaf0 |  | note | • Lot Maps shall be completed to show the extent of works for each lot.
label | 24e84b7a-c86b-53ad-8ee9-23ce43bf2e2f |  | note | Reference Documents: C.5.21
label | 3650747f-f64a-57ab-9cb4-90d4ffc96244 |  | note | Inspection / Test Method: Review
label | fca47132-3529-57f3-95fd-59602f6f24a7 |  | note | Record of conformity: This ITP Signed
label | 37eec2b4-bac9-59a5-8bb2-9b1b52a9ff87 |  | note | HP*
label | 9696be4c-6863-5ab9-b1ea-12f5a7c49dca |  | note | Responsibility: Site Engineer / Superintendent
date | 2d73915a-0e31-57a3-87ff-91bfdcb49186 |  | date | Date Completed:
checkpoint-status |  |  | checkpoint | Final Inspection
label | 2582c3d1-e318-5f0c-8cb6-02d0c3ad9447 |  | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | 576e7a40-60cc-51ea-b563-ce945e365a0e |  | textbox | Print Name:
text | a6e488e5-3434-599a-a2d0-17d39784da42 |  | textbox | Position:
date | a963f957-654f-55b9-bc48-912667ce3e6b |  | date | Date:
holdpoint |  |  | signoff | Sign ITP