## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  |  |  |  | Yes | QA 29 Periodic Flushing / Copper Protection Test Sheet | 0f49bff0-e928-44f8-9110-caa6ba8ab549
checkpoint-no-status |  |  | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
label | 91c3b742-289c-492a-901c-ff5eb4b392cf |  | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
label | f2f35905-7eee-4e46-97d0-b36e27dd7947 |  | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
checkpoint-status |  |  | checkpoint | Flushing Details:
text | 5d9378fc-2d49-495e-8804-0b329389ffb1 |  | textbox | Level / building being flushed:
radio | b6309a52-6d96-4c7c-b975-53b80255d385 |  | radio | Time and Type of flushing: | Ring main –Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains – Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
text | e7243ce2-9d64-4c58-b996-2ac16b7f5196 |  | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
text | ccb89c2e-4237-43fc-b8dc-3020d9be44a1 |  | textbox | Start time of flushing:
text | 3c882fe3-d2b6-42fc-8376-3bae411451e5 |  | textbox | Zone/branch to be flushed:
text | 5b1d763d-c04e-4b55-9006-fb2d93610f2e |  | textbox | Finish time of flushing:
text | 86799bbd-2cc8-46b6-bc85-9472ff1f29ae |  | textbox | Zone/branch to be flushed:
checkpoint-status |  |  | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
checkpoint-status |  |  | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
checkpoint-status |  |  | checkpoint | Have you set a reminder for the next flushing of this pipework?
checkpoint-status |  |  | checkpoint | Have the hot and cold been interconnected for flushing purposes?
checkpoint-status |  |  | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
text | 382e9354-7600-4be9-a9ce-810e71695909 |  | textbox | Date for next flushing:
text | f5f96a13-e5ac-4483-b4df-510f4411d371 |  | textbox | Test completed by:
text | a72591a1-acf7-4841-97b4-8d4d236d9aef |  | textbox | Builder Representative:
checklist-flat |  |  | checklist | QA 24 - Hose Reel Register |  |  |  |  | Yes | QA 24 - Hose Reel Register | 0fec0178-7efd-4c5b-b20c-59542c1aa10e
checkpoint-status |  |  | checkpoint | Hose Reel Register
text | d2369471-f25d-459c-a793-d8f9abaf6e66 |  | textbox | Ref No:
text | 5c8d3906-c0fd-402a-ab8c-00eac64b0a2b |  | textbox | Building:
text | 25f5439d-00bc-4ebb-b4e8-4c1c0aec9f85 |  | textbox | Zone:
text | de293246-7ba9-40e3-82d1-50ac727e0ad9 |  | textbox | Level:
text | c7b4fd1d-204a-4c97-8604-73f3ce42509c |  | textbox | Adjacent to:
text | 32186d76-5651-40c3-9665-db4ae40f7132 |  | textbox | Length:
text | 7bf4b882-9a8e-4250-ba7a-a15e93c10f74 |  | textbox | Date Tested:
text | bc3fb922-0bae-4529-9da6-c39e7830727d |  | textbox | Flow Rate:
button | bdfb94e9-d498-442b-baf9-78788a9df1e2 |  | button | Obstructed Access | No,Yes
button | 831fcd38-1de7-4aaa-abbc-da3f8944805a |  | button | Operating instruction visible and legible | No,Yes
button | 99dd4fe1-4e87-4d80-a09f-cc6cfbe1fa48 |  | button | No leaks throughout hose reel mechanism | No,Yes
button | 4a1eb221-60d9-421d-911a-28eb57072126 |  | button | Hose runs freely through guides | No,Yes
button | 8be63dc0-abc4-45d3-977f-98ee9a496720 |  | button | No signs of corrosion | No,Yes
checkpoint-status |  |  | checkpoint | Result (Pass / Fail)
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Fire |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Fire | 108cce7b-0451-4142-a98b-ea31135a88af
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | 759146f7-d052-4dc9-a78b-90a6a6a0bce4 |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | a6cd316a-a4a1-4d39-ae46-f710c8bd144d |  | note | Spec#: AS3500
label | 6b66e455-efaf-41cd-be88-104d66e14c9d |  | note | MDPE SDR11 PE100 PN16
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | c85c9a9e-57c8-4ce9-9fca-c9f30e6a8cb2 |  | note | Spec#: AS3500
label | a607b76a-ce5a-4632-9a43-e70f34c492c8 |  | note | Packing sand encased pipe
checkpoint-status |  |  | checkpoint | Jointing of pipes
label | 4c7826b1-e8b7-4f1f-9542-7a373a47259f |  | note | Electrofusion and/or Butt Welds
label | c91132b9-771c-4c0b-97f2-e345898ea7b7 |  | note | GPLQA16 form
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
label | cf52bb20-9c57-4d8b-bb3f-d161620f63ee |  | note | GPL QA6 form completed
label | 058c9336-61bb-4f8a-9c97-17d1fb85aa50 |  | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 88be9585-5ffe-443c-ad16-492ae061f75a |  | note | Compacted crushed rock backfill 80% to 100% compaction
label | 87ea8b3c-7126-4b31-bdb0-011b09a5cb12 |  | note | Detectable marker tape
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | 4b8ade35-eb43-4980-87cf-ac27e76d4c07 |  | note | Ongoing
label | be0eb3d1-26b3-4a2a-993d-cc4d917bfde4 |  | note | To be provided
checklist-flat |  |  | checklist | Equipment Calibration Register |  |  |  |  | Yes | QA 11 - Equipment Calibration Register | 14a93f78-7a3d-4ef8-8783-e06d00fb2252
checkpoint-status |  |  | checkpoint | 1
text | 47a9e14c-d0a5-4f1c-9664-761b704b5d85 |  | textbox | Equipment Type:
text | 758656de-076f-4745-a778-350530675274 |  | textbox | Manufacturer:
text | ddea0a37-a857-451d-9ee0-1ad281dab77a |  | textbox | Model and Type:
text | 39a41809-f5ba-48a2-8c6c-be8fc1435051 |  | textbox | Serial No.:
text | 3934c130-9fe3-4344-b29d-b85a3e215085 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 2
text | 16d1aa39-7d3d-4540-9dd2-e972fcbebf06 |  | textbox | Equipment Type:
text | 232f5c69-e5a9-4fd2-a941-0136bd4ba383 |  | textbox | Manufacturer:
text | c58aadb6-51b9-46d1-a135-355445f87aaf |  | textbox | Model and Type:
text | 0a9bb1f2-d114-4ebf-91af-7b435883a837 |  | textbox | Serial No.:
text | e4f3ddae-2c00-436a-9d8a-342801af51b8 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 3
text | 176ababf-4d81-4db4-8920-5254e7163a6d |  | textbox | Equipment Type:
text | a2450bf7-2c04-46c3-b097-c4e9b62d1af8 |  | textbox | Manufacturer:
text | e05d0661-5073-497a-b267-cbebcd3f895b |  | textbox | Model and Type:
text | f1175805-675e-4da2-8b69-977232f5f8a0 |  | textbox | Serial No.:
text | e4fd1fba-637d-4f1c-8d3b-f2dea191e41d |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 4
text | 5b5e1d4f-f9fc-436b-b062-1bf670bf274d |  | textbox | Equipment Type:
text | c7ce4ede-39b0-454b-9253-b222e60df68b |  | textbox | Manufacturer:
text | 434251aa-bd39-4b54-86fa-301f83c3379b |  | textbox | Model and Type:
text | f4a89dcb-4e47-4515-bd86-ced68a954bf0 |  | textbox | Serial No.:
text | bbfe698a-4ae6-4b5e-b9d9-40f829f600ad |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 5
text | ab6cefaf-b995-469f-910b-57a0d4ccb954 |  | textbox | Equipment Type:
text | 5c5a47b3-7f80-4629-8c5d-2226a369d009 |  | textbox | Manufacturer:
text | 27f43d6b-eb88-40a0-972d-0c641da4d90f |  | textbox | Model and Type:
text | ea26ce8d-6758-4672-ba50-7f39a0b0c194 |  | textbox | Serial No.:
text | c5fec240-74b7-4639-95ac-feecdc282c17 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 6
text | 50223c02-af60-4eda-a19b-95b5096b485c |  | textbox | Equipment Type:
text | ea45abed-a0d0-4360-8ea8-961087928ccb |  | textbox | Manufacturer:
text | f8554fe4-e85d-4335-81f8-499ce5a22141 |  | textbox | Model and Type:
text | ac80ec4c-0dcc-4a78-8a7f-f522cc716475 |  | textbox | Serial No.:
text | 9ac3b03b-cacf-4d03-82c6-169881ec1c81 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 7
text | 9f34a9fc-2589-4aa2-9add-01dc00876c43 |  | textbox | Equipment Type:
text | 9776fd50-4f94-4bf7-a9af-027dd291e441 |  | textbox | Manufacturer:
text | 9ce82e6d-aa6b-473a-b94c-cc2eb1bc75a2 |  | textbox | Model and Type:
text | c4babaa9-d8e1-47b4-9611-e8394dd834df |  | textbox | Serial No.:
text | 02bc8107-4231-464f-9570-a39a29edf214 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 8
text | 16edabee-2ea6-45ab-913c-b67abda25ba8 |  | textbox | Equipment Type:
text | c3cb67e6-1e0c-4eac-99cc-6b7769f4c57b |  | textbox | Manufacturer:
text | 3da2f2ed-06d8-4775-a909-295ab66fe0fb |  | textbox | Model and Type:
text | 68a1a285-be2c-4cbd-90b8-93b4f0831d1d |  | textbox | Serial No.:
text | 46545cc4-0521-415c-97a6-46f805d7b77f |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 9
text | 9de1f871-d23e-41f9-88c2-4f88f73345b0 |  | textbox | Equipment Type:
text | 6fdf3c79-95b4-4180-b20b-72661d47d21d |  | textbox | Manufacturer:
text | 68ca8910-3af1-4f79-86e3-9c298203de1e |  | textbox | Model and Type:
text | 1b258249-f05d-49cc-85be-6300f688b4e6 |  | textbox | Serial No.:
text | ac8d35ef-a457-4d02-870e-48f419bf75fd |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 10
text | 98d82710-31db-440a-a0f8-8030b49b46a9 |  | textbox | Equipment Type:
text | 0eb60711-20db-4ae5-9ebf-03f7f5cc9841 |  | textbox | Manufacturer:
text | 1636e898-ac39-45f2-a4af-1d92f7552629 |  | textbox | Model and Type:
text | c0323ad9-1dcc-40c2-8ab3-4a6ba2d55451 |  | textbox | Serial No.:
text | 2c02d390-d619-4804-9c1d-77c1fa62f29d |  | textbox | Next Service Due:
checklist-flat |  |  | checklist | Grease Trap Checklist |  |  |  |  | Yes | QA 8A - Grease Trap Checklist | 26e546a8-f0ff-4e9a-ac6b-dc06f855b103
checkpoint-status |  |  | checkpoint | Set out of pits.
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
checkpoint-status |  |  | checkpoint | Laying and jointing of pipes R.L’s and falls
checkpoint-status |  |  | checkpoint | Connections to pits.
checkpoint-status |  |  | checkpoint | Baffle is in place.
checkpoint-status |  |  | checkpoint | Penetrations are patched and made watertight.
checkpoint-status |  |  | checkpoint | Suction line is installed as per spec.
checkpoint-status |  |  | checkpoint | Outlet pipework is installed as per spec.
checkpoint-status |  |  | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Sewer |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Sewer | 34f6ddc6-b8b4-4e37-aa98-e2ecf581a619
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | 759146f7-d052-4dc9-a78b-90a6a6a0bce4 |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | a6cd316a-a4a1-4d39-ae46-f710c8bd144d |  | note | Spec#: AS3500
label | 6b66e455-efaf-41cd-be88-104d66e14c9d |  | note | UPVC BEP Type ISO 14001
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | c85c9a9e-57c8-4ce9-9fca-c9f30e6a8cb2 |  | note | Spec#: AS3500
label | a607b76a-ce5a-4632-9a43-e70f34c492c8 |  | note | 75mm Q-Minus Bedding and Encasement to top of pipe
checkpoint-status |  |  | checkpoint | Laying and jointing of pipes R.L’s and falls
label | 4c7826b1-e8b7-4f1f-9542-7a373a47259f |  | note | PVC solvent welded
label | c91132b9-771c-4c0b-97f2-e345898ea7b7 |  | note | 1:60 fall
label | cde2c9b4-a714-49bd-9dda-f1d5f61ffb85 |  | note | AS3500
label | fa0e508d-8c66-43a9-9c0c-b7e8f431cfb2 |  | note | RL’s as per hyd drgs
checkpoint-status |  |  | checkpoint | Connections to pits and existing services
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
button | f27f01d4-6007-48ac-a73f-034f2c3ba668 |  | button | Air or Water? | Water,Air
label | cf52bb20-9c57-4d8b-bb3f-d161620f63ee |  | note | Inspected and recorded by Independent Certifier or PIC
checkpoint-status |  |  | checkpoint | Mirror tests are completed if required.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 88be9585-5ffe-443c-ad16-492ae061f75a |  | note | Compacted crushed rock backfill 80% to 100% compaction
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | 4b8ade35-eb43-4980-87cf-ac27e76d4c07 |  | note | Ongoing
label | be0eb3d1-26b3-4a2a-993d-cc4d917bfde4 |  | note | To be provided
checklist-flat |  |  | checklist | Project Photos |  |  |  |  | Yes | Add Project Photos | 425f41ed-9399-4e82-96c9-7ce997e11891
checkpoint-status |  |  | checkpoint | Attach Photos and Comments
checklist-flat |  |  | checklist | Stormwater Drainage Inspection Report |  |  |  |  | Yes | QA 8B - Stormwater Drainage Inspection Report | 523090e0-f121-4bc4-b473-2141c382101a
checkpoint-no-status |  |  | checkpoint | Stormwater Drainage Inspection Report Details:
text | ae28f5ef-1be6-447d-9298-77b7cc535233 |  | textbox | Spec No.:
text | dba0888a-6d98-4ead-b9d3-709711a1e213 |  | textbox | Drawing no.:
text | a75b9960-5172-4b28-9c51-3cea6753ce7b |  | textbox | Zone:
checkpoint-status |  |  | checkpoint | Pipe Lines
text | acc7075c-1cc9-4276-b7ed-df75129bb570 |  | textbox | Date started:
text | d6163adb-2cd4-4e3b-99d7-11cba02eec04 |  | textbox | Drainage Line Number:
button | f0388d22-9ae3-470e-994a-a6f9cc7356eb |  | button | Pipe Damaged? | No,Yes
text | 1f5b0a64-1765-4114-98ff-102d93a5f2f3 |  | textbox | Size and Class
text | fa07ac66-ae61-4c17-9d85-a669bf489329 |  | textbox | Jointing Required
label | fc0dac4c-6276-4d94-abe9-782e25f6657c |  | note | Bedding and Haunching
text | c2685355-4417-45c4-8e74-514571a5eb7b |  | textbox | GPL - Initial/Date
text | 18e7ca6b-8126-490b-a7a3-3da85ff1971a |  | textbox | Builder - Initial/Date
label | 8161f2ba-a893-4431-95ca-b69d0d04cfbb |  | note | Backfill
text | c7575b93-72b3-483f-b92d-8490e5a1d05c |  | textbox | GPL - Initial/Date
text | 2833a462-b5e8-46c7-a84c-0e275ec5f564 |  | textbox | Builder - Initial/Date
text | 115b3685-341e-49ee-911c-c4463a1c6e33 |  | textbox | Comments
label | dc8e08d0-da89-4730-a7a5-f9874173c654 |  | note | Final Sign Off (Initial & Date)
text | 2f5c8d85-b06c-42e5-b012-335237420330 |  | textbox | GPL
text | 2ac6a4e1-bfb1-4090-a669-d090aa096955 |  | textbox | Builder - Initial/Date
text | f85146c2-8973-47b3-86d7-6efee107c5d5 |  | textbox | HCC/CARDNO
checkpoint-status |  |  | checkpoint | Drainage Pits
text | 31062e65-85cb-42fe-81d9-65866158fc11 |  | textbox | Date Installed:
text | 9a9114bf-6256-4cfd-9252-afe37232ec35 |  | textbox | Pit Number:
text | 3c739c76-cdb7-48ef-9c16-0c7c0895e5ca |  | textbox | Pit Base:
text | ef261927-2bb4-4124-a7c1-0afc4bb2343f |  | textbox | Step Irons - GPL Initial/Date
text | a901bfb0-56ba-41f5-b1b4-d42f944ecdbb |  | textbox | Bedding - GPL Initial/Date
label | d5a499d7-8b30-4f26-bcd5-93954f625fc5 |  | note | Benching, Grouting and Patching
text | e03a9b9d-6c81-46e9-b2fb-a37f01259fb9 |  | textbox | GPL - Initial/Date
text | 6909a54d-4e6c-405b-a56b-109ca6a95493 |  | textbox | Builder - Initial/Date
label | a53d5436-0be1-4944-b7b4-b7bc8fe6c709 |  | note | Placement of cover
text | 2c6b89e2-96b9-4fb8-a3f8-84d2e6863eed |  | textbox | GPL - Initial/Date
text | 5420c6d8-6149-4f57-84f1-913a4c2e444a |  | textbox | Builder - Initial/Date
text | f74be5c9-bfb3-4ffa-be60-59f66c2451da |  | textbox | Comments
label | 2bbcc99b-b30e-4907-bc35-2bda9fc70400 |  | note | Final Sign Off (Initial & Date)
text | 2d7a5320-c84f-431f-9a04-a1bf81edd720 |  | textbox | GPL
text | d3c433b5-b3b2-43e0-8fec-d213720f8c73 |  | textbox | Builder - Initial/Date
text | 4d3d16c3-7515-43bf-9f99-2bf7c1ed0245 |  | textbox | HCC/CARDNO
checkpoint-no-status |  |  | checkpoint | Compaction Test Report No.
text | f4d2d6ae-245d-4788-9f59-327e6aea8132 |  | textbox | Compaction Test Report No.:
checklist-flat |  |  | checklist | QA 6D - Quality Control Gas Regulation Test Report |  |  |  |  | Yes | QA 6D - Quality Control Gas Regulation Test Report | 5ff5a3d9-985b-42fa-a033-32e450ccf1be
checkpoint-no-status |  |  | checkpoint | Quality Control Gas Regulation Test Report:
text | aa7b0c11-205c-463c-8c62-82a049595d17 |  | textbox | Drawing No.
text | 4d1d3ce4-7a88-4b67-9e96-d23ace24fae6 |  | textbox | Rev:
checkpoint-status |  |  | checkpoint | Test - Flowing inlet pressure to project
text | e216fdb1-271f-4e79-91ca-5633d815ef7b |  | textbox | Inlet Pipe and Size:
text | 7de8045e-7930-49ae-ba46-67d964a50d0f |  | textbox | Spring range:
text | d18a15dc-e1bf-4df7-9465-5d83a6325d9e |  | textbox | Orifice Size:
text | f1ad6c8e-a239-4d7b-9af1-5e38bd5eb4b9 |  | textbox | Model:
checkpoint-status |  |  | checkpoint | Section
text | 247cb8c4-2227-4c32-bc68-df377a434e79 |  | textbox | Section:
text | 6fcfbb4a-1c51-4fb1-9b87-5263ee5e4231 |  | textbox | Pressure (KPA)
checkpoint-status |  |  | checkpoint | Test upstream inlet pressure to regulation
text | 9c4391dc-c7e1-48c3-99ba-2d1606405ebd |  | textbox | Pressure (KPA)
checkpoint-status |  |  | checkpoint | Test downstream out pressure to regulation
text | 8ffacbec-4c2c-4a2f-8f35-27dd3e40bafc |  | textbox | Pressure (KPA)
text | 8749d5ca-e2bf-4f21-9fdc-701306e2cb4b |  | textbox | Duration (hrs)
checkpoint-status |  |  | checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
text | 0d324147-53c4-43d6-b521-230cbf90d115 |  | textbox | Reading (KPA)
checkpoint-status |  |  | checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
text | 6473941c-75c2-49ed-93a3-2c4c59483622 |  | textbox | Repeat:
checkpoint-status |  |  | checkpoint | Sign Off
text | 43233c89-1a4b-47ea-9d7c-d8d1058b6d2b |  | textbox | Geschke Pty Ltd. Representative:
text | 0d96125b-ca7d-4fbe-99e0-266c688d06fa |  | textbox | Others Present:
text | 8240c602-4096-4731-b197-3675cc91cb1f |  | textbox | Date of Satisfactory Completion:
checklist-flat |  |  | checklist | Installation Test Sheet (Waste, Vent, Downpipes etc) |  |  |  |  | Yes | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.) | 611da09e-e869-4534-990f-38894216f2c0
checkpoint-status |  |  | checkpoint | Installation Test Sheet:
text | 78b2ec8c-6f3a-48f1-ae2a-cb17559e5a36 |  | textbox | Drawing No.:
text | 2310aad6-6704-411a-998f-ff676d596aa1 |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | PIPE CLIP HANGERS
text | 111debee-875b-47e1-82de-fa3b8bf65532 |  | textbox | Details:
text | 1dcd6bc7-08bd-4c74-997d-11f90951183b |  | textbox | Tester:
text | 010772e4-dce3-4244-801f-a42ec054dff3 |  | textbox | Date:
text | 6455a6c5-f338-439d-9072-08d8ef7c0bbf |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | MATERIAL AND SIZE
text | b9ac3170-e4de-4fe9-a6c3-a0f87b029366 |  | textbox | Details:
text | 8df24e14-981d-4093-85f1-b8f2ecf80918 |  | textbox | Tester:
text | c0005153-cab8-4cb0-be8f-04c54c4ee5e4 |  | textbox | Date:
text | 99a4ae60-6d61-47ee-aaae-a6f7bf0249cf |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | ALIGNMENT
text | fa885f5d-1e31-4c2a-b335-e6d617648947 |  | textbox | Details:
text | ced084ce-ac5e-447e-8f6d-82e6edce9378 |  | textbox | Tester:
text | 244ddccb-97ba-4f00-9af5-6c220e07a5bb |  | textbox | Date:
text | 99188a96-1530-43d4-b26d-9a1b5235fcbe |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | LABELLING AND IDENTIFICATION
text | f44d9998-de17-417c-bc21-6e6e6a50a333 |  | textbox | Details:
text | 545dbdac-222e-448a-802d-0fd8447a1c52 |  | textbox | Tester:
text | 622380f3-c20c-4c75-9d7f-e43fec739647 |  | textbox | Date:
text | 446efcf8-ec83-43d9-845b-710f06a5db7c |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | JOINTING
text | 9f18b5d9-2811-4166-bdd1-795ee4340438 |  | textbox | Details:
text | bfee49d2-a676-4a3a-a72b-a333c53abafd |  | textbox | Tester:
text | 82c941cb-d290-48ae-8b92-42ceea3d0ff0 |  | textbox | Date:
text | 4588953d-eaf0-4b8a-87e1-3a1a94bb96fd |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PENETRATION SEALING
text | 80305e88-1e9f-4c40-a3c1-adba0b766946 |  | textbox | Details:
text | 2444abf9-776a-42bb-9d84-d664fb63eb90 |  | textbox | Tester:
text | 330c9865-81a8-473e-869f-dcc435d71a9c |  | textbox | Date:
text | e14773a2-74a9-4dd8-b635-dab2d8a8e80a |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | FIRE STOP COLLARS
text | 7fa99731-ab52-4af6-bde8-03f7e2dd02ec |  | textbox | Details:
text | 7d378379-1632-4bf8-bc04-4243c85a53b8 |  | textbox | Tester:
text | fc068ffb-9a39-4511-9936-4cb7a0dd6cbd |  | textbox | Date:
text | 0e2135fb-7eb5-4d5c-99a8-05a328a6221f |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | TESTING
text | afcd7558-17db-42e5-9e83-7fc2744bb1f3 |  | textbox | Details:
text | b40fc377-229b-48c8-8750-cc1314982c02 |  | textbox | Tester:
text | cc0ec66d-4d68-43ad-9626-8e8d10dc3fc3 |  | textbox | Date:
text | e21d9a8a-62a2-4f77-b0e4-945b89d9c0c8 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AUTHORITY INSPECTION (if applicable)
text | 6f08ac9d-94dc-439b-aeb8-2a782c898a66 |  | textbox | Details:
text | f5856bb4-c4ce-485b-b830-b886e4dd3b87 |  | textbox | Tester:
text | 797e10c1-7d2e-4aa1-b529-361051d7208e |  | textbox | Date:
text | 095cfc15-7823-4998-a3ae-2fe880a08dfe |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
text | 3de90039-49fa-4c21-afbc-055471aa44db |  | textbox | Details:
text | 167d8e39-140e-4dd8-9c94-80a1f067a9a3 |  | textbox | Tester:
text | a17204d0-f37d-4de5-b2f8-c59ab6c235b9 |  | textbox | Date:
text | 3b536854-cf17-42ac-b622-4c5376c3373b |  | textbox | Notes:
checklist-sectioned |  |  | checklist | 2021 |  |  |  |  | Yes | 2021 | 69d125ee-a4fd-438f-85bb-bc4a24389fea
checkpoint-group |  |  | section | 1 - Service room 8R.1
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | 3643c9b9-4c48-59d6-a8e1-40eb35a235f5 |  | textbox | Project:
text | acf9d2f4-60d0-58d5-ab3b-cb4bc82d6edb |  | textbox | Owner/Occupier:
text | 3dc88f26-5bca-5358-87ab-587c1363f918 |  | textbox | Address:
label | 20c3ea98-35e0-53da-be92-06306508f00a |  | note | Type of Test: Annual Test
text | 3a087955-c9a7-57de-b2f3-d39ff2e889e3 |  | textbox | Location of Device:
text | a76b4b9b-143f-57c2-ba45-f85c25ef756e |  | textbox | Authorized Tester Name:
text | 0d0ccfdb-0631-556a-b91b-a8329ae8b344 |  | textbox | Test Kit Serial No.
text | d27911ef-5835-5c25-b46f-6270bf976406 |  | textbox | Tester Licence No.:
text | 7ef255d8-f1d4-500a-89d8-8e8b42427d27 |  | textbox | Test Kit Calibration Date:
text | 0776c77f-4606-50b7-8c2d-4c9ca0788678 |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | 475b3313-8928-5d3e-8b89-d845a241277c |  | button | Permission to Isolate Water Supply | Yes,No
label | b2c4f4dc-bb2c-52c0-9aca-2eb544d53829 |  | note | Device:
text | 6179f241-54e5-54c7-9c14-1bb598c41a18 |  | textbox | Make:
text | da01749f-2eb3-5604-8c08-7281de444440 |  | textbox | Size: |  |  | mm
text | 1a8f5b50-0f9a-5e2e-bb26-21059a3d29d9 |  | textbox | Model No.:
text | a0305970-60c3-5703-b504-8eacb53e48e8 |  | textbox | Serial No.:
button | 86fdae05-7e1e-5c97-8883-7592a7606055 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 20309b14-bfee-52a4-b8e3-4e8e4a7de72a |  | tickbox | Containment Protection
boolean | 757a36fa-2c22-55e2-94fa-579a701c6f2e |  | tickbox | Individual Protection
boolean | dcc37af3-8008-5081-9284-59738d5f6476 |  | tickbox | Zone Protection
button | 5de7d37d-4446-51bb-8d94-396f6c00e699 |  | button | Strainer Installed | No,Yes
button | 9c0e6998-fbdf-5988-8c09-a3561f8adaab |  | button | Strainer Cleaned | No,Yes
radio | eaf31e93-7c56-5e76-9082-825715fb9e08 |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | c970b407-f129-57f8-8fbf-097ba6ab28c9 |  | note | Valve
text | 6385108c-5506-5af8-89a3-c724a830c551 |  | textbox | Check Valve 1
text | c4f585c6-e462-54e6-a57d-a616f7d45cfa |  | textbox | Check Valve 2
text | dba766ea-6b66-57b6-bc82-5558f6ae74d2 |  | textbox | Relief Valve
label | ada7a5a6-d235-5fa3-a9e0-520fac348a63 |  | note | Testing Results
text | c19f55d0-491e-560e-97c5-f8311b2a13fe |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 9a247d45-5de3-563c-90ff-b095a71df224 |  | tickbox | Leaked
text | ed38755c-cbd4-5fcb-8a54-447b9e122bdf |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 6de5f839-d413-549a-b934-43b2130cf454 |  | tickbox | Leaked
text | b18b2f92-ec86-58b5-9737-5b590fee23da |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 19ac02bf-7865-5515-80f5-717967733c73 |  | tickbox | Leaked
label | 317a81f8-6065-5209-a389-317f14d47278 |  | note | Reason for the device failure
boolean | 8e07d478-30aa-5219-8f0a-0f9962a44583 |  | tickbox | Incorrect position
boolean | 5d85a7e4-8a26-5210-8169-31f6e996ff41 |  | tickbox | Incorrect installation
boolean | 1d2673f8-51da-5c17-973d-508fa1ef411f |  | tickbox | Foreign material in the device
boolean | d06217c1-fa26-51eb-a373-ab5958eebe3c |  | tickbox | Spring wear damage
boolean | 863e7385-b61c-5057-b3a7-165284631d1e |  | tickbox | Seal or Rubber Damage
boolean | 4588c26e-c422-5f81-94b0-d263cebc1314 |  | tickbox | Other
text | 32d8af59-3373-5f51-b112-3b5b6e6a47b0 |  | textbox | Other:
label | 3c79b6d7-92c3-51a9-a05d-b13d47a43439 |  | note | Test after maintenance
text | f57d9ac9-5f67-51cb-9755-7c780cdeed94 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | c8cb2480-35ed-5c52-80d6-b5d8c8b928b2 |  | tickbox | Leaked
text | 132e9897-50c0-56d6-81eb-9e5b94d31e9b |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 42039aa1-016e-5ca2-9e46-4d5ac1c1ce7f |  | tickbox | Leaked
text | e559c5d0-4ea0-52b7-b6ae-e95cf6418aaf |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 1ae4956e-9ab8-5953-8780-b02dd1bdc3e2 |  | tickbox | Leaked
button | d642a8eb-6ff5-598f-95d4-16770592c6e4 |  | button | Water turned back on | Yes,No
text | 6d7fe914-8dfc-5a07-882a-8dfc161bd320 |  | textbox | Describe the maintenance:
text | 4936f5f6-36b5-5424-9b74-3dd829c3c74f |  | textbox | Parts used in repair:
button | f15284df-c197-5025-8965-19bdc6f9a97f |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | b0e0aa1f-2744-5b60-819f-fc3c654de0ff |  | textbox | Tester Name:
text | cf2824c6-e293-57c3-85f4-9a64b310d473 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | 2 - Pump Room 8R.08
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | 70ee6a63-7ba3-5bc5-8164-7138d7586383 |  | textbox | Project:
text | f2653211-3dc4-555d-8643-3b5093582b18 |  | textbox | Owner/Occupier:
text | 11884f2f-d631-56cf-a27e-a9f94cece6f4 |  | textbox | Address:
label | 34bba085-49bb-5e16-9c56-dba023c09be0 |  | note | Type of Test: Annual Test
text | 7f5ed6b9-3b58-5e79-a3f4-2144296abb85 |  | textbox | Location of Device:
text | af76a61f-9d81-5810-afd0-72eb75a2cbcb |  | textbox | Authorized Tester Name:
text | a309587e-dd99-5aa4-aca1-f8ae8f11768c |  | textbox | Test Kit Serial No.
text | 13c13c0e-3443-5c69-8b80-1537db039db7 |  | textbox | Tester Licence No.:
text | 3ac25756-f3fb-5a3a-9104-5303e2ba3e06 |  | textbox | Test Kit Calibration Date:
text | 5d965f95-59b2-5d0e-9699-73b66a1aa83a |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | 6fba9399-6b8c-5fd6-be49-007223f6f513 |  | button | Permission to Isolate Water Supply | Yes,No
label | 179aae21-acc6-51de-aeca-7822ca4c86a2 |  | note | Device:
text | 31808b16-6fc2-5f98-bcc0-34dabd5b67fb |  | textbox | Make:
text | f34d1ab8-d106-579c-9746-c16a4db0f047 |  | textbox | Size: |  |  | mm
text | a1eef73d-6207-5a15-bad5-9cdff1cebd5d |  | textbox | Model No.:
text | 788ca242-9e42-5f98-aa03-6e4cff86173d |  | textbox | Serial No.:
button | cee09a2c-e062-514a-82d1-bdb90cd9f320 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 228e566e-40bd-5bea-ab33-639766b8f83f |  | tickbox | Containment Protection
boolean | c2c2ea36-6525-5bdf-9b30-76f6a95dfd29 |  | tickbox | Individual Protection
boolean | 192f1abf-4b64-53fe-8f6e-f22e4c6214fb |  | tickbox | Zone Protection
button | 1eca8d01-db94-5cf6-a181-95d805136d82 |  | button | Strainer Installed | No,Yes
button | 8f79faac-0885-559b-918b-315a7a861c53 |  | button | Strainer Cleaned | No,Yes
radio | 2c82ee5c-0109-54fc-b333-43dddeb38403 |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 99c57f65-61a7-5bec-97e8-bd5d68c53dfd |  | note | Valve
text | 0ccdef50-19f4-5091-b30a-60ece0a36b49 |  | textbox | Check Valve 1
text | 14161bf5-bf5a-55b6-9d14-be917cdffe71 |  | textbox | Check Valve 2
text | 1e8961fc-ac6d-5d71-8389-86a03eff151c |  | textbox | Relief Valve
label | 5757f7c8-592c-5e3b-8f5b-eb2e466c593b |  | note | Testing Results
text | 8080e875-5266-50c6-8bd2-b512cd39904d |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 9a2605a6-2bcc-594c-bd57-3814a8da7462 |  | tickbox | Leaked
text | 9fb4b0f7-7c02-55e6-b1c6-dd50496ba122 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | c09308ea-8624-5fa5-bc78-dc765be891a4 |  | tickbox | Leaked
text | 1c989fe1-c56d-5886-ba4d-04d3f8563a51 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 417749d5-8437-574b-8823-54f346e5d4a6 |  | tickbox | Leaked
label | fbd041dd-1bdf-5821-a8b7-dfc442c959be |  | note | Reason for the device failure
boolean | 4ee00ea7-ae53-5858-bb0d-896b28206be9 |  | tickbox | Incorrect position
boolean | 2e29ecab-20c4-52af-b651-a69c07d2df8d |  | tickbox | Incorrect installation
boolean | 45ca5553-83b7-5189-a86e-67a1ba06e1e9 |  | tickbox | Foreign material in the device
boolean | cf4671d5-3d2d-5ba1-84eb-15bfdc550f5e |  | tickbox | Spring wear damage
boolean | e1fbdfa6-cf1a-5ab5-a0e9-2ba6ef6ca385 |  | tickbox | Seal or Rubber Damage
boolean | 3a2fe8a0-e346-59bd-b6b3-cc3d8a6f190a |  | tickbox | Other
text | 63033a23-d000-5db5-8af4-9d72b8c1d7b7 |  | textbox | Other:
label | d5f4ef34-ff99-50ad-96bd-768bd9cbbfeb |  | note | Test after maintenance
text | 262c5888-6b8a-5ccb-b4e4-b62de2690b25 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 09b08f03-2f50-5592-99b8-6b8c81cb7cf5 |  | tickbox | Leaked
text | 873487da-48e2-5493-9206-bbd1f1efcc98 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | a09b3598-dd2f-57bd-aea7-4ab4b3e2e0cd |  | tickbox | Leaked
text | 4bb2b33f-57d5-5d89-af51-f0566ddfe423 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | bea37075-c58a-567e-b6b9-38377a8ee994 |  | tickbox | Leaked
button | 1f0522d1-1a3a-5a0b-a561-0cf09ee633b2 |  | button | Water turned back on | Yes,No
text | d988f9e2-347f-5310-85cc-99fe5fc6d552 |  | textbox | Describe the maintenance:
text | a999ac65-3423-5052-a3fb-e0453251fab2 |  | textbox | Parts used in repair:
button | 4f74fd71-4fe0-5ba6-9dce-a82c7716deb5 |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | b5a2450e-573b-5d9b-8803-3d18741a7134 |  | textbox | Tester Name:
text | 4c84451b-7f03-5645-b61d-394829e0ccd4 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | 3 - Service Room 8R.10
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | cfb5e2c0-83b9-5bf6-8a1d-09df7d0e9733 |  | textbox | Project:
text | 83f72d7e-34ac-595a-a24d-62c550f355a6 |  | textbox | Owner/Occupier:
text | 253443e2-a7c6-575f-ac72-07287ab52abf |  | textbox | Address:
label | 8db59df8-7154-58dd-b06b-deee2bba8fa4 |  | note | Type of Test: Annual Test
text | 57ba071a-909d-552c-9730-922a5e0276b5 |  | textbox | Location of Device:
text | d75bf51b-231a-51a6-a76b-58698bb4b245 |  | textbox | Authorized Tester Name:
text | f79547a6-f0eb-53b7-bee7-86ba3d75a27f |  | textbox | Test Kit Serial No.
text | ecede4b4-c9b6-592f-9148-127039363625 |  | textbox | Tester Licence No.:
text | 6874efd0-bd53-5d92-8495-842961e8329a |  | textbox | Test Kit Calibration Date:
text | 83eff474-e5a8-5b41-80f9-833c4374beac |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | b0b731d1-5489-5996-9eba-7d8e21b25ab0 |  | button | Permission to Isolate Water Supply | Yes,No
label | ef0e0b12-5b82-51cf-8951-14aaacb9a430 |  | note | Device:
text | 7aef82eb-5bb9-5fa8-bfeb-1f30e6fcee64 |  | textbox | Make:
text | 4aa14cbb-058d-5566-a315-e45d3cca32ae |  | textbox | Size: |  |  | mm
text | 80ef5614-5a46-5e77-918b-d4f4e7b15aef |  | textbox | Model No.:
text | fef96cce-cc26-50d4-ab9b-087d3488afe1 |  | textbox | Serial No.:
button | 7cdf2d08-911b-5f13-994e-8b47e6583077 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 56a7345b-cade-5bbe-aec4-35949e4a1af5 |  | tickbox | Containment Protection
boolean | d14fa81f-3544-5191-94a1-3bb08b8d9f87 |  | tickbox | Individual Protection
boolean | ebccf768-ac72-5a15-a00d-9ca740f4d9b3 |  | tickbox | Zone Protection
button | b95da319-fd61-5ade-a008-27ba1f36ce03 |  | button | Strainer Installed | No,Yes
button | 34590a86-789b-5a20-8dc5-57411b0714d8 |  | button | Strainer Cleaned | No,Yes
radio | d82ff07a-a1d0-57c2-bf91-263f8a5b70da |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | c058410c-c3b4-5481-9d44-28dd0f5223b5 |  | note | Valve
text | 6072370f-4b74-5d23-9f93-10896b6bd62e |  | textbox | Check Valve 1
text | 069cfcb4-c380-586e-a3cb-597848c906d0 |  | textbox | Check Valve 2
text | 80282f6d-1839-5dcf-8529-764fa1c0d258 |  | textbox | Relief Valve
label | 6cfcc600-767c-5684-a548-1ac9dde68e4c |  | note | Testing Results
text | 1a152ae2-21fd-58c8-8469-89ad6d374db9 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 565f1615-d071-55d3-8362-cb6be39b1308 |  | tickbox | Leaked
text | 1b504855-8459-574a-b5a5-30f1d5ab0b06 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 0fae97fe-dfd8-578d-8507-e7be1ce595cf |  | tickbox | Leaked
text | 0d206ba7-8979-5c72-8de5-07a48eae8b9b |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | a4ccba59-ba42-5867-89b5-a72f4952c6be |  | tickbox | Leaked
label | 56e0c463-3dae-54cd-af31-a2e4331a4ea7 |  | note | Reason for the device failure
boolean | c845fe2d-459f-5372-9032-76c76c46ea57 |  | tickbox | Incorrect position
boolean | af213235-9404-574f-9d65-d2690a279204 |  | tickbox | Incorrect installation
boolean | dcf99d9c-a369-5684-a989-e2f98eeef1dd |  | tickbox | Foreign material in the device
boolean | db50608b-6fb5-55f6-af95-54f43e3991d5 |  | tickbox | Spring wear damage
boolean | fb038ba6-670c-51e1-946f-30cec0022319 |  | tickbox | Seal or Rubber Damage
boolean | 210d3602-93af-5dd4-a0ba-de8dfcdafd44 |  | tickbox | Other
text | 932f37ef-6cae-59f6-8b6b-e10b428e3e6e |  | textbox | Other:
label | 5ac09a38-3dec-5e78-87b3-268b9ac48641 |  | note | Test after maintenance
text | b5d8bbfe-f748-5c60-b6f9-f6c615926ebe |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | aec30b37-eadf-5d10-9a52-da3799c0d540 |  | tickbox | Leaked
text | 540c3a2b-01ca-5aef-a2b5-355cd23e7b61 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 07509632-f113-5665-a6fe-c20ddc269c47 |  | tickbox | Leaked
text | 611c6612-11db-550f-865d-9b15207a23ba |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 9931ffb5-4521-5afd-b384-ee5b3c5caf4b |  | tickbox | Leaked
button | 9fa9bbe8-2c60-5f2c-be41-724f915e35d3 |  | button | Water turned back on | Yes,No
text | 6834cc9a-25d0-55dc-a9d4-f0e7cc77e268 |  | textbox | Describe the maintenance:
text | c4c6695e-9291-5318-a93c-5651d484d5a7 |  | textbox | Parts used in repair:
button | 0e437bce-b0b4-54d9-9993-4de3d57ceba6 |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | 9184cf4a-651a-5d93-8029-fe24053aec20 |  | textbox | Tester Name:
text | 53b1515b-f2ce-5bb7-9de0-d7129747ed05 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | 4 - Roof non potable hot water units
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | 249ab8c7-545e-5e43-bda7-25ac563e1c66 |  | textbox | Project:
text | 94ba901c-7c2c-5f0a-b835-a69281400efb |  | textbox | Owner/Occupier:
text | 54463b99-d20a-552f-8ae7-7ca2958fbee9 |  | textbox | Address:
label | a7efd919-cd47-5895-a0ac-ce7424cc68e9 |  | note | Type of Test: Annual Test
text | 8f780d61-6198-5cb1-8962-01fe387bec9d |  | textbox | Location of Device:
text | c8232b34-02ae-5c86-8e1b-99992b280cdd |  | textbox | Authorized Tester Name:
text | f899b995-ad7a-5c66-a107-f4a0053c8cbc |  | textbox | Test Kit Serial No.
text | b0564c36-ae11-57d7-910b-349f227ca2c6 |  | textbox | Tester Licence No.:
text | 3a08afe6-1f30-554b-a40a-7be8a8f05327 |  | textbox | Test Kit Calibration Date:
text | b844b54e-a197-521e-84aa-8bd6c75c4168 |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | f37e817d-8423-5482-b21e-43694fd13afe |  | button | Permission to Isolate Water Supply | Yes,No
label | 86d17ade-b4f1-5339-92c6-dc3dc2d71324 |  | note | Device:
text | f4b1a572-abb1-5be4-8b3a-63e913d99751 |  | textbox | Make:
text | 8a9b9f48-d0c5-5909-b3e4-2085446f5149 |  | textbox | Size: |  |  | mm
text | c093e5fb-2b1f-52e0-b667-4a0854d8bebc |  | textbox | Model No.:
text | 07513702-7cde-5d05-aeb3-ea98f2d40b8c |  | textbox | Serial No.:
button | b5271a30-30d4-5b80-a387-a82ece1213df |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 344f0245-c787-5aff-964d-2dbb83f3046e |  | tickbox | Containment Protection
boolean | 1502ee97-1c79-5ca0-b001-b2ead2b642c2 |  | tickbox | Individual Protection
boolean | 15a729aa-8d41-53bb-84a4-91f2e4424746 |  | tickbox | Zone Protection
button | 2247615a-34da-5ed9-8772-74d180e662c5 |  | button | Strainer Installed | No,Yes
button | 4f5e249f-5f5f-5e67-b474-508addeea641 |  | button | Strainer Cleaned | No,Yes
radio | cfac48f5-3eda-58d3-9f40-b7e0c23cb749 |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 98da5795-623b-553a-963b-9a58604b38a9 |  | note | Valve
text | 0f277993-d6e0-5e80-895d-40615538281a |  | textbox | Check Valve 1
text | 9bcfb1a8-8281-59bb-ba90-c14b2722fe80 |  | textbox | Check Valve 2
text | 3e53e2f2-852d-5e9e-acd2-8f588b9102a7 |  | textbox | Relief Valve
label | 2acb39e5-fe14-587b-b742-9d7e538d8c44 |  | note | Testing Results
text | 1cede4bd-27c6-5e90-b20e-5598499ccddf |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 20f580ed-3282-5169-899a-1f9525a52284 |  | tickbox | Leaked
text | eaa52a1c-2a61-56ef-8ab7-652049008f2c |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 6b3155d5-3ffb-5555-847b-c58c23e8c53e |  | tickbox | Leaked
text | 41bce2a6-6b57-50f6-8458-61669784fca6 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 2d111126-5758-58a3-bc62-e9789cf1cd9a |  | tickbox | Leaked
label | da646e47-9d24-5cc7-b5f9-190321171d79 |  | note | Reason for the device failure
boolean | 556f4ee8-35c0-54bc-a2a7-3c1be002d83e |  | tickbox | Incorrect position
boolean | 0517aac4-e36f-59ef-8f4b-2550562780f8 |  | tickbox | Incorrect installation
boolean | 832048fc-1591-5457-9430-f2d124890cd1 |  | tickbox | Foreign material in the device
boolean | 0c891fa5-3440-51a0-8e2d-a43338bdd82d |  | tickbox | Spring wear damage
boolean | 85617785-d12f-55e7-bab4-60ed6ac5e76e |  | tickbox | Seal or Rubber Damage
boolean | 24ba7308-a0b6-5c27-8ed2-9b5826c95153 |  | tickbox | Other
text | 2affb1d3-4cad-5410-a8a2-8b1aa31b43b9 |  | textbox | Other:
label | 48a3fb5c-f706-5944-a8d7-9d3d02218f4b |  | note | Test after maintenance
text | 95abc54a-4d1a-58e3-8017-586ea3702161 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 5974cb38-f582-5dcb-bc7f-5273d857c4e2 |  | tickbox | Leaked
text | eabb5099-8a7d-5e39-8249-249bcc9f0117 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 807b96e6-db6b-52aa-8d90-085ab7db4810 |  | tickbox | Leaked
text | 3480a7d2-30cb-5f6f-9fad-b1a369dff649 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | cd2fd4de-88dd-525b-a029-4ca5f6588444 |  | tickbox | Leaked
button | a02c8060-4c56-5c48-be99-b8a0ea20bf69 |  | button | Water turned back on | Yes,No
text | 33f88775-2f5e-5e84-b847-81af9d802efd |  | textbox | Describe the maintenance:
text | c74f3980-3a4b-5c0a-9a92-332a2e57c1b6 |  | textbox | Parts used in repair:
button | e7289f6f-12d6-5db7-83d2-9c73b0c9db9e |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | 8d915acb-e48f-5372-b74a-c173a92c1aa0 |  | textbox | Tester Name:
text | eed8498c-8dac-5f2a-9da9-f8e4ab477262 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | 5 - Roof non potable lab water supply - bottom RPZD
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | 4f562ead-309a-5c4a-9872-a110419d5c71 |  | textbox | Project:
text | cbe6847e-5e4a-5e1a-b125-4ad91db8e9e1 |  | textbox | Owner/Occupier:
text | 229752d0-49fe-5a16-8611-815813bfda7b |  | textbox | Address:
label | cf119e9d-a92c-5584-957b-72d4140e1ea0 |  | note | Type of Test: Annual Test
text | 97c24612-c274-5101-b395-96e5e630ea94 |  | textbox | Location of Device:
text | 81b6f87f-5f4c-505a-82a7-a426c1729d77 |  | textbox | Authorized Tester Name:
text | b70f57c9-bb32-52c0-9a7b-204a96562fd3 |  | textbox | Test Kit Serial No.
text | 8a60d817-5eb6-5d51-881a-4230e67e5dcc |  | textbox | Tester Licence No.:
text | e8991355-3b51-5bee-9ca6-597de0ab474e |  | textbox | Test Kit Calibration Date:
text | 5f3a31fe-e06e-5770-be12-83a782a634ba |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | 5bb4923d-c98f-592a-aef3-dbfb13dfea14 |  | button | Permission to Isolate Water Supply | Yes,No
label | 18a16336-e5e8-54fa-8a72-18b4da4a34f0 |  | note | Device:
text | 95cda2dc-d650-5d90-b1cc-476e775d224c |  | textbox | Make:
text | 224a416f-c5a7-51c0-bd97-ba12bc645c06 |  | textbox | Size: |  |  | mm
text | 86e591d0-9098-54a1-9ebe-ac6f68ea1581 |  | textbox | Model No.:
text | dbb0532a-67eb-51ee-8204-531fcfb45b19 |  | textbox | Serial No.:
button | d2d6b744-1246-568f-a1b0-c62182bb3f91 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 92793b4a-bec6-500b-a12f-311f039e5fc2 |  | tickbox | Containment Protection
boolean | ef444946-03ce-5e7f-81eb-91a1b922b536 |  | tickbox | Individual Protection
boolean | 9fd4a988-c14b-5cd3-841f-95c3b2f6cd4b |  | tickbox | Zone Protection
button | 6f2eb0be-cbf4-56b8-a05c-01a71ebec0d0 |  | button | Strainer Installed | No,Yes
button | 77ec6a11-57ba-5231-b514-7801bcd2b8ac |  | button | Strainer Cleaned | No,Yes
radio | aa62c9dc-371d-5f60-8ef7-aa6234dd189c |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 001b6867-0115-5599-b534-b91fb2f6c25d |  | note | Valve
text | af9ade79-54af-5042-8141-87908c9e1859 |  | textbox | Check Valve 1
text | 35c54b2d-10d9-543c-9fc4-d8c7dd7e3517 |  | textbox | Check Valve 2
text | c7cf1a1d-d942-54a6-b5ef-63cc46f6ee4d |  | textbox | Relief Valve
label | 1ed2c8fe-97f9-5396-b0fb-c97816c09297 |  | note | Testing Results
text | 411e9458-06d2-5c7d-93de-63e3e1ac3931 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 739b472d-2142-54e9-843e-bfa90f71a483 |  | tickbox | Leaked
text | c1062d7f-d866-58aa-9bfd-6067ce955b0d |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 5b7923e9-d0c8-590a-92d6-1ee11f63cea8 |  | tickbox | Leaked
text | d07ab59e-e575-5384-b200-a6b6a9c19ccf |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | bb8a56c5-3fd3-5b31-9fcd-a26c47bad22b |  | tickbox | Leaked
label | 42d7cc9a-d380-5b49-9a24-5e428d3a456c |  | note | Reason for the device failure
boolean | a5bae680-2d35-5f84-b028-ff1a559786e9 |  | tickbox | Incorrect position
boolean | e13f2189-48fd-5ff7-95be-bf132300b478 |  | tickbox | Incorrect installation
boolean | 6f8dcdff-3c17-5c61-913b-8d28a1a1cdae |  | tickbox | Foreign material in the device
boolean | af53a184-3bfd-552a-920b-3a65ae60b0ec |  | tickbox | Spring wear damage
boolean | 8391ee19-328b-544f-8e1b-4f8c6c530f11 |  | tickbox | Seal or Rubber Damage
boolean | 1582b683-67fb-58b9-b2bb-cb51fa434a06 |  | tickbox | Other
text | 8aa0c2c4-3873-592c-8ce3-68abca343ead |  | textbox | Other:
label | 167d1973-a53c-52c0-8a57-95b6d6ab9ee1 |  | note | Test after maintenance
text | 8c32143f-4fd5-5b8e-bdf9-44e1813359ee |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | e8b06d4e-f2da-5294-bb37-455d7084130c |  | tickbox | Leaked
text | 452dcfd9-a3d3-5aa2-b8a5-978dc99d4228 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 3e26d6a1-5204-5f18-adce-9391fee06e16 |  | tickbox | Leaked
text | 350241d2-5767-5114-910e-b317bd71f663 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 132c22ef-dfa6-54f2-9e40-733a4dff96a0 |  | tickbox | Leaked
button | 74fa6f85-b6a2-56f1-b926-3db51c9ee9c1 |  | button | Water turned back on | Yes,No
text | c923b215-af5a-56e4-9bc6-6947e3fbc7d3 |  | textbox | Describe the maintenance:
text | 5ad18fd1-3809-55aa-9770-bd425e29a728 |  | textbox | Parts used in repair:
button | be0c555b-6c14-5d8f-8e56-68aaa7502bdf |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | f2159efb-c55d-539c-97dc-d5f2a5321561 |  | textbox | Tester Name:
text | f2e61809-5ab5-5195-b2b0-f9ec13bdab4a |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | Hydraulic plant room/ tanks
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | fccb3e1a-41f0-5aca-be01-d036f5f445b0 |  | textbox | Project:
text | d7912792-8dab-533f-8659-efef4a05eeaf |  | textbox | Owner/Occupier:
text | 4c6ae980-092c-59d3-aed1-d20800fba566 |  | textbox | Address:
label | a6a84d28-bcbb-5696-baf5-4b6f052b235e |  | note | Type of Test: Annual Test
text | 6013734a-d0cd-5b22-9aa5-d245be44bfb1 |  | textbox | Location of Device:
text | 1e7d1617-8ee4-5f21-be6d-72ac98894460 |  | textbox | Authorized Tester Name:
text | a0404187-bb12-58a2-a4d3-3b01b3a29dc1 |  | textbox | Test Kit Serial No.
text | 00f21630-d4ff-552e-97e2-522d4fcf7d6c |  | textbox | Tester Licence No.:
text | 471ff6bb-6a5f-5050-bd3d-0bb69bf2faac |  | textbox | Test Kit Calibration Date:
text | 7b0a3530-b9e7-57df-b743-a8f99d2bc24a |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | e0d351b3-09f6-5a1e-aeea-889f5cc9c33a |  | button | Permission to Isolate Water Supply | Yes,No
label | b561a99a-72ed-5ed3-898d-6e0d402f8867 |  | note | Device:
text | 15daa100-2744-544b-b9fb-e86c104b69d7 |  | textbox | Make:
text | 814f4263-3a87-5126-bf87-72697c59a193 |  | textbox | Size: |  |  | mm
text | 41f55493-fe39-513c-96eb-7d0445e2f2aa |  | textbox | Model No.:
text | 6da652e0-b8a9-5eb6-bf6c-47078d832e82 |  | textbox | Serial No.:
button | 4e728840-4713-5e20-bfbb-79c7eb9f6632 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | Yes,No
boolean | 7b6eb363-a131-5b18-9b62-5bf9b1bbf5b6 |  | tickbox | Containment Protection
boolean | 6c3a4479-69b0-5d18-8f75-441c6e34fadd |  | tickbox | Individual Protection
boolean | da41a99f-0035-5992-a3a1-9c0ca470b532 |  | tickbox | Zone Protection
button | 803dbdeb-d266-5779-bfe2-9810a659a1bf |  | button | Strainer Installed | No,Yes
button | 8f7411b3-673f-503d-b148-2876b49cc495 |  | button | Strainer Cleaned | No,Yes
radio | 24725e1f-b769-592b-a425-66934f4c77bd |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 9dff413f-b4ff-5379-bb32-0f11fdc26024 |  | note | Valve
text | 5ee77361-53c9-57eb-a672-1a67f2aedf5a |  | textbox | Check Valve 1
text | e4f9856b-6f75-5deb-b779-ba5b9973f05e |  | textbox | Check Valve 2
text | 848e318d-912d-544e-ac9d-9b96dc1136fa |  | textbox | Relief Valve
label | dc754793-8920-5d73-8566-106c50a07795 |  | note | Testing Results
text | 72e38bb2-69e9-50dc-b401-47feacb4b759 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 3b365a72-f409-5245-86d1-a8d3667e8450 |  | tickbox | Leaked
text | 2476154c-6ae0-5eab-86a8-8a3838ad8535 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 73333682-c45f-5e2d-8783-7f70ea8442a7 |  | tickbox | Leaked
text | 432d91f9-4255-53d9-94c8-f1533366c512 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 7f0f96ac-691c-511f-9dab-5da6372a4f06 |  | tickbox | Leaked
label | 88f4d1fe-744e-5c48-b28d-4f2d72cb010d |  | note | Reason for the device failure
boolean | f48bf328-f895-5d7c-a5a6-7bf7094ae2cb |  | tickbox | Incorrect position
boolean | 5de90503-b556-5b2d-b18c-494fdc79a0f5 |  | tickbox | Incorrect installation
boolean | 3ce2c37a-46d3-5fa7-9830-aae986b0b6d4 |  | tickbox | Foreign material in the device
boolean | 2f7dfc91-dfa9-58ee-9d14-318db821607a |  | tickbox | Spring wear damage
boolean | 2a9e61e3-80d4-579f-92e7-5f21c4e40914 |  | tickbox | Seal or Rubber Damage
boolean | 62b07417-40d2-5b21-9296-9bd038b54d8d |  | tickbox | Other
text | eeba2499-68b6-55c0-bce5-ac1f242d66ae |  | textbox | Other:
label | 97e17a34-d3c6-5025-90a2-2da7e3ec74d8 |  | note | Test after maintenance
text | 3ae7a4b4-ba43-5db4-bb30-2a720800c528 |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 1fb7ae18-6616-5f37-8912-8d81c138b4e9 |  | tickbox | Leaked
text | ffe32bc0-b648-5727-99ca-0d25e81f65a5 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 478c007c-4103-5470-8d9d-6dcdad74063b |  | tickbox | Leaked
text | 1bbd0f4a-200e-5a74-80ee-17510b3be451 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 5e38b70f-0c20-5240-9553-d939722466d9 |  | tickbox | Leaked
button | 8cf38598-f106-5340-b283-9055cdb13193 |  | button | Water turned back on | Yes,No
text | feca2ff4-8cc0-5000-bedd-9f7f70a451ec |  | textbox | Describe the maintenance:
text | 7d6f0d2f-53d2-5f8a-91cc-660099cbbfa5 |  | textbox | Parts used in repair:
button | f31dad1a-bead-5940-8789-25e1c4f68c3b |  | button | Is the device installed correctly | Yes,No
checkpoint-status |  |  | checkpoint | Test Result
text | 2d4c77dd-1473-5f48-ba63-945a4a4efe3d |  | textbox | Tester Name:
text | 64b9eaf7-dd77-527c-8056-c5cf938580f5 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checkpoint-group |  |  | section | Gas meter room
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | 39012e25-3522-55b7-906a-4c2761e1ccd7 |  | textbox | Owner/Occupier:
text | 2fd2eb5c-1e37-517b-a725-99379185d72c |  | textbox | Address:
radio | 4b82f379-729d-5223-9a26-35b2e098fd61 |  | radio | Type of Test: | Annual Test,Installation Test
text | ee59a72d-d7b7-5111-88d1-e6b0f4deaa29 |  | textbox | Location of Device:
text | 9262044b-ee71-5d7f-813b-3932906ab246 |  | textbox | Authorized Tester Name:
text | aa74a429-c985-5d4a-b3d9-24dd852a4501 |  | textbox | Test Kit Serial No.
text | d5a2e037-57c6-5a94-973c-1af924589295 |  | textbox | Tester Licence No.:
text | 8abd95d4-780c-5432-9211-4182456ad82f |  | textbox | Test Kit Calibration Date:
text | a62103b7-d20b-5b34-baca-0e25c2600bb6 |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | db66fa21-f708-5c37-bf0a-29fde894089f |  | button | Permission to Isolate Water Supply | No,Yes
label | aa1fcf92-a96b-5eef-b451-ad1b04c15dff |  | note | Device:
text | a54e98bd-c868-5fef-b73c-cd97e7ec64f0 |  | textbox | Make:
text | 0b4b0ab6-65e6-5cb0-bcd6-b38b0c7fd9a1 |  | textbox | Size: |  |  | mm
text | 55af51f2-e43b-5dd2-aa40-d8a0b52dcb2e |  | textbox | Model No.:
text | f60ff7b3-a53e-5931-b391-be72e3efc590 |  | textbox | Serial No.:
button | 64b6fc78-003d-508d-9a4c-ec83f1a5d5af |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
boolean | 6c12c435-753d-5890-a38f-3581ebbcd975 |  | tickbox | Containment Protection
boolean | 95e84c42-b05c-5732-9530-3a09077d26c1 |  | tickbox | Individual Protection
boolean | 05c9f03e-6467-5c2b-b35b-4ec468d3deb2 |  | tickbox | Zone Protection
button | 80c30bff-ae41-5b98-b1d8-a1cfe483a64d |  | button | Strainer Installed | No,Yes
button | f47035b1-f14b-5be1-b559-b9d573e4f621 |  | button | Strainer Cleaned | No,Yes
radio | 81b364c3-a16c-568b-9dbe-fe735b67de22 |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 9b90edd9-0be0-51e3-894b-50dde1d5753a |  | note | Valve
text | d99835f1-d843-5784-89d3-b7695c88eaab |  | textbox | Check Valve 1
text | 0722f3a2-e5b0-5bd4-8b5a-3f6991f36cb1 |  | textbox | Check Valve 2
text | e5fb1a23-cdf9-57bc-ac50-e2cd29f68faf |  | textbox | Relief Valve
label | bcde2400-11d2-523c-b204-0bfff8993fd6 |  | note | Testing Results
text | 068730ef-2f6e-5b8e-a7f9-1e86de36d26e |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 1d3c3c0e-95d5-5ff8-b31d-3dafcd6a96a9 |  | tickbox | Leaked
text | fefc6bb0-e59a-5323-9851-f8793202f04a |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 36367504-de49-5bcd-9d2e-77383f6e552a |  | tickbox | Leaked
text | 0cedabc2-785b-5a9a-a988-d2104b00d769 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | ea75c313-3003-5edf-9d7c-53ea1ef7a143 |  | tickbox | Leaked
label | 84cc126e-bdea-53d0-a1ff-291cc561c65c |  | note | Reason for the device failure
boolean | 776d4350-dd5c-5e9d-9f19-0c660fe83873 |  | tickbox | Incorrect position
boolean | 78b5bff4-44ff-56da-8d49-0dcaea265b6d |  | tickbox | Incorrect installation
boolean | 7338381b-4133-58fa-9fbe-90848014d6d5 |  | tickbox | Foreign material in the device
boolean | a0591444-8829-5b3f-842d-af227dea4686 |  | tickbox | Spring wear damage
boolean | 8a149142-5c13-57c3-bc0c-20167d25cb89 |  | tickbox | Seal or Rubber Damage
boolean | 89234246-34f9-5543-8bbc-17e12fb9f995 |  | tickbox | Other
text | 2ff3173d-d603-50d0-a39a-1fde40f2090a |  | textbox | Other:
label | b0948d7b-1aef-5596-abd2-33fd486406cc |  | note | Test after maintenance
text | f0756b82-d34e-5988-8c68-c5b06be1660e |  | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | ad2628cb-71cd-5166-b38c-60413004eafe |  | tickbox | Leaked
text | 4ae05525-7d20-5728-a6ef-f43cdcf5fd46 |  | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | cc214de4-6500-5593-8c45-d927de41a98e |  | tickbox | Leaked
text | e8304b01-4d03-52bc-ba33-57ac1db3f626 |  | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 48c801cb-f5fe-53a3-b969-d666ef4f75ca |  | tickbox | Leaked
button | 8138e5a3-7026-57cc-b0f0-e3c85e0715a5 |  | button | Water turned back on | No,Yes
text | 0d1e6470-04dc-51a3-a873-64daf07748c4 |  | textbox | Describe the maintenance:
text | 7599ad62-f758-5907-912d-d118e9bf30df |  | textbox | Parts used in repair:
button | ebdb2be7-8b69-585a-b07d-ebdf05398bd8 |  | button | Is the device installed correctly | No,Yes
checkpoint-status |  |  | checkpoint | Test Result
text | 860a162e-fdbb-5ef6-83fe-9dc1a8eee5c0 |  | textbox | Tester Name:
text | 71cadf0f-0e64-50f9-b08d-410cd6401383 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Boiling Water Service Maintenance Log |  |  |  |  | Yes | QA 23 - Boiling Water Service Maintenance Log | 6a5da982-4d53-4da7-a29d-76de5a622016
checkpoint-no-status |  |  | checkpoint | Boiling Water Unit Service Details
text | cdbf9859-c5e7-47f9-a298-4dd3daa017d8 |  | textbox | Purchased from:
text | 6697de86-9219-4b49-8d42-40b745aca211 |  | textbox | Make:
text | 12349b69-235e-4fd8-8e30-dd1fcfe3f2be |  | textbox | Model No.:
text | 42ab99cd-b3eb-4e4b-9ce7-e237306e2703 |  | textbox | Location:
text | eca0848e-7f67-4851-8995-a1bc0c89cbe2 |  | textbox | Room Designation:
text | 7c105185-1def-47be-b164-51228d09ae9e |  | textbox | Installed by:
text | 3d878b2c-9134-409a-b6ac-2e2190f318da |  | textbox | Installation Date:
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturer’s instructions
checkpoint-status |  |  | checkpoint | Does the installation appear in good working order.
checkpoint-status |  |  | checkpoint | Confirm all warning lights working correctly
checkpoint-status |  |  | checkpoint | Confirm filter is clean
checkpoint-status |  |  | checkpoint | Confirm Unit is Fully Operational
checkpoint-no-status |  |  | checkpoint | Commissioned By:
text | 9aa05ea6-31bc-4808-a8ab-3ede12603c90 |  | textbox | Name:
text | d0ee9cb1-d584-48e8-9e38-ea4fba358eab |  | textbox | Date:
checklist-flat |  |  | checklist | Fixture/Hydraulic Installation |  |  |  |  | Yes | QA 30 - Fixture/Hydraulic Installation | 6eac9180-13a9-476d-907a-1c1f41955295
checkpoint-status |  |  | checkpoint | What is being installed?
checkpoint-status |  |  | checkpoint | Where is this fixture being installed?
checkpoint-status |  |  | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
checkpoint-status |  |  | checkpoint | Has photos of installation been taken and uploaded?
checklist-sectioned |  |  | checklist | Maintenance Inspection Report - |  |  |  |  | Yes | Maintenance Inspection Report (Dec 2021) | 7a4d8d4d-23f3-45c0-bc74-f45f36c7936e
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Inspection Details - Pass once entered
text | 13c6b75a-0dae-4605-aebd-f22cf8b9ef34 | Hidden property width:50 | textbox | Site Name
text | e9dd538f-b767-48c5-9a68-71d372c010a6 | Hidden property width:50 | textbox | Date
text | a7efaae1-c737-4c27-b0db-1ca7d6edb060 |  | textbox | Site Address
text | 467bc035-0cb9-4f08-bcbe-468fafc94873 | Hidden property width:50 | textbox | Contact
text | 2ae19935-2064-466f-9412-f655a0b16960 | Hidden property width:50 | textbox | Contact Phone #
text | 609f01ea-7840-49f6-9f6e-516a4476d95e | Hidden property width:50 | textbox | Inspection Task Location
text | e651c5e2-9313-49e9-860e-b0140927eb67 | Hidden property width:50 | textbox | Item/Equipment to be Inspected
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturer's instructions
checkpoint-status |  |  | checkpoint | Does the item function as it was designed to
checkpoint-status |  |  | checkpoint | Is there any reports from the customer of the item not working or any issues
checkpoint-status |  |  | checkpoint | Is the item free from damage or future damage
checkpoint-status |  |  | checkpoint | Has all parts i.e strainers, sumps and pits been cleaned
checkpoint-status |  |  | checkpoint | Is there further maintenance or parts required to complete inspection
checkpoint-status |  |  | checkpoint | Photo taken and uploaded to report
checkpoint-status |  |  | checkpoint | Item left in safe working order
checkpoint-status |  |  | checkpoint | Inspection Completed
text | 4d75975b-ada0-47b0-94b1-1864704bd95c |  | textbox | Additional Comments
holdpoint |  |  | signoff | Click to Add Inspector's Signature
checklist-flat |  |  | checklist | Non-Conformance and Rectification Report |  |  |  |  | Yes | QA 9 - Non-Conformance and Rectification Report | 86e6d9a3-8e1c-4820-a5b7-7c8a7eb5c10e
checkpoint-no-status |  |  | checkpoint | Non-Conformance and Rectification Report Details:
text | 9107dfcd-8015-4d19-895f-b935c8c04451 |  | textbox | Drawing No./Rev:
text | 0602b398-54eb-484f-8296-77d007cf8108 |  | textbox | Zone or Grid:
text | 3ef53301-6f2d-472b-8cc2-caee997f4aa6 |  | textbox | Issued To:
text | 42e8adb9-6353-4b09-a75d-70039b65c287 |  | textbox | Item Not Conforming
text | ad31ee15-eec4-4a3c-949a-47ee69041ae8 |  | textbox | Reason For Non-Conformance
text | 6e640059-97cd-407a-b8b1-4b1d20bd767b |  | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
text | 2a9aa999-ec49-4e8e-8e6c-4d7fae975a00 |  | textbox | Action Required:
text | b11b22d5-e7ab-4165-be40-7c11a02bec28 |  | textbox | Date:
text | bbb709e1-afac-4941-83da-40ab1f39f47e |  | textbox | Rectification:
text | 62fd0452-a8e6-4107-94e9-7ad75131e723 |  | textbox | Date:
label | 460c7f85-ab28-4071-889d-4ad27022267c |  | note | Note: Non-conformance register to be updated
checklist-flat |  |  | checklist | TMV 12 Month Service Log (use a separate checklist for each valve) |  |  |  |  | Yes | TMV 12 Month Service Log V.040221 | 8a4e17bc-1334-4878-90a2-7d91f127552f
checkpoint-status |  |  | checkpoint | TMV 12 Month Service Log
text | 6f50691a-1052-508d-8942-49e4f9fee3e3 |  | textbox | Building name:
text | 4b152a5c-c292-5f2b-b65c-9bd875e1b6b0 |  | textbox | Contact person:
text | 9009d3d3-e172-5e90-98c6-2424962fd352 |  | textbox | Address:
text | fe012bfe-2595-5101-b131-a979e02183bb |  | textbox | Phone number:
text | 2474ad68-5cf5-5eb5-bfbd-2aa6b41ee866 |  | textbox | Make of valve:
text | b58ba77d-9724-59e0-b632-a2c01965168a |  | textbox | Model number:
text | cec86261-f94b-5a41-ac58-08fa2f04f68d |  | textbox | Valve location:
text | e0416798-48a1-5701-87e1-805195bb6fda |  | textbox | Room name:
text | 07f0cc2d-796d-535f-ad26-3220c5fe212e |  | textbox | Date of service:
text | 74dc33f9-1bd1-5c78-a8ca-969583863bd7 |  | textbox | Temperature: |  |  | °C
button | 34c78806-8271-5c24-911f-9d7ebdc7ae05 |  | button | Element: | Ok, Faulty
button | 7b702738-5414-58fe-a150-2d29a9bfc558 |  | button | O' rings: | Ok, U, S
button | 42b01cf6-fa34-54d8-8d06-354262c6949c |  | button | Strainers: | Ok, Dirty
button | 5b9b3278-8c97-5b0f-849a-0a296e4355c0 |  | button | Non-return Valves | Ok, Faulty
button | 3364de9b-9acd-5733-b0fa-6204cd3ed21b |  | button | Fail-safe test | Ok, Faulty
text | 71c93ee4-c284-55ce-99e2-9bd18f206e34 |  | textbox | Serviced by:
label | 4fd502bb-1d32-589f-b31f-cc82df6a231d |  | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
checkpoint-status |  |  | checkpoint | Completion
text | bb196e3b-d980-5044-b91f-ae492fc70d5c |  | textbox | Plumber Name:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Quality Control Pressure Test Report |  |  |  |  | Yes | QA 6 - Quality Control Pressure Test Report | 8fc65d60-14fe-4a83-ab80-05c773d4e2fc
checkpoint-no-status |  |  | checkpoint | Quality Control Pressure Test Report:
text | f0020ce6-f8c6-4c95-9cba-f8016f92d882 |  | textbox | Drawing No.:
text | f51854af-ee16-4333-8715-32776b5bacb5 |  | textbox | Rev.:
button | f6b60ee6-7e83-415d-a6dc-07bc09495c1b |  | button | Test: | Air,Water
text | 07f827a5-197f-407d-91c6-cddfa887ff47 |  | textbox | Section
text | cbbfb040-a294-4964-9508-42563b75de17 |  | textbox | From
text | 76a5da44-e4db-4a42-b36d-1f670849b152 |  | textbox | To
label | 16d0a3a1-18b2-41e7-b4b9-464db2d53f07 |  | note | Specified System Working
text | 93777ae4-ec44-4159-8089-2b7c7601064e |  | textbox | Pressure (KPA)
text | 6a49c15d-7b66-42f9-b4ab-2810d0023488 |  | textbox | Duration (HRS)
label | a91d4d7e-0107-48b5-9df5-ed900e2e0349 |  | note | Specified System Test
text | 93411b4d-32cc-4789-9f10-65a65a86cd25 |  | textbox | Pressure (KPA)
text | e6376970-3dc1-4e3f-8a6e-e9e8fda9ed00 |  | textbox | Duration (HRS)
checkpoint-no-status |  |  | checkpoint | 1st Reading
text | 6364d29d-2fa3-4ebe-a8d5-9a895bdddefa |  | textbox | Time
text | 84e1baa4-d000-4f77-a203-2900df2796ca |  | textbox | KPA
text | 61934b17-59b8-48ef-b9ef-7806d742dd13 |  | textbox | Ambient Temp
checkpoint-no-status |  |  | checkpoint | 2nd Reading
text | 9fb1063b-2d09-4e10-b808-796e230734db |  | textbox | Time
text | 5cfefba5-63fd-4495-a223-938cc87e5580 |  | textbox | KPA
text | 2deae83c-0620-470e-8561-fed4e21ada7c |  | textbox | Ambient Temp
checkpoint-status |  |  | checkpoint | Test Result - Passed?
text | 84130c1b-594a-43f5-a991-bf10adc79810 |  | textbox | Repeat
checkpoint-status |  |  | checkpoint | Sign Off
text | 0206be9c-cc17-4318-8775-62e28f4dac95 |  | textbox | Geschke Pty Ltd. Representative
text | c418e431-7211-4541-b825-ade96ac4604f |  | textbox | Others Present
text | bcfc7e84-f4d9-4559-bcf0-d4dacac48159 |  | textbox | Date of Satisfactory Completion
checklist-flat |  |  | checklist | Commissioning Test Report |  |  |  |  | Yes | QA 7 - Commissioning Test Report | 910c7048-0489-4da7-b491-30ad148b09bc
checkpoint-no-status |  |  | checkpoint | Commissioning Test Report:
text | a830f8de-e919-439a-a903-6920b0c94680 |  | textbox | Zone/Grid:
text | 0acba62d-a2a7-463a-aa47-8dccaa5d01b6 |  | textbox | Drawing No.:
text | f9769c84-d87d-4c9c-9958-84cec7f9dc17 |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
label | 8d4580d7-66c8-48cf-b130-65529520e201 |  | note | Test:
label | 62e98b7f-41ad-4c5b-b04c-26e535dd6dca |  | note | Performance Test CL 2.20
label | 595d6a21-3e31-49e0-aab1-42c7c25a0729 |  | note | Fill fixture with water remove plug
label | 8ce736ba-72ac-430a-ad70-e78eacb199ca |  | note | Test for:
label | 06b32d23-51df-42f1-9f5e-e2c12dfa2ccb |  | note | Leaks
label | d030b5bb-9dab-42cf-a3a6-ae5e1e0d3f85 |  | note | Loss of water
label | 551bb508-992b-4461-bb16-e70b688596e0 |  | note | Seal in Trap
label | f978b905-8804-466c-bbb0-abfc802f25c2 |  | note | Induce siphonage in trap of adjacent fixture
label | c0cceb51-7607-4657-b464-c1163217ac84 |  | note | Complete draining of fixture
text | ae77feca-b28f-4a87-bae4-4f63bc69fcc6 |  | textbox | OK:
text | 9243e690-52cd-4cbc-a1b0-2b432c9a5440 |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Item: Water Supply
label | 97a178c6-294c-47d6-88e9-d29e71e519dd |  | note | Test:
label | 0225e636-801d-4b38-8ab4-f461ba3b9fd4 |  | note | Performance Test CL 2.20
label | 318a0e36-837a-4e86-a457-0a95ad6b2ddf |  | note | Check for adequate water volume.
label | 1be7f4cd-4680-49d2-b196-0d763b5b6f59 |  | note | Flush out pipework
label | 87cad9ba-ce88-49ea-b6f0-9357dcdbd11c |  | note | Clean aerator
label | ff6a6905-2dd3-491a-8d56-2bc13d78d8b8 |  | note | Water hammer
text | 154109ae-8a0f-4d25-9cac-a1f4cf8b18d4 |  | textbox | OK:
text | 96b7b6cc-321e-4722-ad67-e88f62a528ff |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Item: Flush Performance
label | 2aa76092-abe7-49de-a3e5-2a38f6b3467a |  | note | Test:
label | 96ce5ee4-9f78-436b-b58a-c6c32b7efe34 |  | note | Performance Test
label | b95e73d6-67d6-4cef-b2a2-5eb817ab2ac1 |  | note | Check for:
label | 1b03f238-2adb-41ef-bd34-b8288e57cd2f |  | note | Water Volume
label | aecdedbd-53b8-48cf-bdee-5464fc8fd3da |  | note | Duration of flush
label | c3f3cf9c-56d4-4931-8b32-515b0312bd84 |  | note | Flush out pipework
label | 572f64a8-d3d4-413a-b2b1-719de1a6ceff |  | note | Water hammer
text | b21979b9-d24d-417e-a499-610b8dfdc10b |  | textbox | OK:
text | 7d5daaa4-bab3-4a89-834c-886c1374552d |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Other
checklist-flat |  |  | checklist | QA 14 - Thermostatic Mixing Valves Commissioning Log Sheet |  |  |  |  | Yes | QA 14 - Thermostatic Mixing Valves Commissioning Log Sheet - MHTP | 965e71ef-8052-458b-ab2d-608bf9e33896
checkpoint-no-status |  |  | checkpoint | Thermostatic Mixing Valves Commissioning Log Sheet:
text | c706257b-80dc-4706-8686-5b40d1eceb30 | Hidden property value:MHTP – Hudson Institute | textbox | Project:
text | 0017eb1c-152d-4fd9-ad06-79fbe404548b |  | textbox | Date:
text | 5f4f3134-e247-4cf6-a4d1-26e48569a571 | Hidden property value:Preventative Maintenance – Hydraulics MHTP | textbox | Contract:
text | 0d797585-e13f-4247-88aa-4b55b1a5e9bf | Hidden property value:45 Kanooka Grove, Clayton | textbox | Address:
text | 07db8739-b368-4c9b-9d8b-c3483f46d3b6 | Hidden property value:Steve Bouralexis | textbox | Contact:
text | a5150914-7d20-4b63-baaa-617e0449b0e6 | Hidden property value:0419 810 008 | textbox | Phone:
checkpoint-no-status |  |  | checkpoint | Valve Details
text | 9e8f600c-15c1-4816-87e1-72db49993f20 | Hidden property value:Bentons Plumbtec Suppliers | textbox | Purchased from:
text | 83bda13f-bf82-4bce-87bf-7631a2eb344e |  | textbox | Make:
text | 11c94b31-580b-40bc-bbff-ecdaa005bb7e |  | textbox | Model No:
text | 94632e92-0e43-4c64-80fd-0348bb26ed4e |  | textbox | Location:
text | ca1c4ce6-8534-4e41-a2c2-3e99f73d8349 |  | textbox | Room Designation:
text | d34d391b-b325-40b8-9c95-11e0d6d96cd9 | Hidden property value:Geschke Plumbing | textbox | Installed by:
text | 044c5ccd-6f53-40e5-b1ab-c52bc0532679 |  | textbox | Installation Date:
text | e8ce5322-01f8-4586-871f-839e97b7e130 |  | textbox | Number of outlets served: (eg. baths, showers, basins)
text | 64731977-0d3f-46e7-b7a1-1875fda9eb59 |  | textbox | Prescribed temperature range for associated warm water: |  |  | degrees C
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturer’s instructions?
checkpoint-status |  |  | checkpoint | Does installation comply with current requirements of the local water supply authority.
checkpoint-status |  |  | checkpoint | Water Temperature Tested
text | 30571207-c25c-4835-89b5-21e5ae584341 |  | textbox | Temperature of hot water supply |  |  | °C
text | fe417f53-e503-4362-8af5-423d776b1610 |  | textbox | Temperature of cold water supply |  |  | °C
text | 8b2f3c39-ad55-4828-9b8c-3ddfb6b32425 |  | textbox | Temperature of warm water supply |  |  | °C
checkpoint-status |  |  | checkpoint | Dynamic Pressure Tested
text | 21b6eabf-5bf2-41fb-999f-d3494b77c8aa |  | textbox | Dynamic pressure of hot water |  |  | KPA
text | 245a2733-90e7-432e-bdf6-828d6569090b |  | textbox | Dynamic pressure of cold water |  |  | KPA
checkpoint-status |  |  | checkpoint | Check Fail Safe Operation (Hot water at least 20°C above warm water)
checkpoint-status |  |  | checkpoint | Commissioned
text | bcc550bd-b2ce-45f9-a5ea-9de23435871f |  | textbox | By Whom:
text | 11235455-5758-4aaf-85ae-bee27c5bd1b2 |  | textbox | Date:
checklist-flat |  |  | checklist | QA 18 - Gasket Installation |  |  |  |  | Yes | QA 18 - Gasket Installation | adf3440f-ad3b-4d8c-a3f8-237557c339ee
checkpoint-status |  |  | checkpoint | Gasket Installtion:
text | 430efedc-dd9c-4236-aead-e337af7f44ba |  | textbox | Location/Identification:
text | ae93b69f-f96e-45fd-b8aa-6a4798799033 |  | textbox | Nominal Bolt Size:
text | e1743935-4673-4690-a3ba-31923cf4972e |  | textbox | Gasket Contact Surface Finish on Flange:
text | fdb76cc3-37bb-4fb1-95bd-3db46865da8d |  | textbox | Lubricant used:
label | b9b2bb68-8d71-45e2-9dd7-fced4283079f |  | note | 1. Galvanised nuts and bolts – must use good quality lubricating oil on threads
label | fb480488-23e0-4b19-8c1b-73d5e72d4bb9 |  | note | 2. Below Ground Galvanised nuts and bolts– must denzo and plastic wrap full flange and cover bolts
label | 7799041d-5634-4591-99ca-ed37700b95e7 |  | note | 3. Stainless steel nuts and bolts – must use anti seize / molybond on threads – must return 24 hrs later to tighten in sequence and required torque
label | fd9896a6-0f72-4ef0-985c-4682b6041abf |  | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
label | 2bd1c31f-5a4c-4b2e-8a27-668a59ad93f8 |  | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
label | 23214540-a965-4269-acfb-32239a78b70b |  | note | 6. Zinc bolts, nuts and washers rust when used externally – use galvanised
checkpoint-status |  |  | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
checkpoint-status |  |  | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
checkpoint-status |  |  | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
checkpoint-status |  |  | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
checkpoint-status |  |  | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier – seek from GPL foreman
checkpoint-status |  |  | checkpoint | Check gap for uniformity.
checkpoint-status |  |  | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a “Round”)
checkpoint-status |  |  | checkpoint | Final Torque
text | 123f3bdd-2886-4664-bf4a-7f558d44d00a |  | textbox | Final torque*: |  | (Nm)
label | 18671f02-f1c0-4e99-a5af-027938efa57c |  | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
label | 5b49e326-d25e-4b49-9e96-a55caec9644f |  | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
text | 4c06d229-bcb4-4059-aa54-94eb302e6a01 |  | textbox | Round 1 – Tighten to: |  | (Nm) | 1st torque value in torque chart* (20% of final torque)
text | 2614a5d8-f14e-4335-9c5d-3fa72aa0f634 |  | textbox | Round 2 – Tighten to: |  | (Nm) | 2nd torque value in torque chart* (50% of final torque)
text | 13681d5e-a954-4727-a3cc-ff3f9a8c1d96 |  | textbox | Round 3 – Tighten to: |  | (Nm) | 3rd torque value in torque chart* (75% of final torque)
label | 7c31052f-1707-4cd0-b6b2-39efc2ef0e5b |  | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
label | f0838d4b-d4a6-4ae8-8b6c-8f8962b87b64 |  | note | Final Rotational Round – 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
label | b6feb547-4af0-447f-bdad-8aebd0ba3a7a |  | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
select | abd159a8-7e40-411e-9da2-9b295a92fc12 |  | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
text | 9a8f7400-7a6e-45fe-80c5-3b92c67858d4 |  | textbox | Other:
text | 48411f23-53f6-4d8e-8b6a-c2b4b4374a76 |  | textbox | Where was torque information provided from:
text | 0667cc04-8cbe-4257-9d04-05cd7cae565e |  | textbox | Joint Assembler Name:
holdpoint |  |  | signoff | Joint Assembler Signature
checklist-flat |  |  | checklist | Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  |  |  |  | Yes | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) | ae84ec28-3d70-45bd-a3e4-8aa7c689a83b
checkpoint-status |  |  | checkpoint | Installation Test Sheet:
text | 1f7548c7-5d87-4a04-93c5-e847e3a808a6 |  | textbox | Drawing No.:
text | 8bd7d34e-287c-4f30-9271-af09ba403454 |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | PIPE CLIP HANGERS
text | a3cbb802-7bab-4c84-8f2d-7820f06ae0a7 |  | textbox | Details:
text | ad3f7f0d-a464-4cd5-abdd-261b922a7db4 |  | textbox | Tester:
text | 78a487fc-6f15-4a56-98cf-aec42ae4d87e |  | textbox | Date:
text | c8580cc9-5067-48a3-a564-d25d219fd09f |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | MATERIAL AND SIZE
text | 6275b31d-456f-4c62-854c-9c81017ad908 |  | textbox | Details:
text | 496a52bb-c521-4346-b17a-e07cd100b363 |  | textbox | Tester:
text | 3aed5fd2-9130-4044-9b28-6eed7eef219f |  | textbox | Date:
text | e05f2c90-e7f9-44c8-a88a-83894925b9bb |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | ALIGNMENT
text | e3557446-edb8-4b35-8240-493eee8f72fd |  | textbox | Details:
text | 19e0c19b-8d58-45ae-b2e7-352b7d5ff1a2 |  | textbox | Tester:
text | c6fc59c1-6fdd-437e-9209-8e5d140e1ff4 |  | textbox | Date:
text | 8e09d774-b6c3-4e7a-a010-bfe9161cf1ed |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | LABELLING AND IDENTIFICATION
text | e72fbace-1f83-414a-ad19-9bc8194c6582 |  | textbox | Details:
text | 498b7a52-6206-4f6b-a50c-b43a8150ab93 |  | textbox | Tester:
text | 7c803dbb-6d03-428f-be21-eb3221260230 |  | textbox | Date:
text | 4ce89a29-d4bc-452b-9e9f-228386e40866 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | JOINTING
text | 5fcacd4e-9813-4597-99fd-29500cb6bf49 |  | textbox | Details:
text | 88bd517f-7111-4655-8b99-f1abecd867f7 |  | textbox | Tester:
text | b8f07ae3-1392-4eb5-b81a-9c36c25b0957 |  | textbox | Date:
text | 1fed5425-0a58-4b76-9046-2092ed71e26d |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PENETRATION SEALING
text | b4787143-e689-4453-8882-62df8c53b4bd |  | textbox | Details:
text | 537088ff-9926-4c43-be9d-da2dcf12da27 |  | textbox | Tester:
text | ff779dba-8b05-4fe4-ad32-0bb7383337bb |  | textbox | Date:
text | b875589d-abbf-4ed2-8548-0ce36b3c8d0f |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | FIRE STOP COLLARS
text | 05cc8ae4-86e3-4ce8-9686-5e7b19c0ff84 |  | textbox | Details:
text | 2f14f3d2-f6fd-4efa-b093-821628a6bf3f |  | textbox | Tester:
text | 30b2e673-34a6-419c-abf1-00f6ecd6de1d |  | textbox | Date:
text | d17f69a5-c2f7-4d64-a368-2886869742a4 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PRESSURE TESTING COMPLTED (QA6)
text | 5eac9eae-4862-4baf-9679-308a8ba60982 |  | textbox | Details:
text | d276ba2f-f51b-49a9-bcbd-a29766e4994e |  | textbox | Tester:
text | f2ef7cb8-b573-40a0-b8b5-d292d3758ec7 |  | textbox | Date:
text | 53d81ed9-6600-41cc-babf-a56ea05ee1e8 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AUTHORITY INSPECTION (if applicable)
text | ef7ae029-6ebf-4fe3-ab1b-87dd797e6e4c |  | textbox | Details:
text | 4a6b5e0b-7343-42a2-851d-a440b1ff3a54 |  | textbox | Tester:
text | 2c2eaae7-edbe-419d-9f23-0dbb3a06b2d2 |  | textbox | Date:
text | 60eb4fad-e40f-48f8-9180-39878e5edabc |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
text | b94ccee7-dd3f-46d4-8179-8f4018a6ebd2 |  | textbox | Details:
text | 4cfb2300-83f1-4f37-8933-d74e640c5604 |  | textbox | Tester:
text | c1060386-3a26-4c29-b2f5-420b05c4d218 |  | textbox | Date:
text | b6bf2ff6-2d67-4143-95ea-9c96cf67f595 |  | textbox | Notes:
checklist-flat |  |  | checklist | Backflow Prevention Device Test Report |  |  |  |  | Yes | QA 13 - Backflow Prevention Device Test Report | b2650a6c-2053-43c2-8712-31c9a2d6ad00
checkpoint-no-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | f410d39b-ad24-4bdd-ba7c-01553f0ef997 |  | textbox | Owner/Occupier:
text | 6a4073ca-3457-4e32-a420-fdad9878523e |  | textbox | Address:
label | d1de0fc3-3017-48bb-9e43-592dd9865336 |  | note | Licence: 50043
radio | 6d5cb041-d49d-44b2-bbae-5cce5376dbe0 |  | radio | Type of Test: | Annual Test,Installation Test
text | ef6fa439-fc69-4472-b1ea-4aeb218411e5 |  | textbox | Location of Device:
text | 99b3eafa-279b-471d-9a23-6cf6a3472fdf |  | textbox | Authorized Tester Name:
text | 4349cb90-8421-4436-a763-3a2add813133 |  | textbox | Test Kit Serial No.
text | b09805ac-531a-4936-ad58-c3ba96c30fb9 |  | textbox | Tester Licence No.:
text | 925f9e0e-f441-4156-8843-4062e169f58e |  | textbox | Test Kit Calibration Date:
text | d206f6d9-d8ae-4284-9b9b-3745e22fd8cd |  | textbox | Date of Test:
checkpoint-no-status |  |  | checkpoint | Device Details and Test Results
button | 72f150a8-e37e-4852-8a8c-6ba61ff01c89 |  | button | Permission to Isolate Water Supply | No,Yes
label | d59645b6-d3e6-46f3-9afb-a512e096106c |  | note | Device:
text | 65e31627-f74c-43ef-a6e3-6f69144e96ee |  | textbox | Make:
text | 97daca2d-70d9-40ea-8dcb-f07897026cf4 |  | textbox | Size: |  |  | mm
text | ce21fff7-9326-4e34-af99-daec8296c3ea |  | textbox | Model No.:
text | 0525f8ec-1b02-444b-8cdf-cee8bd77a81b |  | textbox | Serial No.:
button | d70590ca-e754-4c6a-84e8-5c238d625365 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
boolean | 73ea10e4-06c6-47e0-ab58-f5a69bb9fb27 |  | tickbox | Containment Protection
boolean | 52db5c72-b31b-4285-8d87-f6ca610723e0 |  | tickbox | Individual Protection
boolean | c7707c0f-22f5-4385-a3e2-1e6263bab7fd |  | tickbox | Zone Protection
button | f785e82d-e93b-4d1a-94f6-318eb74844ad |  | button | Strainer Installed | No,Yes
button | 702de382-efc6-484c-90fe-7a012fd08c9e |  | button | Strainer Cleaned | No,Yes
radio | 5919347b-701b-4574-99bb-7759cafbfc54 |  | radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
label | 816bdd13-012b-4d96-b968-06a29064fa4d |  | note | Valve
text | 8f81d0c2-9cb6-4aec-af8b-60197d1e4cee |  | textbox | Check Valve 1
text | 45d44b8d-e5a4-4335-a45e-259317de5c54 |  | textbox | Check Valve 2
text | bd86a83a-c2a2-44dd-bc6a-56634aad4e56 |  | textbox | Relief Valve
label | 03eab4e9-3ebf-42f9-8196-5dfa18172e3f |  | note | Testing Results
text | 34d01901-54fb-40af-8fc2-9450a2ae3465 | Hidden property width:25 | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 55755879-a681-417c-9d19-8ed86125fe19 |  | tickbox | Leaked
text | 0d69dbc2-8915-4b3a-9c0c-8a028500d665 | Hidden property width:25 | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 24a70e8d-6bfe-4d77-a555-85088600d6c8 |  | tickbox | Leaked
text | 7723f5ae-d2f0-417b-aa7f-ea7d2d37189e | Hidden property width:25 | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | 23b765f7-956f-4425-98b6-9f7e6fb0a8dd |  | tickbox | Leaked
label | d0d4a1bf-baf8-41d9-bd93-86b6b29d2be3 |  | note | Reason for the device failure
boolean | 09e45f43-b6ea-4cbc-9032-3eb1a54693d7 |  | tickbox | Incorrect position
boolean | d72c8c4a-adc7-448b-aead-d29c3e2f4ffb |  | tickbox | Incorrect installation
boolean | 6bef8833-8521-4cd3-83e3-962ea4f7c231 |  | tickbox | Foreign material in the device
boolean | d438e234-a68b-4326-b1e7-0f2d76e23d0a |  | tickbox | Spring wear damage
boolean | 773e3323-7c74-4186-8a83-08e159968cea |  | tickbox | Seal or Rubber Damage
boolean | 9f0f8229-7f40-4c70-bd22-e3f6b6810de1 |  | tickbox | Other
text | ff097791-84ea-41e5-8831-c04c7cbf4f2c | Hidden property width:50 | textbox | Other:
label | 1fb8e4d0-2f30-417e-b0be-e43b10418c02 |  | note | Test after maintenance
text | f03ca57e-90d2-4a98-8074-e62620da4154 | Hidden property width:25 | textbox | Close tight at: |  |  | kpa (min 35kpa)
boolean | 1a053029-2602-4290-a1f7-bc8e40f09a68 |  | tickbox | Leaked
text | f8859869-9edc-4f7f-b518-b6d4c7bac614 | Hidden property width:25 | textbox | Close tight at: |  |  | kpa (min 7kpa)
boolean | 39d096fa-3fa1-40e5-a496-5408d1cfa378 |  | tickbox | Leaked
text | 33d91e54-39ca-41ea-ab19-9f8eebc38540 | Hidden property width:25 | textbox | Opened at: |  |  | kpa (min 14kpa)
boolean | f84a97ab-a2f5-4260-baa0-a76e8010a4db |  | tickbox | Leaked
button | 9efa7747-8117-4d23-96d8-36675568233e |  | button | Water turned back on | No,Yes
text | 8911480b-a85c-4177-9781-a3bcec45d7e7 |  | textbox | Describe the maintenance:
text | a5f490d7-0d1c-40e3-a568-d79eacab1e75 |  | textbox | Parts used in repair:
button | 2059a641-b5c0-4141-a661-54b3dc48405f |  | button | Is the device installed correctly | No,Yes
checkpoint-status |  |  | checkpoint | Test Result
text | 1d68c866-481e-4854-8933-dd0a658b8a5b |  | textbox | Tester Name:
text | 40356a55-2557-47ec-89e9-5ac9499550cf |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Water |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Water | b811a74a-2e99-4cd7-af79-36946844d1fe
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | 759146f7-d052-4dc9-a78b-90a6a6a0bce4 |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | a6cd316a-a4a1-4d39-ae46-f710c8bd144d |  | note | Spec#: AS3500
label | 6b66e455-efaf-41cd-be88-104d66e14c9d |  | note | MDPE SDR11 PE100 PN16
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | c85c9a9e-57c8-4ce9-9fca-c9f30e6a8cb2 |  | note | Spec#: AS3500
label | a607b76a-ce5a-4632-9a43-e70f34c492c8 |  | note | Packing sand encased pipe
checkpoint-status |  |  | checkpoint | Jointing of pipes
label | 4c7826b1-e8b7-4f1f-9542-7a373a47259f |  | note | Electrofusion and/or Butt Welds
label | c91132b9-771c-4c0b-97f2-e345898ea7b7 |  | note | GPLQA16 form
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
label | cf52bb20-9c57-4d8b-bb3f-d161620f63ee |  | note | GPL QA6 form completed
label | 058c9336-61bb-4f8a-9c97-17d1fb85aa50 |  | note | Water system tested to 1400 kpa regularly prior to finished surfaces are completed.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 88be9585-5ffe-443c-ad16-492ae061f75a |  | note | Compacted crushed rock backfill 80% to 100% compaction
label | 87ea8b3c-7126-4b31-bdb0-011b09a5cb12 |  | note | Detectable marker tape
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | 4b8ade35-eb43-4980-87cf-ac27e76d4c07 |  | note | Ongoing
label | be0eb3d1-26b3-4a2a-993d-cc4d917bfde4 |  | note | To be provided
checklist-flat |  |  | checklist | TMV Commissioning Log Sheet |  |  |  |  | Yes | TMV Commissioning Log Sheet | c897f6ec-28e2-4070-b995-6fcf864d10dc
checkpoint-no-status |  |  | checkpoint | TMV Commissioning Log Sheet:
text | 15b418f0-1b3b-401e-ba8e-e18fae7d8106 |  | textbox | Building Name:
text | e1d1b25a-d5ba-47c8-b68a-c56300991c6b |  | textbox | Contact Person:
text | 7c1582ed-575b-4087-bb04-f61f987f7ad8 |  | textbox | Address:
text | 722b1592-1d6b-4d9a-98ab-07c6fcf1218d | Hidden property value:50043 | textbox | Lic:
text | e650d50f-5f54-4f9e-8bac-fd15d15f9dcc |  | textbox | Registration number:
text | c85e7ee9-7b7b-4449-99b9-ba3be8605655 |  | textbox | Phone number:
text | 393798d2-5441-4376-a770-419b2780bc38 |  | textbox | Make of valve:
text | aa7e7706-18c1-40b8-92bd-8084d952e380 |  | textbox | Model number:
text | 4cb27e12-fa66-4aa8-9f3b-411200d077bc |  | textbox | Valve location:
text | ad09c704-5a39-4f16-9686-d05f54fe5f50 |  | textbox | Room name:
text | 2b8393cd-8f88-4c9f-abad-00f9398a1226 |  | textbox | Valve purchased from:
text | 36c9de8e-2782-42a4-abcc-6de06a4874fe |  | textbox | Installation date:
text | e31fe524-a228-4234-abe2-1183014454a0 |  | textbox | Valve installed by:
text | 42d231e7-230d-4bd1-ace8-113ccf65b588 |  | textbox | Number of outlets served - Baths:
text | 881ae3e9-f1f9-415e-ad3b-9fbb35220bc0 |  | textbox | Number of outlets served - Basins:
text | 0a184dba-eb66-4080-b73c-fd6704399b43 |  | textbox | Number of outlets served - Showers:
text | a1cb3b78-8383-45f7-ab2b-9e53354c6918 |  | textbox | Total number of mixing valves on site:
button | 081a586d-6861-4499-b571-7c079c97fa21 |  | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
button | e345ca02-a825-4e17-ad67-50fe1021ec43 |  | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
text | 68222715-5a31-42b2-aa4b-5e1ec1e92136 |  | textbox | Temperature of hot water supply? |  |  | °C
text | 10132879-7f9c-48a6-9b5e-86166907aeae |  | textbox | Temperature of cold water supply? |  |  | °C
text | c88000d0-b3ff-4b4e-ba74-b60073cc1c25 |  | textbox | Temperature of warm water delivery at outlet fitting? |  |  | °C
text | 67b204c5-1a84-4737-b5c3-c2c05209e79b |  | textbox | Dynamic pressure of hot water: |  |  | kPa
text | 2dd9c946-3343-4be6-aea0-7ec355fbac6d |  | textbox | Dynamic pressure of cold water: |  |  | kPa
checkpoint-status |  |  | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
checkpoint-status |  |  | checkpoint | Commissioned by
text | 7d93333d-e1b2-497a-b7a5-c51ff5d87b41 |  | textbox | Commissioned by:
text | c293ca9b-9246-4ff2-a0c2-6fea544cd458 | Hidden property value:Geschke Pty Ltd | textbox | Company name:
checklist-flat |  |  | checklist | Quality Control Flow Test and Compliance Report - Safety Showers |  |  |  |  | Yes | QA 6C - Quality Control Flow Test and Compliance Report - Safety Showers | cfb15047-b97d-46bc-b43f-e518e8bd4400
checkpoint-no-status |  |  | checkpoint | Quality Control Flow Test and Compliance Report - Safety Showers:
text | b14d1049-af08-41a2-98c9-9c62629f50d0 |  | textbox | Drawing nos/rev:
text | 008c58eb-8168-4bf0-84bc-51a18cebf7e0 |  | textbox | Appliance Tested:
text | f3677c28-0774-463d-b112-49b79bbf1f9b |  | textbox | Room No.:
checkpoint-status |  |  | checkpoint | Specified System Working
text | c849cfcd-b7d0-4a01-9543-477a7ba859a5 |  | textbox | Pressure: |  |  | KPA
text | 71416316-3068-4987-beea-bf90ade28599 |  | textbox | Flow Rate: |  |  | LPS
checkpoint-status |  |  | checkpoint | International Standard ANSI Z358.1 2004
text | 58e2bbc7-7619-46e8-b611-d11a0c856414 |  | textbox | Pressure: |  |  | KPA
text | 7564516f-8345-4962-85b4-75dc5a25d5fb |  | textbox | Flow Rate: |  |  | LPS
checkpoint-status |  |  | checkpoint | Pipe Installed
text | e5acad32-0a4f-45ba-85de-90c38b383177 |  | textbox | Pressure set on each floor: KPA
text | 0216e034-6f71-45ce-a37c-e21ecbe42627 | Hidden property width:50 | textbox | Cold - Size: |  |  | mm
text | cc6952a2-37f9-4dec-a628-ce1fb7b86eda | Hidden property width:50 | textbox | Capable Flow Rate: |  |  | LPS
text | 8bd4e67c-43d3-4133-91ec-46c1ea616e03 | Hidden property width:50 | textbox | Hot - Size: |  |  | mm
text | 9e55d907-d068-4c81-bfd6-d3bc80325a27 | Hidden property width:50 | textbox | Capable Flow Rate: |  |  | LPS
checkpoint-status |  |  | checkpoint | TMV Installed
text | f315c819-2965-4b09-82c0-39f52938c450 |  | textbox | Brand:
text | f4516f85-2047-4dc4-a502-0b42f31825c4 |  | textbox | Model:
text | b32fb06f-1976-4dbd-83eb-a54ea4317d5f |  | textbox | Flow Rate: |  |  | LPS
text | 4e8280f8-235f-4f7f-9ae1-c9504a266412 |  | textbox | Temp Set:
checkpoint-status |  |  | checkpoint | Pull Lever Confirm Flow
checkpoint-status |  |  | checkpoint | Riser Valves Open
checkpoint-status |  |  | checkpoint | Safety Shower Valve Open
checkpoint-status |  |  | checkpoint | Drain Outlet not Obstructed
checkpoint-status |  |  | checkpoint | Temperature Test
label | 5d44111d-3764-4d03-bf3f-b14190141042 |  | note | Disconnect shower head, connect hose and extend to drain, turn on shower, test temperature.
text | f5dc0a0a-24aa-4583-a1b7-5c340d0accd1 |  | textbox | Temperature: |  |  | deg C
checkpoint-status |  |  | checkpoint | Sign Off
text | a0fe32eb-8c42-42c6-a154-e50282f0c03f |  | textbox | Name - Geschke Pty Ltd Representative
text | 5103a93b-fb92-4af1-a9da-3693a04bab4a |  | textbox | Others Present
text | 52a3b00a-ee62-4309-bb6c-c1c3a44e8bfc |  | textbox | Date of Completion of Satisfactory Test
checklist-flat |  |  | checklist | Fire Penetration: |  |  |  |  | Yes | Add Fire Penetration Checklist | d98fc64b-1ad3-4d7f-8b2a-2568c35ca7e0
checkpoint-no-status |  |  | checkpoint | Treatment Type
select | da624f9e-3af9-4c6b-a1e2-5cad93dbf255 |  | dropdown | Treatment Type: | A1,A2,B,C,D,E,F,G,H1,H2,H3,J,K,M,N1,N2,O,P,Q,R,S,T,V
checkpoint-status |  |  | checkpoint | Photo of penetration and sticker must be taken
text | 87ec71e4-9233-4b93-8c07-219f4611a91e |  | textbox | Installed by:
text | a635ba49-3f67-4ee1-8ff7-3375f17de5a1 |  | textbox | Comments / Reasons why cannot complete:
checklist-flat |  |  | checklist | Fire Hose Reel (FHR) Test Report |  |  |  |  | Yes | QA 20 - Fire Hose Reel (FHR) Test Report | e419d222-ac3e-4ef1-a9a5-0df2c2bc6e17
checkpoint-no-status |  |  | checkpoint | Fire Hose Reel (FHR) Test Report:
text | 341c268c-ae3b-468f-a835-2eb38496ab79 |  | textbox | Location of FHR:
text | ab3ea171-6fb8-4126-8055-0067ca4dd083 |  | textbox | ID Number of FHR (If applicable):
text | 84838fcf-b48c-46a5-8708-e042669ae935 |  | textbox | Manufacturer:
text | 6ad6be36-3e6d-4f04-973e-6f0a1159cacb |  | textbox | Model:
text | 3745c5fe-ca29-42c8-be81-26d7d6bf0699 |  | textbox | Size:
label | 4ee0c848-82f6-4035-b4fd-1512ecf95dd1 |  | note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
radio | 617e4c9c-8d89-4598-a932-596836625a11 |  | radio | Measurement Apparatus: | Bucket
text | 66f84fbd-9c11-46b5-ab8f-863f9b0d8e5c |  | textbox | Bucket Size:
label | 0a870b20-7ea4-40a4-a54f-c7415a142993 |  | note | Measurement Method:
label | 8307d075-2ad2-4dff-adb0-68ac4108242e |  | note | 1. Connect pressure gauge and outlet to end of hose
label | f5b92eee-5a93-4cf2-ac6a-1d29eaebd9b0 |  | note | 2. Note static pressure reading on gauge
label | 9da32103-6e66-4af3-a39e-a07eafbcccf5 |  | note | 3. Place bucket at outlet of FHR and fill
checkpoint-status |  |  | checkpoint | Reading
label | 36e52097-39cc-435b-875a-a879819a5f35 |  | note | 3.3L
text | f0f1abb1-d55b-4cc6-b910-018a93ffbf12 |  | textbox | TIME (sec)
text | f775af7d-6e2f-4523-8cd9-0e14f45efb14 |  | textbox | Flow Pressure:
label | a27a1ccd-3253-46bc-96cd-508a1f398a5f |  | note | 6.6L
text | bbf85e44-216b-4b77-bce3-d2ea3c697aad |  | textbox | TIME (sec)
text | 626f87d9-1cbf-4dbc-85b4-365758ef2ab5 |  | textbox | Flow Pressure:
label | 6196dc09-ef3f-4866-adab-bd5499d77969 |  | note | 9.9L
text | 16125d35-1bec-4866-a386-19513857f966 |  | textbox | TIME (sec)
text | 0df2c75b-9782-4c39-88e0-505858a04814 |  | textbox | Flow Pressure:
checkpoint-no-status |  |  | checkpoint | Completion
text | 8524e16d-bfb0-48d3-b177-fef946cd0e98 |  | textbox | Geschke Pty Ltd. Representative:
text | 36c46586-0dc6-497d-96e3-3f218ae046b4 |  | textbox | Others Present:
text | 66f43fa5-a2b9-4798-b298-2caa5c3bf32e |  | textbox | Date of Completion of Satisfactory Test:
checklist-flat |  |  | checklist | TMV 12 Month Service Log (use a separate checklist for each valve) |  |  |  |  | Yes | zSYS - TMV 12 Month Service Log (old version) | ed4a811c-4f4d-49b7-97b6-8c87be1d78e4
checkpoint-status |  |  | checkpoint | TMV 12 Month Service Log
text | 8b2c1381-80ce-4eee-bfaa-c4b55a0262a0 |  | textbox | Building name:
text | d60bdd63-bf64-43af-a715-3315bfdd92a9 |  | textbox | Contact person:
text | f3dff51d-6ad6-4a3b-aba3-7fc8f2ad2a26 |  | textbox | Address:
text | c3780028-cee4-4279-9912-a0059e44b11f |  | textbox | Phone number:
text | b2da72e4-9887-44bb-a88a-7ce62d9955f7 |  | textbox | Make of valve:
text | a8047f35-e8ea-4c21-9778-1b4590085513 |  | textbox | Model number:
text | ec4421ab-5ffc-44ae-a745-8c7f692ddfc9 |  | textbox | Valve location:
text | e36d135f-eddd-4b62-bcb9-3e304cf602b2 |  | textbox | Room name:
text | 36a212da-e0c3-4bbb-820e-a7f833d412b2 |  | textbox | Date of service:
button | 7d537217-b029-4284-ad59-5b90e03748cf |  | button | Element: | Ok, Faulty
button | f3821a49-39b9-47ff-ac80-565acc8be263 |  | button | O' rings: | Ok, U, S
button | 75edbba2-e427-4136-aeb2-3bb2512db76b |  | button | Strainers: | Ok, Dirty
button | bceaa093-588b-45d5-823c-99e4d2745486 |  | button | Non-return Valves | Ok, Faulty
button | 5e4168b4-a94b-48c6-ad62-bc8e815c8dc0 |  | button | Fail-safe test | Ok, Faulty
text | 02d9558d-c406-4e41-abb3-32849142da3b |  | textbox | Serviced by:
label | 6f5d8efd-1714-4f04-8369-00ad8187f872 |  | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
checkpoint-status |  |  | checkpoint | Completion
text | b8842739-1838-4d27-9df5-d6244e9e24d5 |  | textbox | Plumber Name:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Hot Water Service Maintenance Log |  |  |  |  | Yes | QA 22 - Hot Water Service Maintenance Log | f1016649-598c-4469-9049-4e55a41b5e81
checkpoint-no-status |  |  | checkpoint | Hot Water Service Unit Details
text | 73232872-48e7-498c-b33f-0ad2ce164a89 |  | textbox | Purchased from:
text | f49cc8f5-d638-494c-aae4-e87315ecefec |  | textbox | Make:
text | 6d32c8ea-045a-4baa-9350-1efbf2d16077 |  | textbox | Model No.:
text | 4bf32fdb-c518-4de5-972f-799c79562caa |  | textbox | Location:
text | 1291969f-6a93-4c90-b5cc-0bc39e0326fe |  | textbox | Room Designation:
text | 8c3f1bfc-979c-41c2-be68-41c2adc745ba |  | textbox | Installed by:
text | c97479b1-738a-41f7-8c6d-e5578847672b |  | textbox | Installation Date:
text | 68acad5c-1e32-4a81-b2d8-fa6ac4e31e4d |  | textbox | Number of units in series:
text | 85b99816-779a-4a10-9246-3c4f39aea377 |  | textbox | Prescribed temperature set on unit or combined package:
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturer’s instructions
checkpoint-status |  |  | checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint-status |  |  | checkpoint | Clean Pump Strainers
checkpoint-status |  |  | checkpoint | Clean Hot Water inlet Strainer
checkpoint-status |  |  | checkpoint | Clean Hot Water Return Strainer
checkpoint-status |  |  | checkpoint | Confirm all Valve Isolation reinstatement
checkpoint-status |  |  | checkpoint | Confirm Unit is Operational
checkpoint-status |  |  | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint-no-status |  |  | checkpoint | Commissioned By:
text | bf621b8f-a810-4f29-92ae-e075509f1193 |  | textbox | Name:
text | 90e35d94-fcb9-41fc-ba89-da7b6200df48 |  | textbox | Date:
checklist-flat |  |  | checklist | TMV Routine Service Log Sheet |  |  |  |  | Yes | TMV Routine Service Log Sheet | f4ba8512-3904-4ebf-a7d8-561be5220970
checkpoint-status |  |  | checkpoint | TMV Routine Service Log Sheet:
text | b3b5298c-5146-4750-a917-0051faafac4c |  | textbox | Building name:
text | 2fc5edf8-5a2c-40ad-aac3-3407a9604c07 |  | textbox | Contact Person:
text | c4ff76e4-8a50-4d7d-92e7-8a12012ba4de |  | textbox | Address:
text | e30d845d-59e7-4dfc-bd81-0aa33e2109a5 |  | textbox | Phone number:
text | dc86f59a-7f77-412d-80b6-ae2eeae94552 |  | textbox | Make of valve:
text | 0a3fe44e-944a-40b7-a221-e003c8736baa |  | textbox | Model number:
text | cbcef3fa-e09c-4618-9035-062c48d19e98 |  | textbox | Valve location:
text | 8a5a6647-7cc9-42f3-a1c5-ab7583af0aab |  | textbox | Room name:
text | 0dd0812d-41b4-4280-992a-220dda4ef815 |  | textbox | Date of service:
text | d4079f56-9c69-4170-9352-9764a8fbab13 |  | textbox | Outlet water temperature:
button | fc21d0a0-bfad-420d-9631-e00a6d0988ba |  | button | Outlets flushed for 15 seconds | Yes, No
button | a3b7de3b-fdb6-4aca-b4d7-4bf257a8fd19 |  | button | Shower heads disinfected | Yes, No
text | 9aa72656-c4e6-4e5f-93f0-a5afe04f7546 |  | textbox | Serviced By:
checkpoint-no-status |  |  | checkpoint | Recommended Service Periods
label | 06c4306f-c3f3-4ef0-b0de-cf6ffef1e9b1 |  | note | Outlet water temperature = Fortnightly
label | 9d91e029-ed11-4b9c-9b9b-ed88b5fe3089 |  | note | Flushing of outlets = Weekly
label | ed6f22a1-1a4c-408a-bf1d-b6a7ebb244b3 |  | note | Disinfect shower heads = Monthly
checkpoint-status |  |  | checkpoint | Completed by:
text | 76c2177f-130f-49fb-a27b-99f2acfb0c4b |  | textbox | Plumber Name:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Butt Welding |  |  |  |  | Yes | QA 25 - Butt Welding Checklist | fa254ed1-5f1c-45e8-9de1-d0f3cd10169c
checkpoint-no-status |  |  | checkpoint | Operator Details:
text | 6a659436-5134-4e70-a368-2de3aa84d684 |  | textbox | Name:
text | a94e3f38-b37f-43b5-a71d-06b958451003 |  | textbox | Company:
text | c7b573eb-eb5c-4cca-9642-c3d16f62f6cd |  | textbox | Phone:
text | 6d9861ea-738b-4861-92e7-16c5da6cf324 |  | textbox | Address:
checkpoint-no-status |  |  | checkpoint | Welding Machine Details:
text | 8cbdd58f-1c3c-436e-9a8a-8032d9a9ae7a |  | textbox | Manufacturer:
text | 2e18da27-97e1-44f6-ac74-55aa1def1fb1 |  | textbox | Type/Model:
text | e36c8c98-73a4-440e-a0c9-40d55cc08d41 |  | textbox | Serial Number:
text | c00b20e8-0a9f-4479-8717-2df08091ff5f |  | textbox | Year Built:
checkpoint-no-status |  |  | checkpoint | Pipe / Material Details:
text | b0003cd3-7513-440e-ba9a-975c9297f333 |  | textbox | Dn (OD)
text | 7df8d07f-de86-4f15-b675-25baad7f7db9 |  | textbox | SDR
text | 6c670580-8582-4923-991d-5877dd146fbd |  | textbox | En
text | 042563bf-52d0-49dc-8533-228e44539c10 |  | textbox | Type
text | 874155e2-a153-4d54-9fee-bd8dd9881746 |  | textbox | Parameter
text | 74717529-829b-4bae-aff4-059409441572 |  | textbox | SLP
text | 59d72c35-8bdd-4fe7-93aa-09468c5e1512 |  | textbox | SHP
checkpoint-status |  |  | checkpoint | 1
text | 1502dcfa-94cd-4ed5-9c52-d966954e0920 |  | textbox | Time
text | 889786ca-9ff5-43e5-9eb3-c051944005ab |  | textbox | Ambient °C
text | 3f43f75b-91e7-4f52-b5dc-8cb3aeb7544e |  | textbox | Heater Plate °C
text | b1fc3204-0e4c-458a-9676-e5db0237ba12 |  | textbox | Drag Pressure
text | aa11bf59-b0b6-497b-b28f-fa0028e22fdf |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 0d0ba5b8-5f09-4529-8146-11656b64fa9a |  | textbox | Bead Up: t1 (Evidence)
text | 2a9fb209-0f87-42cf-99b6-cdf7f9a45210 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | eec56b15-07c0-4b21-b5bf-30a444783a3f |  | textbox | Heat Soak: t2 (Seconds)
text | fbfb9445-9cc3-4bf3-9713-bb3a0e713c71 |  | textbox | Change Over: t3 (Seconds)
text | f8d3dfa4-e341-4d73-ac0f-8699b9cd4a7a |  | textbox | Pressure Up: t4* (Seconds)
label | cc79ea4d-6ef2-4167-af40-41787ab15af3 |  | note | *t4 not applicable for SHP situations
text | 1f6da46c-5382-425b-8528-ae44d954d5d9 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | a4800d6d-18b4-4767-9e82-ed25bc32bdfa |  | textbox | Weld and Cool: t5 (h:m)
text | 8cbf3c78-6440-4f1f-b16a-2cb53fc0160d |  | textbox | Rough Handling: t6 (h:m)
text | 6451a9dd-9369-4f78-a841-f8a70b6f96a2 |  | textbox | Bead Size: Min
text | 8a86986d-99cf-4230-b762-94be3af838e3 |  | textbox | Bead Size: Max
text | a3dbb6f7-8801-4faa-bc92-b1aa29a07dc8 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 2
text | b0a153e6-914b-4e70-a9d4-bd9071541f89 |  | textbox | Time
text | a78907e6-7ca8-4551-af26-108593b3bb32 |  | textbox | Ambient °C
text | 59ee58c0-db9b-42c7-88cb-715f37965ba9 |  | textbox | Heater Plate °C
text | 9ff19879-c8d2-44c6-9204-b1e350570cbe |  | textbox | Drag Pressure
text | c580bf9d-7a68-4f3d-86b4-d203cb1a9f25 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 803cf34d-6c8d-41b0-958c-8c3e5b1619de |  | textbox | Bead Up: t1 (Evidence)
text | 02974677-b096-4a6c-b836-eb9f0c4b0306 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 7cf158a0-a331-4ab3-a6b4-e835d0c7da73 |  | textbox | Heat Soak: t2 (Seconds)
text | 74a9250a-b80d-4659-956d-f4ddf3124bb9 |  | textbox | Change Over: t3 (Seconds)
text | 83382db9-c7f5-48f0-ba8d-4e2310c75f4e |  | textbox | Pressure Up: t4* (Seconds)
label | 70fee494-c529-4119-b32c-17fa73eed894 |  | note | *t4 not applicable for SHP situations
text | a822e53c-88c3-47f1-bed1-ca2287b29b4c |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | f5e7683e-7a49-4a23-9005-b91f85eb5000 |  | textbox | Weld and Cool: t5 (h:m)
text | 6bd1795b-1456-4063-a341-4c2b34043659 |  | textbox | Rough Handling: t6 (h:m)
text | e55a194d-5e3c-48ba-a298-422ad97245e5 |  | textbox | Bead Size: Min
text | c7c1beaa-cb25-497e-be9c-2f68d079a3af |  | textbox | Bead Size: Max
text | f85bf750-c2d5-464a-931c-94c2dfc7bbcd |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 3
text | 95c8416d-3927-4b0d-b35a-54d2f303fc3f |  | textbox | Time
text | cd15c9b7-3336-4b11-92bc-7f36096fec8f |  | textbox | Ambient °C
text | 515da16c-4602-45eb-947c-b06432bfad4d |  | textbox | Heater Plate °C
text | fbb32919-5736-4365-a271-1bd670c59233 |  | textbox | Drag Pressure
text | eff16332-162f-44f4-ac9a-02f90e38cfbe |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 0bd3260d-5455-4e9b-bcf4-8c66da5b5da6 |  | textbox | Bead Up: t1 (Evidence)
text | ae633361-9087-426e-8730-1f17d8e2047c |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 4c7b6ecd-8f97-4fec-a253-83dcc6d42e4a |  | textbox | Heat Soak: t2 (Seconds)
text | 58720e26-787c-465f-a5c0-b2b4d7119d60 |  | textbox | Change Over: t3 (Seconds)
text | fd4d787a-c88c-41e5-8a49-fc2de607f848 |  | textbox | Pressure Up: t4* (Seconds)
label | 436f6679-269d-4291-8d81-eccfa6ce6d00 |  | note | *t4 not applicable for SHP situations
text | 0f7769c3-c466-4b32-bbdd-717baa9f8032 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 54c4c619-78a5-4618-ba35-61101ddd32b7 |  | textbox | Weld and Cool: t5 (h:m)
text | 1060d1e7-8d5d-4ef7-995b-33a82883a7a5 |  | textbox | Rough Handling: t6 (h:m)
text | fa0d9f68-03a8-44dc-9a45-c9b7d88e45ee |  | textbox | Bead Size: Min
text | 2007e70d-ad87-4ed4-a98d-eb069dc3c800 |  | textbox | Bead Size: Max
text | e94648c2-f9a5-406b-a47c-e31a87cd27df |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 4
text | 92a303db-1cca-4578-8241-1f51fd0e9e5e |  | textbox | Time
text | a2370c38-6383-4f0a-a277-b5faf2b990c7 |  | textbox | Ambient °C
text | 4457d5f8-a1dd-4d4e-bc89-b109a318f679 |  | textbox | Heater Plate °C
text | e4d7bef0-6881-4832-a80a-e5c0abc42bc1 |  | textbox | Drag Pressure
text | 66cae7c2-68a3-4758-a681-4b310e2cb48d |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 4138ced9-c857-45f0-9bc4-381e4c5ae8d5 |  | textbox | Bead Up: t1 (Evidence)
text | 43c6a42e-8d99-4a70-bf29-22cfc179c451 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 92ae3dc3-d34c-41c6-a8a1-5650e7bb0d89 |  | textbox | Heat Soak: t2 (Seconds)
text | c7e1effa-b5af-4ba5-8e5b-bdff3925ff5e |  | textbox | Change Over: t3 (Seconds)
text | ee5b6764-44c8-4f6d-9a18-c99bd415a329 |  | textbox | Pressure Up: t4* (Seconds)
label | 6609e128-33a3-45f1-9f41-ef0c2e3bff3d |  | note | *t4 not applicable for SHP situations
text | 95f8bd39-4bbc-4815-b4f3-1c489d8bea1e |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 8d1e45fb-90cd-4456-bd53-f7e62f86b188 |  | textbox | Weld and Cool: t5 (h:m)
text | c86338df-9489-4dd8-bd13-4b374718e604 |  | textbox | Rough Handling: t6 (h:m)
text | 33990059-9332-4c6b-9ac9-22e35e214a32 |  | textbox | Bead Size: Min
text | 120bb0d0-2f97-48a1-939f-ae34c007a669 |  | textbox | Bead Size: Max
text | 35bc18d9-b1af-4637-8650-582896b1ebf7 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 5
text | 491eaac4-a6a5-4d80-b77e-d0e6f4c0c35d |  | textbox | Time
text | 11bf175b-7aec-464c-b7f5-e1f1eb276d4f |  | textbox | Ambient °C
text | 0fca29b6-5a33-40f6-b417-609355290958 |  | textbox | Heater Plate °C
text | 0006e1fd-ff76-4b72-afc7-ae8de3ad980d |  | textbox | Drag Pressure
text | ad5bbbbd-ecee-4c11-999d-d911317af60c |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 8265d05b-730d-482a-8fe2-23124e7997f4 |  | textbox | Bead Up: t1 (Evidence)
text | 9702cb4a-1862-4c52-ab9c-666b826f26a5 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | f5741b8f-2dc5-4088-a95c-e5f524a32c75 |  | textbox | Heat Soak: t2 (Seconds)
text | ecbc9170-ea1e-45d0-a56a-ab86108de8dc |  | textbox | Change Over: t3 (Seconds)
text | 01f0cc87-2162-4585-963f-00414ccc3fb8 |  | textbox | Pressure Up: t4* (Seconds)
label | 329dbf0f-b31c-4124-a0eb-f16dd4a31d51 |  | note | *t4 not applicable for SHP situations
text | 0c91990c-c26a-41e8-8488-5cad884337b0 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | f6f53b3c-be74-4fee-af3c-1f251fc304dc |  | textbox | Weld and Cool: t5 (h:m)
text | e91c80e3-0e46-43fe-b24d-edc90e60ba36 |  | textbox | Rough Handling: t6 (h:m)
text | 418121e2-6aaf-43e4-9b0d-301a9b253b5d |  | textbox | Bead Size: Min
text | 16148672-c032-4f85-a6be-ba417df6fdf2 |  | textbox | Bead Size: Max
text | a083f7f2-168a-4809-9d87-a727818362db |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 6
text | 9bf4eea7-c15b-449c-b127-247504126fe4 |  | textbox | Time
text | 26f04774-6185-43a9-87c5-a89f9e8427e6 |  | textbox | Ambient °C
text | feb138ff-23d4-485b-a6fb-42afabf6b719 |  | textbox | Heater Plate °C
text | 29c963bb-e999-4c56-94c0-c48072dca9b3 |  | textbox | Drag Pressure
text | 11c4f159-57c2-452d-a8b4-be431c5c63c1 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 16f08445-4abc-448d-a1c6-de5101350b60 |  | textbox | Bead Up: t1 (Evidence)
text | 2b1f211e-0afb-46a9-97d4-bf1bce2a2506 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 74284adf-f246-45bf-8aa2-bcaecb18417e |  | textbox | Heat Soak: t2 (Seconds)
text | 08f98208-7a72-47e5-847b-03876059ddfd |  | textbox | Change Over: t3 (Seconds)
text | 46764ef2-0027-457d-a34b-df91673a98df |  | textbox | Pressure Up: t4* (Seconds)
label | 33d2e0d7-e85c-4339-9911-9bfbc77f1079 |  | note | *t4 not applicable for SHP situations
text | a41df091-ece0-4a17-a5f2-3cc66a9fb990 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | c246fcc3-5333-463d-a78d-73d5eaa4adae |  | textbox | Weld and Cool: t5 (h:m)
text | fb437c4d-5ff4-436a-9359-f4c1c05789a2 |  | textbox | Rough Handling: t6 (h:m)
text | f9efdf25-d4b9-425a-bc1a-075cc8e62bfa |  | textbox | Bead Size: Min
text | 20a9d9ed-7ef4-4654-b6f1-ae9ee64a2f90 |  | textbox | Bead Size: Max
text | f5b33377-68fd-4514-9be2-48afc06c0874 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 7
text | aa009d00-20f0-4a35-93f6-682487906fa0 |  | textbox | Time
text | 7d4bde2c-c2ee-4175-b4f3-7a016d293a40 |  | textbox | Ambient °C
text | 16ba281e-ef91-4613-94a5-b51a02190f5f |  | textbox | Heater Plate °C
text | 8b6fa33e-d92a-41f4-b6e0-9fb4b9400fa9 |  | textbox | Drag Pressure
text | 4add3960-f6c9-4547-b202-aa6bb63934c0 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | ea8e58b6-2748-4f20-a2df-f91eb8a8df03 |  | textbox | Bead Up: t1 (Evidence)
text | 2056287a-caf1-45b7-bd6b-92ff82bebc1a |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 1293364e-7429-4d19-8409-c4b91690b3b3 |  | textbox | Heat Soak: t2 (Seconds)
text | 19877051-0214-4308-8ce3-28fba67f77fb |  | textbox | Change Over: t3 (Seconds)
text | 41a56918-8c34-49a9-a123-3b9168703c0b |  | textbox | Pressure Up: t4* (Seconds)
label | 890c3d1b-e5c7-4909-8601-599720e3a014 |  | note | *t4 not applicable for SHP situations
text | 2c6b3722-e504-41e5-82db-051d1475c558 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 589ecb18-40c3-4444-a9b9-fff7355a1b40 |  | textbox | Weld and Cool: t5 (h:m)
text | 755614ca-3baf-4570-b7ee-b9c6b5a9ea8d |  | textbox | Rough Handling: t6 (h:m)
text | 0bfbad76-de58-4d3a-8e25-a9db6eaf1b2d |  | textbox | Bead Size: Min
text | 34238a92-d630-44eb-b6ae-35ce2386303e |  | textbox | Bead Size: Max
text | a02a0471-e3dc-45eb-95dd-0b19ee05977b |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 8
text | b1ea04a7-9098-4012-b830-29283c7e7ea5 |  | textbox | Time
text | 77cfa2bd-4129-4938-b01c-feb8e69b8f8c |  | textbox | Ambient °C
text | a7afd392-da57-4f03-8f10-05a6d57f6d8d |  | textbox | Heater Plate °C
text | a07df96e-0c78-412c-a869-fa83326af39b |  | textbox | Drag Pressure
text | 6644a14e-b614-4a26-abc6-ac6cd57b9304 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | c1279c72-f2a5-4efa-bf05-181a23cd0746 |  | textbox | Bead Up: t1 (Evidence)
text | 0323ec8f-f40f-45c8-b855-fe0715ec9550 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 4157aa69-ae86-4c9b-aeb7-bb377757da14 |  | textbox | Heat Soak: t2 (Seconds)
text | e25558cd-2a8e-4446-a3ac-c04c9dd3623c |  | textbox | Change Over: t3 (Seconds)
text | 2ee59cd7-7a7c-49a2-8fa7-9973e45104ff |  | textbox | Pressure Up: t4* (Seconds)
label | 2300a9fd-309e-4c99-af63-a6e5ffc3f696 |  | note | *t4 not applicable for SHP situations
text | a4a5b208-c6f5-4c04-a47d-ca9e4bc479c8 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | ce7f0123-129f-4234-a53e-b5731a395ff8 |  | textbox | Weld and Cool: t5 (h:m)
text | fac4c4b5-2964-4057-a554-a5b4ec2d4eaf |  | textbox | Rough Handling: t6 (h:m)
text | 57c32eff-e69f-4f89-8833-552ac2835b4e |  | textbox | Bead Size: Min
text | a5dff216-4c1d-4b21-98a0-d8f807580583 |  | textbox | Bead Size: Max
text | 6f2037f6-89fd-46f7-b55c-721eaa0d2374 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 9
text | 12d5cd83-6dd1-4753-8421-6934af05933d |  | textbox | Time
text | d1409ede-3921-4c47-9298-0301a69aad3a |  | textbox | Ambient °C
text | 325f87f6-80a9-49d8-81e9-0245daac46bf |  | textbox | Heater Plate °C
text | f822b94e-734c-4c2f-b919-998ecf3c665e |  | textbox | Drag Pressure
text | 1bc677ff-7d68-48d3-a0b3-ab8af79442cc |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 8de3afdd-2570-4e4f-9c1a-c827e7e2fe86 |  | textbox | Bead Up: t1 (Evidence)
text | 4f412618-2d05-47f9-b2d3-3ad14b492ccf |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 69e2fda3-aaf4-44dd-805e-274f2f41ebb1 |  | textbox | Heat Soak: t2 (Seconds)
text | ba408c3e-ce80-4145-9a21-bfec1ec6e091 |  | textbox | Change Over: t3 (Seconds)
text | 08faf1f4-2b97-46ba-baf6-0af207a9bd57 |  | textbox | Pressure Up: t4* (Seconds)
label | 709e4d41-3296-4b08-aade-9716437909d7 |  | note | *t4 not applicable for SHP situations
text | 349a733e-0609-45eb-a7cc-4f360c53285a |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | a221639d-4e26-4684-939e-8666f7bb1a61 |  | textbox | Weld and Cool: t5 (h:m)
text | 837270ba-cc93-4f28-b2ee-adb553331b41 |  | textbox | Rough Handling: t6 (h:m)
text | 30ab9463-c8bb-45d5-adf4-39e68686611d |  | textbox | Bead Size: Min
text | bcfdb232-74bb-4c92-9fa8-8249ffd70158 |  | textbox | Bead Size: Max
text | b7436212-b172-4726-bcaf-7a2280620c44 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 10
text | 8a81356e-e859-4f35-be69-f388617c383a |  | textbox | Time
text | 705f2241-4f4d-4654-8183-b1fc6eaaf263 |  | textbox | Ambient °C
text | 8f0abaa2-225e-4fe6-b147-7bfbd85af462 |  | textbox | Heater Plate °C
text | 20979a79-ff27-4ece-a881-c05342013fb2 |  | textbox | Drag Pressure
text | 9ae5dc0b-efd1-452a-840a-2ec5cb492eb4 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 9fc642f3-e13e-48ab-9884-3f394bfbd443 |  | textbox | Bead Up: t1 (Evidence)
text | 26eacfc3-a1aa-4e6a-af80-7903ffb77416 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d1e080eb-2ac6-43a7-b0fe-1594c22f0940 |  | textbox | Heat Soak: t2 (Seconds)
text | bce57c61-77b2-4061-bcc4-21ed7f9f0503 |  | textbox | Change Over: t3 (Seconds)
text | dab89a80-aba5-4245-b62d-bd18d4d3feae |  | textbox | Pressure Up: t4* (Seconds)
label | ae2fe6d1-f199-4f59-808b-4986381fbd7f |  | note | *t4 not applicable for SHP situations
text | 801f8db2-2db2-4e55-97a5-05df5afd5754 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 1a18f890-0597-4288-abdc-6b224b6cacfb |  | textbox | Weld and Cool: t5 (h:m)
text | e60bb6ca-45be-44b6-95d7-2926475ea46f |  | textbox | Rough Handling: t6 (h:m)
text | a5e774b8-7d02-4a25-975a-ce7565d084bc |  | textbox | Bead Size: Min
text | 939ec515-5373-4d83-a75f-c96050b3f50c |  | textbox | Bead Size: Max
text | 558135f6-0f5e-47e1-8f19-4eba7a35827f |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 11
text | 7e3e3379-1cc8-42f7-9811-298d90984239 |  | textbox | Time
text | c0afcbd4-e1a6-4b8a-8e4b-3a3f0df4dc8f |  | textbox | Ambient °C
text | 46843fd8-a136-403b-ab2d-58cc717420b5 |  | textbox | Heater Plate °C
text | e8cd568e-8324-49f9-8319-5f106731db54 |  | textbox | Drag Pressure
text | 75f15e9b-ee6c-48be-b6f0-861985889e63 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 1c112f86-82a2-4bd3-916d-46b3f89094e6 |  | textbox | Bead Up: t1 (Evidence)
text | eebebb71-17aa-439d-aa9f-b45d9de7dbd6 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | b4eee4b1-d4c9-4e38-a08f-a87bd39a5e31 |  | textbox | Heat Soak: t2 (Seconds)
text | 38314a48-dcb3-40e9-843b-50322c0739e4 |  | textbox | Change Over: t3 (Seconds)
text | 31d99da5-736e-4403-b17a-75aed21d4668 |  | textbox | Pressure Up: t4* (Seconds)
label | dd9d6b9e-c06c-4cc7-92a9-5d937ebc5d7b |  | note | *t4 not applicable for SHP situations
text | ed868fa4-bd3a-4257-b666-8cdab3c18a15 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 25028bd4-fe9f-475a-8199-6caf3ac707b9 |  | textbox | Weld and Cool: t5 (h:m)
text | e888a548-63d8-4dc1-9401-da51628d7d00 |  | textbox | Rough Handling: t6 (h:m)
text | 4ee3e54a-a787-453e-8d91-579fe688b532 |  | textbox | Bead Size: Min
text | 3c0f3513-5734-4e6a-9282-008828c87187 |  | textbox | Bead Size: Max
text | d7c72a23-bcd8-4b41-a0fc-753a5991571c |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 12
text | 4ba6356d-8427-4e3a-bb01-5d3305e215d5 |  | textbox | Time
text | 4f894de1-7172-4927-bcd4-9e924472d30f |  | textbox | Ambient °C
text | 6b6c8dd8-3095-4f0b-bbd1-7408b9aa338b |  | textbox | Heater Plate °C
text | 049bf2bc-db12-44dc-a440-140922f5de19 |  | textbox | Drag Pressure
text | c2fb4539-e7fc-40aa-98be-dcd4ca55f2ab |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 0bd62fa7-4a67-4c95-8a37-95706fcbe7a5 |  | textbox | Bead Up: t1 (Evidence)
text | 297d2b89-aa2f-4e85-afbd-6808682ed807 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 28054da2-667e-4e08-b1f1-c4e97a14e1d9 |  | textbox | Heat Soak: t2 (Seconds)
text | c8ee2f15-7de2-4d0d-8e05-5b815a7bf232 |  | textbox | Change Over: t3 (Seconds)
text | cbb69069-3652-4533-b41a-684bbdcf5025 |  | textbox | Pressure Up: t4* (Seconds)
label | afbe615a-d85a-4163-934a-75244dc1842c |  | note | *t4 not applicable for SHP situations
text | aa08f05f-3371-400a-9d6e-ca14611b7836 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 07400bab-e118-43a1-87f8-73f40c655831 |  | textbox | Weld and Cool: t5 (h:m)
text | 1f09f620-0f89-41ab-b448-cda8330ee5ac |  | textbox | Rough Handling: t6 (h:m)
text | 64556a21-fd49-4e56-aa0f-5ece9f255788 |  | textbox | Bead Size: Min
text | 420f8f28-887d-47b3-8a57-af4abb1bec40 |  | textbox | Bead Size: Max
text | b7adb257-9e18-425d-9526-d915fc6bf0cd |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 13
text | a310d016-f58a-48a8-940f-9d336b120753 |  | textbox | Time
text | 0c27d0e7-3f6d-4a4f-a749-e0c5ce283ca1 |  | textbox | Ambient °C
text | f340d26b-8639-4c80-a932-78653cc8dc79 |  | textbox | Heater Plate °C
text | 87281659-d97d-4d49-a1b0-91448c359445 |  | textbox | Drag Pressure
text | 92384837-c7f0-425b-9914-dd600009cbdc |  | textbox | Bead Up: P1 (Kpa/Bar)
text | e89e3274-9e5f-49c6-bbca-f57b8f0d5bf4 |  | textbox | Bead Up: t1 (Evidence)
text | e9d16d77-5394-4221-b14b-2d52cc4687a1 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | febfc885-e98b-4abf-843f-1f965dea113d |  | textbox | Heat Soak: t2 (Seconds)
text | b373189d-295c-42ef-a4a2-5b227e3770d6 |  | textbox | Change Over: t3 (Seconds)
text | ccfd8516-7aab-4d99-bb33-64f043c59f91 |  | textbox | Pressure Up: t4* (Seconds)
label | 4aa00c6f-7775-4f56-ad50-5a165c5290a5 |  | note | *t4 not applicable for SHP situations
text | 39530b3a-ce62-44c7-9b42-6354cf6afee8 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 1e4cd914-a15d-47da-b747-48960f25e8d2 |  | textbox | Weld and Cool: t5 (h:m)
text | 3a270710-f648-43e0-a21b-7c6b85c3efe2 |  | textbox | Rough Handling: t6 (h:m)
text | 8ea9877d-af51-40fe-8fdd-349ddf0b58bd |  | textbox | Bead Size: Min
text | 91afbe0e-2050-4e9f-8430-01950062907c |  | textbox | Bead Size: Max
text | b18cf759-1888-4ae8-a6c4-a8b3aa67b6e0 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 14
text | 9e1d7087-d340-4086-82cf-003cc96568b5 |  | textbox | Time
text | 3d9979a7-b9db-4ec9-bedd-15f7032ec82b |  | textbox | Ambient °C
text | 27b26f9b-3dc6-494b-becf-4f762e137e89 |  | textbox | Heater Plate °C
text | a7517728-d168-448f-9e9d-ea8e5ad8c041 |  | textbox | Drag Pressure
text | 8fd5aebf-6572-4392-b6ff-5299006c4ba3 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | c6e280f9-c768-4526-9178-e3a716ee97d6 |  | textbox | Bead Up: t1 (Evidence)
text | 1320e3d2-045a-468d-a468-3afdd05bc669 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 04f63696-52f2-4894-9adc-7e3ecb35b09c |  | textbox | Heat Soak: t2 (Seconds)
text | 2b5e9c19-5209-4e3a-8a1e-1ee172bbb14c |  | textbox | Change Over: t3 (Seconds)
text | fef69dd5-8a6f-4c64-9131-d8e86d0f8099 |  | textbox | Pressure Up: t4* (Seconds)
label | 28507ad5-cda7-465e-b866-82efb43a1b00 |  | note | *t4 not applicable for SHP situations
text | 4d029a80-9ac9-416a-9b2f-12ba26f95f15 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 52e5fa2a-53c6-42a9-98a3-5ac53b4a7fdc |  | textbox | Weld and Cool: t5 (h:m)
text | ca1fc7a9-2fd5-49f9-849d-2480bd251e28 |  | textbox | Rough Handling: t6 (h:m)
text | 376540fc-4584-44c2-9839-dd59c5829b29 |  | textbox | Bead Size: Min
text | 6a5178a5-0795-48c9-8c49-324cc1292d69 |  | textbox | Bead Size: Max
text | f7097215-2b91-4070-9e02-88764fe54791 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 15
text | 7b8921a8-611d-434e-b868-ae0c71a9698f |  | textbox | Time
text | 38ee9f5f-e500-4d89-8177-10bb275a535f |  | textbox | Ambient °C
text | 717d5d2f-770b-47da-8f90-3adfb58aab8c |  | textbox | Heater Plate °C
text | 1453cfc7-bc26-43b5-9897-81b8bba270df |  | textbox | Drag Pressure
text | 84913943-bbbd-44cd-840a-ab1450f3f5dc |  | textbox | Bead Up: P1 (Kpa/Bar)
text | dd9c48c2-7bbd-4e54-9b97-547f4de335da |  | textbox | Bead Up: t1 (Evidence)
text | b8f21413-36ee-4d68-8873-bad30b65548c |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 384bf76b-1ec6-4e3e-9616-96faf5189a42 |  | textbox | Heat Soak: t2 (Seconds)
text | 5d98364e-5e28-41d7-84f6-e956065628fc |  | textbox | Change Over: t3 (Seconds)
text | fa3c612c-fe84-463b-b426-06495b179ff6 |  | textbox | Pressure Up: t4* (Seconds)
label | 83be92dd-6def-4889-a9d1-29be3b76b2cf |  | note | *t4 not applicable for SHP situations
text | 304d21d2-1da9-4343-9b30-978733faee98 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 761ec7bf-36f9-4148-afc7-67c7bf5f160b |  | textbox | Weld and Cool: t5 (h:m)
text | fcd1f6d3-8fc5-406a-85ff-0865f70fed32 |  | textbox | Rough Handling: t6 (h:m)
text | 78b3b39c-cc99-46f9-abb4-f0b1f51ef7f5 |  | textbox | Bead Size: Min
text | c5583b44-f511-4268-b543-71da2e94dcc1 |  | textbox | Bead Size: Max
text | fdd68282-f20e-4c03-9a97-093f61caf6a0 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 16
text | f82cb24a-e623-4e74-a55f-dae87b5a98f6 |  | textbox | Time
text | 506392ef-eaa1-4cf4-a38b-6c2e55657cd2 |  | textbox | Ambient °C
text | 9185c75f-9ff2-4759-8f0a-2237da483c1b |  | textbox | Heater Plate °C
text | 8a4a08ff-128d-45fd-b4a9-d9243b319dd8 |  | textbox | Drag Pressure
text | d564ec53-2428-4766-b77d-5835e19e251b |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 6789cd73-7cea-4187-bdba-f6373be7a565 |  | textbox | Bead Up: t1 (Evidence)
text | df20ed1b-0743-486a-8317-6952a4582d55 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | ed3a3ed2-c14a-47f5-b933-14084fd96859 |  | textbox | Heat Soak: t2 (Seconds)
text | d35fdcc8-7fae-4fff-a2ac-4a6bf01a3a2f |  | textbox | Change Over: t3 (Seconds)
text | b159cefb-1c23-46fa-a482-c4877cb1a908 |  | textbox | Pressure Up: t4* (Seconds)
label | 40739f57-53a0-4fd7-b2f4-cb532789c449 |  | note | *t4 not applicable for SHP situations
text | a86db6a4-c222-42b8-b6fb-e3a02dbb4907 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 99052310-3cde-406d-9260-34e3f37078b3 |  | textbox | Weld and Cool: t5 (h:m)
text | da71dabb-fa25-48d0-9e71-a057497a2d9b |  | textbox | Rough Handling: t6 (h:m)
text | 3ab63069-1b80-4fc7-a246-2f1ba89ebe1f |  | textbox | Bead Size: Min
text | 01179a0f-a4a0-4223-8474-d8df63ef8f83 |  | textbox | Bead Size: Max
text | ea85b647-9258-4c4f-9e23-b4bd8a817fe7 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature