## Table 1
Light Pole Foundation Inspection and Test Plan
Project: Wellesley St Bus Interchange - WSBI
Number and Revision: DN1211 - 004 - Rev 00
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity
[6 empty] | Activity | By | MSQA signature (Blank as Req.) | Engineer Rep Signature (Blank as req.) | Comments / Closeout Details
SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
3.1 | Construction Pack | Submit a Construction Pack including a Methodology and JSEA to the Engineer before works | Downer | Construction Pack | Submit 5 days prior to commencement of works | H | PE |  | H
3.2 | Survey Setout | Survey Set out as per contract drawings and specification, capturing pre- construction levels where needed. | Downer | Survey Records | Prior to Works | H | SV | C
3.3 | Service Location | Complete the Excavation permit process to identify, locate and protect all services. | Downer | Excavation Permit | Prior to Excavation | H | SE
3.4 | Internal Permits | Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc. | Downer | Internal Permits | Prior to Excavation | H | SE
3.5 | External Permits | Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc. | Downer | External Permits | Prior to Excavation | H | PE |  | R
3.6 | Approved Construction Drawings | Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version. | Downer | IFC Drawings | Prior to works start | H | PE
SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
4.1 | Mix Design | Concrete to be 30Mpa as per DRG-SS-2231 19mm max aggregate . Contractor to provide mix design and strength testing records on request | Downer | Approved MAR | Once Prior | H | PE | R | R
4.2 | Mortar | Consisting of two parts fine, sharp, well graded sand to one part dry cement. Mix by hand or mixer in small quantities use within 30 minutes | Downer | Approved MAR | Once Prior | H | PE | R | R
4.3 | Reinforcing | Reinforcing as per Aurecon Specification | Downer | Approved MAR | Once Prior | H | PE | R | R
4.4 | Hold Down bolts | Hold Down bolts as per pole manufacturers requirements | Downer | Approved MAR | Once Prior | H | PE | R | R
SECTION 5 – CONSTRUCTION ACTIVITY – LIGHT POLE INSTALLATION
5.1 | Set | Centre of Pile set out as per Model coordinates provided. Hold down bolts to be surveyed to essure they align with the location of Light pole bolts. | Downer | QA Checksheet | Prior to concrete pour | H | PE
5.2 | Reinforcing | Reinforcing and embedded items cut, bent (cold) and accurately placed as shown on design drawings. At least 30mm cover to all reinforcing +5mm/-0mm Bar spacing as per Drawings +/-10mm Bend locations as per drawings +/-5mm | Downer | QA Checksheet | Prior to concrete pour | I | PE
5.3 | Conduit Install | Conduits installed as per NUO requirements and DRG-SS-2231 | Downer | QA Checksheet | Prior to concrete pour | I
5.4 | Pre Pour inspection | Notify Engineer for inspection atleast 24 hours prior to pour | Downer | Pre pour checksheet | Prior to concrete pour | H | DES | C
5.5 | Light pole bases / Pile | Concrete shall be high grade with a minimum compressive strength at 28 days of 30 MPa Concrete slump shall be 175mm +/-25 mm. Concrete to be tremied. Vibrating pokers to be used during entire pile length pour. Delivery dockets dated and showing the concrete supplier and design strength shall be collected and held for every pour. Record location and date of each pour. 3 cylinders taken for each pour slump targets as per mix design (1 sample per 75m^3 or each pour) | Aurecon Spec 15.5 | QA Checksheet | each structure During pour | C | SE | W
5.6 | Post Pour | Concrete cylinders to achieve minimum target satrenght after 28 days. At the Engineers request site samples/cores for indepentdant testing of fresh or cured concrete to review grading, mix design, strength and thickness. | Aurecon spec 13. | Test Report | As requested | H | ENG | R | R
SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
6.1 | Construction Record Compilation | Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted. | Downer | Records | Post construction | H | SE | R | H
6.2 | Survey Records | Ensure all items have been surveyed and records are assembled for asbuilting | Downer | Records | Post construction | H | SV | R | H
6.3 | Redline Drawings | Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. | Downer | Redlines | Post construction | H | PE | R | H
6.4 | Defect, Snag and Punch List | Update the project Defect, Snag and Punch List Register | Downer | Register | Post construction | H | PE | R | H